## Introduction
ADMS
16.0.0
Modeling Reference Tables
Document Date: Apr 24, 2024
This Excel workbook is a supplement to the Distribution Modeling Reference Guide.
Each worksheet tab contains a table. Each table and its use is described in the Distribution Modeling Reference Guide.
Copyright
Copyright 2025, GE Vernova and/or its affiliates ("GE Vernova"). All Rights Reserved. This document is the confidential and
proprietary information of GE Vernova and may not be reproduced, transmitted, stored, or copied in whole or in part, or
used to furnish information to others, without the prior written permission of GE Vernova.

## Station Input
Sort | Type | Field Name (XML) | Field Name (CSV) | Authoritative Source | Description | Attribute Type | Imperial Units | Metric Units | Scope | Default | Possible Values or Reference | Required? | Low Value Imperial Units | High Value Imperial Units | Low Value Metric Units | High Value Metric Units | Queryable Field Name | Available in 3.11 | Available in 3.10 | Available in 3.9 | Available in 3.8.6
1 | Automation Scheme | Description | DESCRIPTION_SCHEME | Externals | Description of the automation scheme | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | DESCRIPTION | Yes | Yes | Yes | No
2 | Automation Scheme | Id | ID_SCHEME | Externals | ID of the automation scheme | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | No
3 | Automation Scheme | Name | NAME_SCHEME | Externals | Name of the automation scheme | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | No
4 | Automation Scheme Team | Description | DESCRIPTION_TEAM | Externals | Description of the automation scheme team | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | DESCRIPTION | Yes | Yes | Yes | No
5 | Automation Scheme Team | Id | ID_TEAM | Externals | ID of the automation scheme team | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | No
6 | Automation Scheme Team | Name | NAME_TEAM | Externals | Name of the automation scheme team | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | No
7 | Automation Scheme Team | Scheme | SCHEME_TEAM | Externals | The name of the associated automation scheme | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | No
8 | Automation Scheme Team Switch | Id | ID_TEAMSW | Externals | ID of the switching device | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | No
9 | Automation Scheme Team Switch | Name | NAME_TEAMSW | Externals | Name of the switching device | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | No
10 | Automation Scheme Team Switch | Role | ROLE_TEAMSW | Externals | Switching device role (primary or secondary) | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ROLE | Yes | Yes | Yes | No
11 | Automation Scheme Team Switch | SecondId | SECONDID_TEAMSW | Externals | Alternate ID of the switching device | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | No
12 | Automation Scheme Team Switch | Station1 | STATION1_TEAMSW | Externals | The first station that is associated with the switching device | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATION1 | Yes | Yes | Yes | No
13 | Automation Scheme Team Switch | Station2 | STATION2_TEAMSW | Externals | The second station that is associated with the switching device (For boundary switches) | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATION2 | Yes | Yes | Yes | No
14 | Automation Scheme Team Switch | Team | TEAM_TEAMSW | Externals | The name of the associated automation scheme team | String | #N/A | #N/A | OPS, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | No
15 | Breaker | Address | ADDRESS_BREAKER | Internals | Breaker address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
16 | Breaker | AltGroundTrip | #N/A | Internals | Relay alternate ground trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 3000 | 0 | 3000 | BRKALTPHTRPAMP | Yes | Yes | Yes | Yes
17 | Breaker | AltPhaseTrip | #N/A | Internals | Relay alternate phase trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 3000 | 0 | 3000 | BRKALTGRTRPAMP | Yes | Yes | Yes | Yes
18 | Breaker | CompanyName | COMPANYNAME_BREAKER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
19 | Breaker | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID (for station internal devices only). | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
20 | Breaker | ComputeFlows | COMPUTEFLOWS_BREAKER | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
21 | Breaker | County | COUNTY_BREAKER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
22 | Breaker | CustomField:IsString | CUSTOMFIELDISSTRING_BREAKER |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
23 | Breaker | CustomField:Name | CUSTOMFIELDNAME_BREAKER |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
24 | Breaker | CustomField:Value | CUSTOMFIELDVALUE_BREAKER |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
25 | Breaker | DERId | DERID_BREAKER |  | The ID of the Distributed Energy Resource (DER) that this protective device connects/disconnects from the electrical network. It is used by the FISR DER blocking functionality.. | String | #N/A | #N/A | FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONDER | No | No | No | No
26 | Breaker | DSOOverride | DSOOVER_BREAKER | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: Not Set 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
27 | Breaker | ExternalInterfaceExternallyOwned |  | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
28 | Breaker | ExternalInterfaceMember |  | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
29 | Breaker | FeedMainBound | FEEDMAINBOUND_BREAKER | Externals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag for topology objects. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
30 | Breaker | FromNode | FRNODE_BREAKER | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
31 | Breaker | Future | FUTURE_BREAKER | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS, NTP | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
32 | Breaker | Grdcapbl | #N/A | Internals | Flag indicating the breaker has ground trip capability (True = has ground trip capability). | Boolean | #N/A | #N/A | DPF, FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GRDCAP | Yes | Yes | Yes | Yes
33 | Breaker | GroundOps | GROUNDOPS_BREAKER | Internals | Total number of ground reclose operations. | Integer | count | count | DPF, FISR | User-configurable through Defaults File | User-configurable through Defaults File | FALSE |  |  |  |  | NUMGROPS | Yes | Yes | Yes | Yes
34 | Breaker | GroundTrip | #N/A | Internals | Relay normal ground trip setting (Amps). | Float | Amps | Amps | DPF |  |  | TRUE | 0 | 3000 | 0 | 3000 | BRKGRTRPAMP | Yes | Yes | Yes | Yes
35 | Breaker | HoldFaultIndicationCapable | #N/A | Internals | Flag indicating if the breaker is capable of holding fault indication. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
36 | Breaker | Id | ID_BREAKER | Internals | Breaker unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
37 | Breaker | IncidentEnergyCat | INCIDENTENGCAT_BREAKER | Internals | Breaker incident energy category. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENERGYCAT.NOAPPSTR | Yes | Yes | Yes | Yes
38 | Breaker | LabelPlacement:CharacterRotation | LABELCHRROTATION_BREAKER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. By default the character rotation is set to same value as label rotation. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
39 | Breaker | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_BREAKER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
40 | Breaker | LabelPlacement:FontSize | LABELSIZE_BREAKER | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
41 | Breaker | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_BREAKER | Internals | Label Geometry Level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
42 | Breaker | LabelPlacement:GeometryType | LABELGEOMTYPE_BREAKER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
43 | Breaker | LabelPlacement:Rotation | LABELROT_BREAKER | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
44 | Breaker | LabelPlacement:Text | LABELTEXT_BREAKER | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
45 | Breaker | LabelPlacement:X | LABELX_BREAKER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
46 | Breaker | LabelPlacement:Y | LABELY_BREAKER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
47 | Breaker | LargestCoordFuse | LARGESTCOORDFUSE_BREAKER | Internals | Largest coordination fuse size (Amps). This field is used in the upstream device coordination check executed in the Protection Validation (PRV) application. | Float | Amps | Amps | DPF, PRV | 1 |  | FALSE | 1 | 600 | 1 | 600 |  | Yes | Yes | Yes | Yes
48 | Breaker | LoadShedDefaultCircuitClass | LSDEFCLASS_BREAKER | Internals | Device specific load shed classification | Integer | #N/A | #N/A | SLS | 10 | 0: Ignore 1: Do Not Shed 2-10: Circuit Classification | FALSE | 0 | 10 | 0 | 10 | LOADSHEDDEFCLASS | Yes | Yes | Yes | Yes
49 | Breaker | LocationDescription | LOCATIONDESCRIPTION_BREAKER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
50 | Breaker | Maxint | MAXINT_BREAKER | Internals | Maximum interruption rating (Amps). | Float | Amps | Amps | DPF, PRV |  |  | FALSE | 1 | 100000 | 1 | 100000 | RECINTERRUPTAMPS | Yes | Yes | Yes | Yes
51 | Breaker | Municipality | MUNICIPALITY_BREAKER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
52 | Breaker | Name | NAME_BREAKER | Internals | Breaker display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
53 | Breaker | NeutralCurrentTrip | To Be Decided | Internals | This field is the neutral trip setting (in Amps) which is checked by the protection validation functions. | Float | Amps | Amps | DPF | 0 |  | TRUE | 0 | 3000 | 0 | 3000 | NEUTRALRELAYTRIPCURRENT | Yes | No | No | No
54 | Breaker | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_BREAKER | Internals | Nominal feeder ID for the breaker. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for breakers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
55 | Breaker | NominalFeederBoundary | NOMINALFEEDERBOUNDARY_BREAKER | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
56 | Breaker | NormallyDeenergized | NORMDEENERGIZED_BREAKER | Internals | Flag indicating that the breaker is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
57 | Breaker | NormallyLooped | NORMLOOPED_BREAKER | Internals | Flag indicating that the breaker is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP, DPF | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
58 | Breaker | NormallyNetworkLooped | NORMNETWORKLOOPED_BREAKER | Internals | Flag indicating that the breaker is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
59 | Breaker | NormallyOpen | NOPEN_BREAKER | Internals | Flag indicating the breaker is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS, NTP, DPF |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A | NOPEN | Yes | Yes | Yes | Yes
60 | Breaker | NormallyParallelLooped | NORMPARALLELLOOPED_BREAKER | Internals | Flag indicating that the breaker is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
61 | Breaker | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched breakers that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_FUSE field. | String | #N/A | #N/A | NTP |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
62 | Breaker | NoteTCMS | NOTETCMS_BREAKER | Internals | Notify Outage Management System (OMS) flag. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
63 | Breaker | OCRelay | OCRELAY_BREAKER | Internals | Associated overcurrent relay record ID. | String | #N/A | #N/A | DPF, PRV, FISR |  | This field must match a relay ID given in the station file. | FALSE | #N/A | #N/A | #N/A | #N/A | OCPROT | Yes | Yes | Yes | Yes
64 | Breaker | PermitAreaId | PERMITAREAID_BREAKER | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
65 | Breaker | Phase | PHASE_BREAKER | Internals | Breaker phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
66 | Breaker | PhaseOps | PHASEOPS_BREAKER | Internals | Total number of phase reclose operations. | Integer | count | count | DPF, FISR | User-configurable through Defaults File | User-configurable through Defaults File | FALSE |  |  |  |  | NUMPHOPS | Yes | Yes | Yes | Yes
67 | Breaker | PhaseTrip | #N/A | Internals | Relay normal phase trip setting (Amps). | Float | Amps | Amps | DPF |  |  | TRUE | 0 | 3000 | 0 | 3000 | BRKPHTRPAMP | Yes | Yes | Yes | Yes
68 | Breaker | RelayType | RELAYTYPE_BREAKER | Internals | User defined relay type enumeration defined in the global.csv file Enumerations table. | Integer | #N/A | #N/A | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
69 | Breaker | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
70 | Breaker | SecondId | TROUBLECALLID_BREAKER | Internals | Alternate switch ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
71 | Breaker | ServiceCenter | SERVCNTR_BREAKER | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
72 | Breaker | State | STATE_BREAKER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
73 | Breaker | SuppressFeeder |  | Internals | Flag indicating that the feeder name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
74 | Breaker | SwitchModel | SWMOD_BREAKER | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
75 | Breaker | SwitchModelPhA | SWMODA_BREAKER | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
76 | Breaker | SwitchModelPhB | SWMODB_BREAKER | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
77 | Breaker | SwitchModelPhC | SWMODC_BREAKER | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
78 | Breaker | SymbolPlacement:GeometryLevel | GEOMLEVEL_BREAKER | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
79 | Breaker | SymbolPlacement:GeometryType | GEOMTYPE_BREAKER | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
80 | Breaker | SymbolPlacement:Rotation | ROTATION_BREAKER | Internals | Rotation angle. | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | SWPLACE.ROTATION | Yes | Yes | Yes | Yes
81 | Breaker | SymbolPlacement:Size | SIZE_BREAKER | Internals | Placement size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SWPLACE.SIZE | Yes | Yes | Yes | Yes
82 | Breaker | SymbolPlacement:X | WCX_BREAKER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X | Yes | Yes | Yes | Yes
83 | Breaker | SymbolPlacement:X2 | WCX2_BREAKER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X2 | Yes | No | Yes | No
84 | Breaker | SymbolPlacement:Y | WCY_BREAKER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y | Yes | Yes | Yes | Yes
85 | Breaker | SymbolPlacement:Y2 | WCY2_BREAKER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y2 | Yes | No | Yes | No
86 | Breaker | ThirdPartyOwned | THIRDPARTYOWNED_BREAKER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
87 | Breaker | ToNode | TONODE_BREAKER | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
88 | Breaker | ToStation | TOSUB_BREAKER | Internals | Associated external substation name. This field should only be set if the breaker connects two substations together. | String | #N/A | #N/A | OPS, DPF, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
89 | Breaker | UserDefinedRelayType |  | Internals | User defined relay type enumeration. | Integer | #N/A | #N/A | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
90 | Breaker | #N/A | NUMGEOM_BREAKER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
91 | Breaker | #N/A | NUMLABELGEOM_BREAKER | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
92 | Breaker | FeederHeadTieBeaker |  | Internals | Indicates whether the breaker acts as a feeder head tie breaker between two feeder head breakers. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
93 | Breaker | BusTieSwitch | BUSTIESWITCH_BREAKER | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
94 | Bus | CompanyName | COMPANYNAME_BUS | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
95 | Bus | County | COUNTY_BUS | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
96 | Bus | Future | FUTURE_BUS | Internals | Individual phases that are constructed but are not energized. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FUTURE | Yes | Yes | Yes | Yes
97 | Bus | Id | ID_BUS | Internals | Bus unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
98 | Bus | LabelPlacement:CharacterRotation | LABELCHRROTATION_BUS | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
99 | Bus | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_BUS | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
100 | Bus | LabelPlacement:FontSize | LABELSIZE_BUS | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
101 | Bus | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_BUS | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
102 | Bus | LabelPlacement:GeometryType | LABELGEOMTYPE_BUS | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
103 | Bus | LabelPlacement:Rotation | LABELROT_BUS | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
104 | Bus | LabelPlacement:Text | LABELTEXT_BUS | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
105 | Bus | LabelPlacement:X | LABELX_BUS | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
106 | Bus | LabelPlacement:Y | LABELY_BUS | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
107 | Bus | LocationDescription | LOCATIONDESCRIPTION_BUS | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
108 | Bus | Municipality | MUNICIPALITY_BUS | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
109 | Bus | Name | NAME_BUS | Internals | Bus display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
110 | Bus | Node | NODE_BUS | Internals | Associated node. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODE | Yes | Yes | Yes | Yes
111 | Bus | NormallyDeenergized | NORMDEENERGIZED_BUS | Internals | Flag indicating that the bus is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
112 | Bus | NormallyLooped | NORMLOOPED_BUS | Internals | Flag indicating that the bus is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
113 | Bus | NormallyNetworkLooped | NORMNETWORKLOOPED_BUS | Internals | Flag indicating that the bus is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
114 | Bus | NormallyParallelLooped | NORMPARALLELLOOPED_BUS | Internals | Flag indicating that the bus is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
115 | Bus | PermitAreaId | PERMITAREAID_BUS | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
116 | Bus | State | STATE_BUS | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
117 | Bus | SuppressFeeder |  | Internals | Flag indicating that the feeder name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
118 | Bus | SymbolPlacement:GeometryLevel | GEOMLEVEL_BUS | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
119 | Bus | SymbolPlacement:GeometryType | GEOMTYPE_BUS | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
120 | Bus | SymbolPlacement:X | WCXn_BUS | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
121 | Bus | SymbolPlacement:X2 | WCX2n_BUS | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | No | No
122 | Bus | SymbolPlacement:Y | WCYn_BUS | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
123 | Bus | SymbolPlacement:Y2 | WCY2n_BUS | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | No | No
124 | Bus | ThirdPartyOwned | THIRDPARTYOWNED_BUS | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
125 | Bus | VemrgHigh | VEMRGHIGH_BUS | Internals | Emergency high voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRHIGH | Yes | Yes | Yes | Yes
126 | Bus | VemrgLow | VEMRGLOW_BUS | Internals | Emergency low voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRLOW | Yes | Yes | Yes | Yes
127 | Bus | VnrmHigh | VNRMHIGH_BUS | Internals | Normal high voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VNRMHIGH | Yes | Yes | Yes | Yes
128 | Bus | VnrmLow | VNRMLOW_BUS | Internals | Normal low voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VNRMLOW | Yes | Yes | Yes | Yes
129 | Bus | VoltageBase | VOLTAGEBASE_BUS | Internals | Voltage base value. | Float | Volt | Volt | DPF |  | 120 | FALSE | #N/A | #N/A | #N/A | #N/A | VOLTAGEBASE | Yes | Yes | Yes | Yes
130 | Bus | VoltUnit | VOLTSUNITS_BUS | Internals | Enumeration that indicates whether the bus voltage values are given in per unit (1) or on a configurable voltage base (2). | Integer | enumeration | enumeration | DPF, LVM |  | 1: Per unit 2: Configurable voltage base | FALSE | 1 | 2 | 1 | 2 | VOLTUNIT | Yes | Yes | Yes | Yes
131 | Bus | VoptEmrgHigh | VOPTEMRGHIGH_BUS | Internals | Optimization emergency high voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRHIGH | Yes | Yes | Yes | Yes
132 | Bus | VoptEmrgLow | VOPTEMRGLOW_BUS | Internals | Optimization emergency low voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRLOW | Yes | Yes | Yes | Yes
133 | Bus | VoptNormHigh | VOPTNORMHIGH_BUS | Internals | Optimization normal high voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRHIGH | Yes | Yes | Yes | Yes
134 | Bus | VoptNormLow | VOPTNORMLOW_BUS | Internals | Optimization normal low voltage limit (per unit or configurable voltage base) | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRLOW | Yes | Yes | Yes | Yes
135 | Bus | #N/A | NUMGEOM_BUS | Externals | Number of geometries | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
136 | Bus | #N/A | NUMVERT_BUS | Externals | Number of vertices | Integer | count | count | OPS |  | Number of vertex pairs defining the geographic presentation of the bus (At least two vertices must be supplied in order for a bus to be displayed). | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
137 | Bus | #N/A | NUMLABELGEOM_BUS | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
138 | Capacitor Bank | CapacitorBankMastID |  | Externals | ID of the master capacitor. | String | #N/A | #N/A | #N/A | #N/A | #N/A | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
139 | Capacitor Bank | Id |  | Externals | ID of the capacitor in the sequence | String | #N/A | #N/A | #N/A | #N/A | #N/A | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
140 | Capacitor Bank | OnSequence |  | Externals | The On sequence number. The OnSequence numbering begins from zero. | Integer | #N/A | #N/A | #N/A | #N/A | #N/A | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
141 | Capacitor Bank | OffSequence |  | Externals | The Off sequence number. In the capacitor sequence of a capacitor bank, the OffSequence numbering should be in the opposite order of the OnSequence | Integer | #N/A | #N/A | #N/A | #N/A | #N/A | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
142 | Capacitor Bank | SwitchId |  | Externals | ID of the associated switch. | String | #N/A | #N/A | #N/A | #N/A | #N/A | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
143 | Composite Switch | Address | ADDRESS_COMPSW | Internals | Composite switch address. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
144 | Composite Switch | CompanyName | COMPANYNAME_COMPSW | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
145 | Composite Switch | CompositeSwitchLinkMasterID | #N/A | Internals | Composite switch link master ID (for station internal devices only). | String | #N/A | #N/A | OPS |  | The Composite switch link master ID has to be entered for Station Internals Composite Switches. It is to be of the format: "ID=MASTER" where ID could be any string (say "AAA"). | FALSE |  |  |  |  | MASTER | Yes | Yes | Yes | Yes
146 | Composite Switch | CompSwModel | MODEL_COMPSW | Internals | Associated composite switch model name (in the global resources file). A composite switch model must always be given because it contains the valid switch state table. | String | #N/A | #N/A | OPS |  | The composite switch model name must match a composite switch model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | CMPSWMOD.NAME | Yes | Yes | Yes | Yes
147 | Composite Switch | County | COUNTY_COMPSW | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
148 | Composite Switch | CustomField:IsString | CUSTOMFIELDISSTRING_COMPSW |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
149 | Composite Switch | CustomField:Name | CUSTOMFIELDNAME_COMPSW |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
150 | Composite Switch | CustomField:Value | CUSTOMFIELDVALUE_COMPSW |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
151 | Composite Switch | DSOOverride | DSOOVER_COMPSW | Internals | Eligibility override for the switching reconfiguration applications (under development). | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
152 | Composite Switch | Id | ID _COMPSW | Internals | Composite switch unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
153 | Composite Switch | InternalWorldPlacement | INTRLGEOMTYPEn_COMPSW | Internals | The names of the internal geometries. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ARRYSWIT.SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
154 | Composite Switch | LabelPlacement:CharacterRotation | #N/A | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
155 | Composite Switch | LabelPlacement:ConnectionPoint | #N/A | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
156 | Composite Switch | LabelPlacement:GeometryLevel | #N/A | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
157 | Composite Switch | LabelPlacement:GeometryType | LABELGEOMTYPE_COMPSW | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
158 | Composite Switch | LabelPlacement:Vertex:Rotation | NAMELABELROTn_COMPSW | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
159 | Composite Switch | LabelPlacement:Vertex:Size | NAMELABELSIZEn_COMPSW | Internals | Label size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
160 | Composite Switch | LabelPlacement:Vertex:X | NAMELABELXn_COMPSW | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
161 | Composite Switch | LabelPlacement:Vertex:Y | NAMELABELYn_COMPSW | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
162 | Composite Switch | LabelsPlacement:FontSize | #N/A | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
163 | Composite Switch | LabelsPlacement:GeometryLevel | #N/A | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
164 | Composite Switch | LabelsPlacement:GeometryType | #N/A | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
165 | Composite Switch | LabelsPlacement:Rotation | #N/A | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
166 | Composite Switch | LabelsPlacement:Text | #N/A | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
167 | Composite Switch | LabelsPlacement:X | #N/A | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
168 | Composite Switch | LabelsPlacement:Y | #N/A | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
169 | Composite Switch | LocationDescription | LOCATIONDESCRIPTION_COMPSW | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
170 | Composite Switch | Master | MASTER_COMPSW | Internals | Associated master composite switch ID (for a throwover device). | String | #N/A | #N/A | OPS |  | The master composite switch must be found in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | COMPSWMASTER | Yes | Yes | Yes | Yes
171 | Composite Switch | Municipality | MUNICIPALITY_COMPSW | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
172 | Composite Switch | Name | NAME_COMPSW | Internals | Composite switch display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
173 | Composite Switch | Objects:ID | SWITCHn_COMPSW | Internals | Associated switching device IDs that make up the complex device. | String | #N/A | #N/A | OPS |  | Each switching device must match a switch ID in the file. | TRUE | #N/A | #N/A | #N/A | #N/A | ARRYSWIT.ID | Yes | Yes | Yes | Yes
174 | Composite Switch | Objects:Ivalue | SWITCHFUNCTYPEINTn_COMPSW | Internals | Integer format of associated switching device types that make up the complex device. This field is being deprecated. | Integer | #N/A | #N/A | OPS |  | Referring following table: Recloser 1 BypSwitch 2 AutoSwitch 3 IsolSwitch 4 Transformer 5 VacIntSwitch 6 Switch 7 Fuse 8 Bus 9 VacSwitch 10 Fault_Ind 11 Sect 12 Jumper 13 Throwover 14 Multi_Sw 15 |  | #N/A | #N/A | #N/A | #N/A | FUNCTYPE | Yes | Yes | Yes | Yes
175 | Composite Switch | Objects:Type | SWITCHTYPEn_COMPSW | Internals | Associated switching device types (SWITCH or FUSE) that make up the complex device. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ARRYSWIT.MODEL | Yes | Yes | Yes | Yes
176 | Composite Switch | PermitAreaId | PERMITAREAID_COMPSW | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
177 | Composite Switch | Permman | PERMMAN_COMPSW | Internals | Flag indicating manual device operation (True = manual). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MANOP | Yes | Yes | Yes | Yes
178 | Composite Switch | PhaseSenseAlt | PHASESENSEALT_COMPSW | Internals | Phases measured on alternate side of a throwover switch. | String | #N/A | #N/A | OPS |  | ABC, AB, BC, CA, A, B, or C. | FALSE | #N/A | #N/A | #N/A | #N/A | PHALT | Yes | Yes | Yes | Yes
179 | Composite Switch | PhaseSensePref | PHASESENSEPREF_COMPSW | Internals | Phases measured on preferred side of a throwover switch. | String | #N/A | #N/A | OPS |  | ABC, AB, BC, CA, A, B, or C. | FALSE | #N/A | #N/A | #N/A | #N/A | PHPREF | Yes | Yes | Yes | Yes
180 | Composite Switch | ServiceCenter | SERVCNTR_COMPSW | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
181 | Composite Switch | State | STATE_COMPSW | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
182 | Composite Switch | SwitchType | SWITTYPE_COMPSW | Internals | Composite switch type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COMPSWTYPE | Yes | Yes | Yes | Yes
183 | Composite Switch | SymbolPlacement:GeometryLevel | GEOMLEVEL_COMPSW | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
184 | Composite Switch | SymbolPlacement:GeometryType | GEOMTYPE_COMPSW | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PLACEMNT.GEOMETRY | Yes | Yes | Yes | Yes
185 | Composite Switch | SymbolPlacement:IsPoint | ISPOINT_COMPSW | Internals | Flag indicating it is a point placement type. | Boolean | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
186 | Composite Switch | SymbolPlacement:Rotation | ROTATION_COMPSW | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.ROTATION | Yes | Yes | Yes | Yes
187 | Composite Switch | SymbolPlacement:Size | SIZE_COMPSW | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.SIZE | Yes | Yes | Yes | Yes
188 | Composite Switch | SymbolPlacement:Vertex:X | WCXn_COMPSW | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX | Yes | Yes | Yes | Yes
189 | Composite Switch | SymbolPlacement:Vertex:X2 | WCX2n_COMPSW | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX2 | Yes | No | Yes | No
190 | Composite Switch | SymbolPlacement:Vertex:Y | WCYn_COMPSW | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY | Yes | Yes | Yes | Yes
191 | Composite Switch | SymbolPlacement:Vertex:Y2 | WCY2n_COMPSW | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY2 | Yes | No | Yes | No
192 | Composite Switch | SymbolPlacement:X | WCX_COMPSW | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X | Yes | Yes | Yes | Yes
193 | Composite Switch | SymbolPlacement:X2 | WCX2_COMPSW | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X2 | Yes | No | Yes | No
194 | Composite Switch | SymbolPlacement:Y | WCY_COMPSW | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y | Yes | Yes | Yes | Yes
195 | Composite Switch | SymbolPlacement:Y2 | WCY2_COMPSW | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y2 | Yes | No | Yes | No
196 | Composite Switch | ThirdPartyOwned | THIRDPARTYOWNED_COMPSW | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
197 | Composite Switch | TimeDelay | TIMEDELAY_COMPSW | Internals | Throwover operation time delay (seconds). | Float | seconds | seconds | OPS |  |  | FALSE | 0 | 600 | 0 | 600 | TMDELAY | Yes | Yes | Yes | Yes
198 | Composite Switch | #N/A | NUMBSWITCH_COMPSW | Externals | The number of switching devices that make up the composite switch. | Integer | count | count | OPS |  |  | TRUE | 1 | 6 | 1 | 6 | NUMSWIT | Yes | Yes | Yes | Yes
199 | Composite Switch | #N/A | NUMINTRLGEOMTYPE_COMPSW | Externals | The number of internal geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 | NUMGEOM | Yes | Yes | Yes | Yes
200 | Composite Switch | #N/A | LOOPNUMB_COMPSW | Externals | Associated loop number. This field is deprecated. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
201 | Composite Switch | #N/A | NUMGEOM_COMPSW | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
202 | Composite Switch | #N/A | NUMVERT_COMPSW | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | PLACEMNT.NUMVERT | Yes | Yes | Yes | Yes
203 | Composite Switch | #N/A | NUMLABELGEOM_COMPSW | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
204 | Composite Switch | #N/A | NUMNAMELABEL_COMPSW | Externals | Number of vertices. | Integer | count | count | OPS |  |  | FALSE |  |  |  |  | NUMVERT | Yes | Yes | Yes | Yes
205 | Composite Switch | #N/A | NUMLABELGEOM_COMPSW | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
206 | Composite Switch | #N/A | NUMNAMELABEL_COMPSW | Externals | Number of vertices. | Integer | count | count | OPS |  |  | FALSE |  |  |  |  | NUMVERT | Yes | Yes | Yes | Yes
207 | Duct Bank | CompanyName | COMPANYNAME_DBANK | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
208 | Duct Bank | County | COUNTY_DBANK | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
209 | Duct Bank | CustomField:IsString | CUSTOMFIELDISSTRING_DBANK |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
210 | Duct Bank | CustomField:Name | CUSTOMFIELDNAME_DBANK |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
211 | Duct Bank | CustomField:Value | CUSTOMFIELDVALUE_DBANK |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
212 | Duct Bank | Id | ID_DBANK | Internals | Duct bank unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
213 | Duct Bank | LabelPlacement:CharacterRotation | LABELCHRROTATION_DBANK | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
214 | Duct Bank | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_DBANK | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
215 | Duct Bank | LabelPlacement:FontSize | LABELSIZE_DBANK | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
216 | Duct Bank | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_DBANK | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
217 | Duct Bank | LabelPlacement:GeometryType | LABELGEOMTYPE_DBANK | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
218 | Duct Bank | LabelPlacement:Rotation | LABELROT_DBANK | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
219 | Duct Bank | LabelPlacement:Text | LABELTEXT_DBANK | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
220 | Duct Bank | LabelPlacement:X | LABELX_DBANK | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
221 | Duct Bank | LabelPlacement:Y | LABELY_DBANK | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
222 | Duct Bank | LineN | LINEn_DBANK | Internals | Collection of lines in the duct bank (Line IDs). | String | #N/A | #N/A | OPS |  | Each line must be found in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
223 | Duct Bank | LocationDescription | LOCATIONDESCRIPTION_DBANK | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
224 | Duct Bank | Municipality | MUNICIPALITY_DBANK | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
225 | Duct Bank | Name | NAME_DBANK | Internals | Duct bank display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
226 | Duct Bank | PermitAreaId | PERMITAREAID_DBANK | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
227 | Duct Bank | State | STATE_DBANK | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
228 | Duct Bank | SymbolPlacement:GeometryLevel | GEOMLEVEL_DBANK | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
229 | Duct Bank | SymbolPlacement:GeometryType | GEOMTYPE_DBANK | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
230 | Duct Bank | SymbolPlacement:Vertex:X | WCXn_DBANK | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
231 | Duct Bank | SymbolPlacement:Vertex:X2 | WCX2n_DBANK | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
232 | Duct Bank | SymbolPlacement:Vertex:Y | WCYn_DBANK | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
233 | Duct Bank | SymbolPlacement:Vertex:Y2 | WCY2n_DBANK | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
234 | Duct Bank | ThirdPartyOwned | THIRDPARTYOWNED_DBANK | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
235 | Duct Bank | #N/A | NUMLINE_DBANK | Externals | The number of lines in the duct bank. | Integer | count | count | OPS |  |  | FALSE |  |  |  |  | NUMLINE | Yes | Yes | Yes | Yes
236 | Duct Bank | #N/A | NUMGEOM_DBANK | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
237 | Duct Bank | #N/A | NUMVERT_DBANK | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
238 | Duct Bank | #N/A | NUMLABELGEOM_DBANK | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
239 | Energy Resource | Address | ADDRESS_ENERGYRES | Internals | Energy resource address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
240 | Energy Resource | AggregationGroupName | AGGREGATIONGROUPNAME_ENERGYRES | Internals | Name of the associated aggregation group if the device is managed under an aggregation group. | String | #N/A | #N/A | OPS, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | AGGREGATIONGROUPNAME | Yes | Yes | Yes | Yes
241 | Energy Resource | AggregationManaged | AGGREGATIONMANAGED_ENERGYRES | Internals | Flag indicating that the device is managed under an aggregation group (true = managed in aggregation group). | Boolean | #N/A | #N/A | OPS, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | AGGREGATIONMANAGEDFLAG | Yes | Yes | Yes | Yes
242 | Energy Resource | AltName | ALTNAME_ENERGYRES | Internals | Energy resource alternate ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ALTNAME | Yes | Yes | Yes | Yes
243 | Energy Resource | AutomaticReconnectCapable | AUTOMATICRECONNECTCAPABLE_ENERGYRES | Internals | Flag indicating whether energy resource can automatically reconnect to the system when the system voltage is restored. | Boolean | #N/A | #N/A | OPS, DPF, FISR, LVM | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
244 | Energy Resource | AutomaticReconnectTimeDelay | AUTORECONNECTTIMEDELAY_ENERGYRES | Internals | Time delay that delays reconnection after the system voltage is restored if generator can automatically reconnect to the system when the system voltage is restored (seconds). | Float | #N/A | #N/A | OPS, DPF, FISR, LVM | 300 |  | FALSE | 0 | 10000 | 0 | 10000 | AUTORECONNECTTIMEDELAY | Yes | Yes | Yes | Yes
245 | Energy Resource | CommunicationId | COMMUNICATIONID_ENERGYRES | Internals | Communication ID | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COMMUNICATIONID | Yes | Yes | Yes | Yes
246 | Energy Resource | CompanyName | COMPANYNAME_ENERGYRES | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
247 | Energy Resource | ConnectionControl | CONNECTIONCONTROL_ENERGYRES | Internals | Flag indicating that the connection (connect/disconnect) status can be controlled. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONCONTROLFLAG | Yes | Yes | Yes | Yes
248 | Energy Resource | ConnectionType | CONTYPE_ENERGYRES | Internals | Generator connection type enumeration, allowed values: NotSet, Induction, DFIG, InverterCoupled | String |  |  | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | CONTYPE | Yes | Yes | Yes | Yes
249 | Energy Resource | ControlCapability | CONTROLCAP_ENERGYRES | Internals | Control type enumeration, allow values: NoControl, OnOffControl, P_OnOffControl, P_NoOnOffControl, Q_OnOffControl, Q_NoOnOffControl, PQ_OnOffControl, PQ_NoOnOffControl.This Field is being deprecated. | String |  | #N/A | OPS, DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONTROLCAP | Yes | Yes | Yes | Yes
250 | Energy Resource | County | COUNTY_ENERGYRES | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
251 | Energy Resource | CustomField:IsString | CUSTOMFIELDISSTRING_ENERGYRES |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
252 | Energy Resource | CustomField:Name | CUSTOMFIELDNAME_ENERGYRES |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
253 | Energy Resource | CustomField:Value | CUSTOMFIELDVALUE_ENERGYRES |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
254 | Energy Resource | DeviceType | DEVTYPE_ENERGYRES | Internals | Device Type enumeration, allowed values: Not,Set, Wind, Solar, Micro_Turbine, Fuel_Cell, Battery_Storage, Gas, Biomass, Others,Co_Gen, Hydro,Charging_Station | String |  |  | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | DEVTYPE | Yes | Yes | Yes | Yes
255 | Energy Resource | DSO Override | DSOOVER_ENERGYRES | Internals | Eligibility override of the normal rules for the advanced applications including Load and Volt/VAR Management (LVM). | Integer | #N/A | #N/A | OPS, LVM | 2 | 0: Not Set 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
256 | Energy Resource | EnergyRating | ENERGYRATING_ENERGYRES |  | The useable capacity of the storage device. | Double | kWh | kWh |  | 0 |  | STATE: ENERGYRATING; No: Yes; No: No; No: No; No: No
257 | Energy Resource | EnergyResourceModel | ENERGYRESMODEL_ENERGYRES | Internals | Associated energy resource model name (in the global resources file). | String | #N/A | #N/A | DPF |  | The energy resource model name must match an energy reource model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | ENERGYRESMODEL | Yes | Yes | Yes | Yes
258 | Energy Resource | EnergyResPrimSource | PRIMSOURCE_ENERGYRES | Internals | Flag indicating that energy resource is considered as primary source (True = Primary Source) | Boolean | #N/A | #N/A | DPF, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENERGYPRIMARYSOURCE | Yes | Yes | Yes | Yes
259 | Energy Resource | EnResGatewayEnabled | ENRESGATEWAYENABLED_ENERGYRES |  | Flag indicating device control type is 2030.5 Gateway. | Boolean | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | No
260 | Energy Resource | ExciteMode | EXCITEMODE_ENERGYRES | Internals | Excitation mode enumeration, allowed values: NotSet, ConstantV, ConstantQ, ConstantPF | String |  |  | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | EXITEMODE | Yes | Yes | Yes | Yes
261 | Energy Resource | FrequencyMaxSep | FREQUENCYMAXSEP_ENERGYRES | Internals | Maximum frequency before separation from the network (Hz). By default, 63 Hz. | Double | Hz | Hz | OPS | 63 |  | TRUE |  |  |  |  | FREQUENCYMAXSEP | Yes | Yes | Yes | Yes
262 | Energy Resource | FrequencyMinSep | FREQUENCYMINSEP_ENERGYRES | Internals | Minimum frequency before separation from the network (Hz). By default, 56 Hz. | Double | Hz | Hz | OPS | 56 |  | TRUE |  |  |  |  | FREQUENCYMINSEP | Yes | Yes | Yes | Yes
263 | Energy Resource | Future | FUTURE_ENERGYRES | Internals | Individual phases that are constructed but are not energized. | String | #N/A | #N/A | OPS | “” | Value should be blank or match the Phase field. | FALSE | #N/A | #N/A | #N/A | #N/A | FUTURE | Yes | Yes | Yes | Yes
264 | Energy Resource | GenType | PVTYPE_GEN | Internals | Flag indicating the generator is Real Power and Voltage type (PV) or Real Power and Reactive Power type (PQ) (True = PV, false = PQ). | Boolean | #N/A | #N/A | OPS, DPF |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GENTYPE | Yes | Yes | Yes | Yes
265 | Energy Resource | Grounded | GROUNDED_ENERGYRES | Internals | Flag indicating energy resource is grounded. | Boolean | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GROUNDED | Yes | Yes | Yes | Yes
266 | Energy Resource | Id | ID_ENERGYRES | Internals | Energy resource unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
267 | Energy Resource | KVA | KVA_ENERGYRES |  | Energy resource rating. | Float | kVA | kVA | DPF, LVM |  |  | TRUE: TRUE; ID: KVA; Yes: Yes; Yes: Yes; Yes: Yes
268 | Energy Resource | LabelPlacement:CharacterRotation | LABELCHRROTATION_ENERGYRES | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
269 | Energy Resource | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_ENERGYRES | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
270 | Energy Resource | LabelPlacement:FontSize | LABELSIZE_ENERGYRES | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE | 0 | 100 | 0 | 100 | SIZE | Yes | Yes | Yes | Yes
271 | Energy Resource | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_ENERGYRES | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
272 | Energy Resource | LabelPlacement:GeometryType | LABELGEOMTYPE_ENERGYRES | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
273 | Energy Resource | LabelPlacement:Rotation | LABELROT_ENERGYRES | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE | -360 | 360 | -360 | 360 | ROTATION | Yes | Yes | Yes | Yes
274 | Energy Resource | LabelPlacement:Text | LABELTEXT_ENERGYRES | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
275 | Energy Resource | LabelPlacement:X | LABELX_ENERGYRES | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | X | Yes | Yes | Yes | Yes
276 | Energy Resource | LabelPlacement:Y | LABELY_ENERGYRES | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y | Yes | Yes | Yes | Yes
277 | Energy Resource | LifeCycleStatus | LIFECYCLESTATUS_ENERGYRES | Internals | Life cycle status | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIFECYCLESTATUS | Yes | No | No | No
278 | Energy Resource | Load | LOAD_ENERGYRES | Internals | Associated load Id (optional, either the Node ID or Load ID must be provided).. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOAD | Yes | Yes | Yes | Yes
279 | Energy Resource | LocationDescription | LOCATIONDESCRIPTION_ENERGYRES | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
280 | Energy Resource | LVMControlType | LVMCONTROLTYPE | Internals | LVM control type value from enumeration | Integer | #N/A | #N/A | OPS, LVM | 2 | 0: Voltage control 1: VAR control 2: PF control | FALSE | 0 | 2 | 0 | 2 | LVMCONTROLTYPE | Yes | Yes | Yes | Yes
281 | Energy Resource | MaximumSOC | MAXIMUMSOC_ENERGYRES |  | The maximum state of charge (or nominal capacity), which is the maximum amount of charge that can be stored in the device. | Double | kWh | kWh |  | 0 |  | LOAD: MAXSOC; Yes: Yes; Yes: No; Yes: No; Yes: No
282 | Energy Resource | MinimumSOC | MINIMUMSOC_ENERGYRES |  | Charge level below which the device should never be drawn | Double | kWh | kWh |  | 0 |  | LOAD: MINSOC; Yes: Yes; Yes: No; Yes: No; Yes: No
283 | Energy Resource | Municipality | MUNICIPALITY_ENERGYRES | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
284 | Energy Resource | Name | NAME_ENERGYRES | Internals | Energy resource display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
285 | Energy Resource | Node | NODE_ENERGYRES | Internals | Associated node Id (optional, either the Node ID or Load ID must be provided). | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODEID | Yes | Yes | Yes | Yes
286 | Energy Resource | NomKV | NOMKV_ENERGYRES | Internals | Rated line to ground voltage (in kV). | Float | kV | kV | OPS |  |  | TRUE | 0.1 | 300 | 0.1 | 300 | NOMVOLT | Yes | Yes | Yes | Yes
287 | Energy Resource | NormallyDeenergized | NORMDEENERGIZED_ENERGYRES | Internals | Flag indicating that the energy resource is normally de-energized. | Boolean | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMDEENER | Yes | Yes | Yes | Yes
288 | Energy Resource | NumSCVoltageRanges | NUMSCVOLTAGERANGES_ENERGYRESMOD |  | The number of fault current levels | Integer |  |  | DPF |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
289 | Energy Resource | Ownership | OWNERSHIP_ENERGYRES | Internals | Ownership enumeration, allow values: Unspecified, CustomerOwnedMaintained, CustomerOwner_UtilityMaintained, UtilityOwnedMaintained. | String |  | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | OWNERSHIP | Yes | Yes | Yes | Yes
290 | Energy Resource | PermitAreaId | PERMITAREAID_ENERGYRES | Internals | Permission area ID (8-character maximum). | String | String | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
291 | Energy Resource | PgenMax | PGENMAX_ENERGYRES |  | Maximum real power output. | Float | kW | kW | DPF, LVM |  |  | FALSE: TRUE; NAME: PGENMAX; Yes: Yes; Yes: Yes; Yes: Yes
292 | Energy Resource | PgenMin | PGENMIN_ENERGYRES |  | Minimum real power output. | Float | kW | kW | DPF, LVM |  |  | FALSE: TRUE; NAME: PGENMIN; Yes: Yes; Yes: Yes; Yes: Yes
293 | Energy Resource | Phase | PHASE_ENERGYRES | Internals | Phase connection flag. | String | #N/A | #N/A | OPS |  | ABC, A, B, C, AB, BC, CA | FALSE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
294 | Energy Resource | Phasesense | PHASESENSE_ENERGYRES | Internals | The phases that are measured for controlling the unit. | String | #N/A | #N/A | DPF |  | ABC, A, B, C, AB, BC, CA | FALSE | #N/A | #N/A | #N/A | #N/A | PHSENSE | Yes | Yes | Yes | Yes
295 | Energy Resource | PlannedRestorationTime | RESTORETIME_ENERGYRES | Internals | Planned restoration time after re-energization of the feeder (seconds). | Integer | Seconds | Seconds | DPF | 0 |  | TRUE | 0 | 18000 | 0 | 18000 | PLANNEDRESTORATIONTIME | Yes | Yes | Yes | Yes
296 | Energy Resource | PowerSchedule | POWERSCH_ENERGYRES | Internals | Associated real power generation schedule name (in the global resources file). For battery, if the schedule point value is positivie, then it mean discharging values. If the schedule point is negative, then it means charging values. | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | PSCHED | Yes | Yes | Yes | Yes
297 | Energy Resource | ProgramEnrollment | PROGRAMENROLLMENT_ENERGYRES | Internals | Integer used for associating one or more program enrollments (represented with a 64 bit integer). Each program enrollment is represented by an integer bit (0/1 - 63), to correspond to an Energy Resource Program object defined in the global.csv file. | Integer64 | #N/A | #N/A | OPS | 0 | Multiple bits LSB 1 to 63 may be set, 0 represents "no program". | FALSE | 0 | 9,223,372,036,854,775,807 | 0 | 9,223,372,036,854,775,807 | PROGRAMENROLLMENT | Yes | No | No | No
298 | Energy Resource | QgenMax | QGENMAX_ENERGYRES |  | The maximum reactive power output. | Float | kVAR | kVAR | DPF, LVM |  |  | FALSE: TRUE; NAME: QGENMAX; Yes: Yes; Yes: Yes; Yes: Yes
299 | Energy Resource | QgenMin | QGENMIN_ENERGYRES |  | The minimum reactive power output. | Float | kVAR | kVAR | DPF, LVM |  |  | FALSE: TRUE; NAME: QGENMIN; Yes: Yes; Yes: Yes; Yes: Yes
300 | Energy Resource | ReactivePowerControl | REACTIVEPOWERCONTROL_ENERGYRES | Internals | Flag indicating that the reactive power output can be controlled. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | REACTIVEPOWERCONTROLFLAG | Yes | Yes | Yes | Yes
301 | Energy Resource | ReactivePowerSchedule | REACTIVEPOWERSCH_ENERGYRES | Internals | Associated reactive power generation schedule name (in the global resources file). | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | QSCHED | Yes | Yes | Yes | Yes
302 | Energy Resource | RealPowerControl | REALPOWERCONTROL_ENERGYRES | Internals | Flag indicating that the real power output can be controlled. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | REALPOWERCONTROLFLAG | Yes | Yes | Yes | Yes
303 | Energy Resource | RegNode | REGNODE_ENERGYRES | Internals | Regulation voltage node ID. | String | #N/A | #N/A | DPF, LVM |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | REGNODE | Yes | Yes | Yes | Yes
304 | Energy Resource | RGround | RGROUND_GEN | Internals | Resistance to ground (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | TRUE | 0 | 100 | 0 | 100 | RGROUND | Yes | Yes | Yes | Yes
305 | Energy Resource | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
306 | Energy Resource | ServiceCenter | SERVCNTR_ENERGYRES | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
307 | Energy Resource | State | STATE_ENERGYRES | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
308 | Energy Resource | SymbolPlacement:GeometryLevel | GEOMLEVEL_ENERGYRES | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
309 | Energy Resource | SymbolPlacement:GeometryType | GEOMTYPE_ENERGYRES | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
310 | Energy Resource | SymbolPlacement:Rotation | ROTATION_ENERGYRES | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE | -360 | 360 | -360 | 360 | ROTATION | Yes | Yes | Yes | Yes
311 | Energy Resource | SymbolPlacement:Size | SIZE_ENERGYRES | Internals | Size. | Integer | points | points | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | SIZE | Yes | Yes | Yes | Yes
312 | Energy Resource | SymbolPlacement:X | WCX_ENERGYRES | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | X | Yes | Yes | Yes | Yes
313 | Energy Resource | SymbolPlacement:X2 | WCX2_ENERGYRES | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | X2 | Yes | No | Yes | No
314 | Energy Resource | SymbolPlacement:Y | WCY_ENERGYRES | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | Y | Yes | Yes | Yes | Yes
315 | Energy Resource | SymbolPlacement:Y2 | WCY2_ENERGYRES | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | Y2 | Yes | No | Yes | No
316 | Energy Resource | ThirdPartyOwned | THIRDPARTYOWNED_ENERGYRES | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
317 | Energy Resource | VARSupport | VARSUPPORT_ENERGYRES | Internals | Flag indicating that the device can provide VAR support. | Boolean | #N/A | #N/A | OPS, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | VARSUPPORTFLAG | Yes | Yes | Yes | Yes
318 | Energy Resource | VmaxSep | VMAXSEP_ENERGYRES | Internals | Maximum voltage before separation from network (per unit or on a configurable voltage base depending on the flag set on the energy resource model). | Float | per unit or Volt | per unit or Volt | OPS |  |  | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VMAXSEP | Yes | Yes | Yes | Yes
319 | Energy Resource | VminSep | VMINSEP_ENERGYRES | Internals | Minimum voltage before separation from network (per unit or on a configurable voltage base depending on the flag set on the energy resource model). | Float | per unit or Volt | per unit or Volt | OPS |  |  | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VMINSEP | Yes | Yes | Yes | Yes
320 | Energy Resource | VoltageBase | VOLTAGEBASE_ENERGYRES |  | Voltage base value. | Float | V | V | DPF |  |  | TRUE |  |  |  |  | VOLTAGEBASE | Yes | Yes | Yes | Yes
321 | Energy Resource | VoltageSchedule | VOLTSCH_ENERGYRES | Internals | Associated voltage schedule name (in the global resources file). | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | VSCHED | Yes | Yes | Yes | Yes
322 | Energy Resource | VoltUnits | VOLTUNITS_ENERGYRES |  | Enumerated flag indicating the voltage units that should be used. The following values are supported: 1 = Per unit voltage, 2 = Actual voltage (on a user-configured voltage base specified in VoltageBase field) | Integer | enumeration | enumeration | DPF |  |  | TRUE |  |  |  |  | VOLTUNIT | Yes | Yes | Yes | Yes
323 | Energy Resource | VregLineline | VREGLINELINE_ENERGYRES | Internals | Flag that indicates whether the voltage for the regulated (sensed) phases is measured line to line or line to ground (True = line to line). | Boolean | #N/A | #N/A | DPF |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | VREGLL | Yes | Yes | Yes | Yes
324 | Energy Resource | XGround | XGROUND_GEN | Internals | Reactance to ground (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | TRUE | 0 | 100 | 0 | 100 | XGROUND | Yes | Yes | Yes | Yes
325 | Energy Resource | Yconnected (Deprecated) | WYECONN_ENERGYRES | Internals | Flag indicating energy resource is wye connected. Deprecated functionality. Only wye connection is supported for DER. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | WYE | Yes | Yes | Yes | Yes
326 | Energy Resource | #N/A | NUMGEOM_ENERGYRES | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
327 | Energy Resource | #N/A | NUMLABELGEOM_ENERGYRES | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
328 | Fault Detector | Address | ADDRESS_FDTECT | Internals | Fault detector address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
329 | Fault Detector | AmpRate | AMPRATE_FDTECT | Internals | Fault detector rating (amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 1500 | 0 | 1500 | AMPRATE | Yes | Yes | Yes | Yes
330 | Fault Detector | BackupType | BACKTYPE_FDTECT | Internals | Enumeration indicating device backup mechanism type. The following values are used: 1 = Battery, 2 = Super_Capacitor. | Integer | #N/A | #N/A | OPS |  | 1: Battery backed 2: Super capacitor backed | FALSE | 1 | 2 | 1 | 2 | BACKUPTYPE | Yes | Yes | Yes | Yes
331 | Fault Detector | CompanyName | COMPANYNAME_FDTECT | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
332 | Fault Detector | County | COUNTY_FDTECT | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
333 | Fault Detector | CustomField:IsString | CUSTOMFIELDISSTRING_FDTECT |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
334 | Fault Detector | CustomField:Name | CUSTOMFIELDNAME_FDTECT |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
335 | Fault Detector | CustomField:Value | CUSTOMFIELDVALUE_FDTECT |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
336 | Fault Detector | Directional | DIRECTIONAL_FDTECT | Internals | Flag indicates if the device is a directional Fault Detector (True = directional). | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | DIRECTIONAL | Yes | Yes | Yes | Yes
337 | Fault Detector | DirectionalType | DIRECTIONALTYPE_FDTECT | Internals | For directional fault detectors, the type of directional : 1: bus vs cable side; 2: forward and reverse direction. | String | #N/A | #N/A | OPS | 2 |  | FALSE | #N/A | #N/A | #N/A | #N/A | DIRECTIONALTYPE | Yes | Yes | Yes | Yes
338 | Fault Detector | EmsFile | EMSFILE | Internals | A flag indicating that the fault indicator is on the station internals view | Boolean | #N/A | #N/A | OPS | 2 |  | FALSE | #N/A | #N/A | #N/A | #N/A | EMSFILE | Yes | No | No | No
339 | Fault Detector | ExternalId | EXTERNALID_FDTECT | Internals | External Id of the Fault Detector. This information currently is not used by the DMS Applications. It is provided for use by any other application that might use the source data. | String | #N/A | #N/A | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
340 | Fault Detector | Future | FUTURE_FDTECT | Internals | Individual phases that are constructed but are not energized. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | FUTURE | Yes | Yes | Yes | Yes
341 | Fault Detector | Id | ID_FDTECT | Internals | Fault detector unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
342 | Fault Detector | LabelPlacement:CharacterRotation | LABELCHRROTATION_FDTECT | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
343 | Fault Detector | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_FDTECT | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
344 | Fault Detector | LabelPlacement:FontSize | LABELSIZE_FDTECT | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
345 | Fault Detector | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_FDTECT | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
346 | Fault Detector | LabelPlacement:GeometryType | LABELGEOMTYPE_FDTECT | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
347 | Fault Detector | LabelPlacement:Rotation | LABELROT_FDTECT | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
348 | Fault Detector | LabelPlacement:Text | LABELTEXT_FDTECT | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | count | count | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
349 | Fault Detector | LabelPlacement:X | LABELX_FDTECT | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
350 | Fault Detector | LabelPlacement:Y | LABELY_FDTECT | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
351 | Fault Detector | LocationDescription | LOCATIONDESCRIPTION_FDTECT | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
352 | Fault Detector | Municipality | MUNICIPALITY_FDTECT | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
353 | Fault Detector | Name | NAME_FDTECT | Internals | Fault detector display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
354 | Fault Detector | Node | NODE_FDTECT | Internals | Associated node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODE | Yes | Yes | Yes | Yes
355 | Fault Detector | NOMINAL_FEEDER_ID_FDTECT | NOMINAL_FEEDER_ID_FDTECT | Internals | Nominal feeder ID for the fault detector This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for fault indicators marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
356 | Fault Detector | PermitAreaId | PERMITAREAID_FDTECT | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
357 | Fault Detector | Phase | PHASE_FDTECT | Internals | Fault detector phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | FAULTINDPHASING | Yes | Yes | Yes | Yes
358 | Fault Detector | PhaseAgnosticFaultIndication | PHASEAGNOSTICFAULTINDICATION_FDTECT | Internals | Fault indicator's awareness about the faulted phase. If not defined the default value is false. Default value false indicates that fault indicator knows about the phase, during the fault. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PHASEAGNOSTICFAULTINDICATION | Yes | Yes | No | No
359 | Fault Detector | ResetType | RESETTYPE_FDTECT | Internals | Enumeration indicating device reset mechanism type. The following values are used: 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer | enumeration | enumeration | OPS |  | 1: Automatic 2: Manual 3: Remote 4: Arc suppression coil | FALSE | 1 | 4 | 1 | 4 | ENUMTYPE | Yes | Yes | Yes | Yes
360 | Fault Detector | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
361 | Fault Detector | ServiceCenter | SERVCNTR_FDTECT | Internals | Associated service center. | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
362 | Fault Detector | Side1BranchId | SIDE1BRANCHID_FDTECT | Internals | For directional fault detectors. If directional type is 1, it is the ID of the bus side or the cable side device. If directional type is 2, it is the ID of the conncected branch so that if a fault is at that branch, the fault indicator will be set as forward. Normally, it is the branch downstream of the fault indicator. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SIDE1BRANCHID | Yes | Yes | Yes | Yes
363 | Fault Detector | Side1BranchType | SIDE1BRANCHTYPE_FDTECT | Internals | For directional fault detectors, the DNOM branch object type of the bus side or the cable side device. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SIDE1BRANCHTYPE | Yes | Yes | Yes | Yes
364 | Fault Detector | State | STATE_FDTECT | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
365 | Fault Detector | SymbolPlacement:GeometryLevel | GEOMLEVEL_FDTECT | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
366 | Fault Detector | SymbolPlacement:GeometryType | GEOMTYPE_FDTECT | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
367 | Fault Detector | SymbolPlacement:Rotation | ROTATION_FDTECT | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
368 | Fault Detector | SymbolPlacement:Size | SIZE_FDTECT | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
369 | Fault Detector | SymbolPlacement:X | WCX_FDTECT | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
370 | Fault Detector | SymbolPlacement:X2 | WCX2_FDTECT | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
371 | Fault Detector | SymbolPlacement:Y | WCY_FDTECT | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
372 | Fault Detector | SymbolPlacement:Y2 | WCY2_FDTECT | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
373 | Fault Detector | Telemetered | TELEMETERED_FDTECT | Internals | If not defined, the default value is False, meaning the device is not telemetered in SCADA. This information currently is not used by the DMS applications. It is provided for use by any other application that might use the source data. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE |  |  |  |  | TELEMETEREDFAULTIND | Yes | Yes | Yes | Yes
374 | Fault Detector | ThirdPartyOwned | THIRDPARTYOWNED_FDTECT | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
375 | Fault Detector | TimeDelay | TIMEDELAY_FDTECT | Internals | Time delay (seconds) for telemetered device to put scada quality on "suspect". Global parameter value from server config will be considered if this value is set to "0"and backup type enum is set to super capacitor. | Integer | seconds | seconds | OPS |  |  | FALSE | 0 | 3600 | 0 | 3600 | TMDELAY | Yes | Yes | Yes | Yes
376 | Fault Detector | #N/A | NUMGEOM_FDTECT | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
377 | Fault Detector | #N/A | NUMLABELGEOM_FDTECT | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
378 | Feeder | Address | ADDRESS_FEEDER | Internals | Feeder address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
379 | Feeder | AlternateName | ALTNAME_FEEDER | Internals | Alternate name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ALTERNATENAME | Yes | Yes | Yes | Yes
380 | Feeder | AppHeadBreaker | APPBREAKER_FEEDER | Internals | Specified feeder head breaker. It is optional. When the feeder breaker is defined above feeder head node, normally this CB does not have feeder assigned. To fix this, you could explicitly specify this field as static feeder breaker. The internal topology process function will solve from this switching device, and a nominal feeder will be assigned. | String | #N/A | #N/A | DPF, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FDRBREAKERNAME or NOMINALBREAKER | Yes | Yes | Yes | Yes
381 | Feeder | CompanyName | COMPANYNAME_FEEDER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
382 | Feeder | County | COUNTY_FEEDER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTLY | No | No | No | No
383 | Feeder | DefColor | DEFCOLOR_FEEDER | Internals | Default feeder color (integer from 1–24). Refer to the section describing Feeder Colors in the ADMS Modeling Reference Guide. | Integer | #N/A | #N/A | OPS |  |  | TRUE | 1 | 24 | 1 | 24 | DEFCOLOR | Yes | Yes | Yes | Yes
384 | Feeder | FRP | FRP_FEEDER | Internals | Feeder Restoration Priority (FRP). This is a fixed value, which defines the order in which feeder lockouts should be addressed mainly during times of severe weather. Feeders with lower FRP have higher restoration priority. | Integer | #N/A | #N/A |  | 0 |  | FALSE |  |  |  |  | FRP | No | No | No | No
385 | Feeder | Id | ID_FEEDER | Internals | Feeder unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
386 | Feeder | IsPrimaryFeeder | ISPRIMARY_FEEDER | Internals | Flag to indicate if this feeder is a primary feeder or secondary feeder (True = primary). | Boolean | #N/A | #N/A | OPS | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISPRIMFDR | Yes | Yes | Yes | Yes
387 | Feeder | LabelPlacement:CharacterRotation | LABELCHRROTATION_FEEDER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
388 | Feeder | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_FEEDER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
389 | Feeder | LabelPlacement:FontSize | LABELSIZE_FEEDER | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
390 | Feeder | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_FEEDER | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
391 | Feeder | LabelPlacement:GeometryType | LABELGEOMTYPE_FEEDER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
392 | Feeder | LabelPlacement:Rotation | LABELROT_FEEDER | Internals | Label rotation angle. | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
393 | Feeder | LabelPlacement:Text | LABELTEXT_FEEDER | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
394 | Feeder | LabelPlacement:X | LABELX_FEEDER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. Modeling the feeder label placement in the internals file for the primary geometry also works. | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
395 | Feeder | LabelPlacement:Y | LABELY_FEEDER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. Modeling the feeder label placement in the internals file for the primary geometry also works. | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
396 | Feeder | LoadShedDefaultCircuitClass | LSDEFCLASS_FEEDER | Internals | Feeder (circuit) level load shed classification. | Integer | #N/A | #N/A | SLS | 10 | 0: Ignore 1: Do Not Shed 2-10: Circuit Classification | FALSE | 0 | 100 | 0 | 100 | LOADSHEDDEFCLASS | Yes | Yes | Yes | Yes
397 | Feeder | LocationDescription | LOCATIONDESCRIPTION_FEEDER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
398 | Feeder | MaxUnCtrlCapacitors | MAXUNCTRLCAPACITORS_FEEDER | Internals | Maximum number of uncontrollable capacitors. If the LVM automatic disabling feature is enabled, and the number of uncontrollable capacitors on the feeder exceeds this limit, then the feeder is disabled for that LVM execution. | Integer | #N/A | #N/A | DPF, LVM | -1 |  | FALSE | -1 | 20 | -1 | 20 | MAXUNCTRLCAPACITORS | Yes | Yes | Yes | Yes
399 | Feeder | MaxUnCtrlTapChangers | MAXUNCTRLTAPS_FEEDER | Internals | Maximum number of uncontrollable regulating transformers (Load Tap Changers, or LTCs, and regulators). If the LVM automatic disabling feature is enabled, and the number of uncontrollable regulators/LTCs on the feeder exceeds this limit, then the feeder is disabled for that LVM execution. | Integer | #N/A | #N/A | DPF, LVM | -1 |  | FALSE | -1 | 20 | -1 | 20 | MAXUNCTRLTAPS | Yes | Yes | Yes | Yes
400 | Feeder | Municipality | MUNICIPALITY_FEEDER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
401 | Feeder | Name | NAME_FEEDER | Internals | Feeder display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
402 | Feeder | Node | NODE_FEEDER | Internals | Feeder head node Id. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | HEADNODE.NAME | Yes | Yes | Yes | Yes
403 | Feeder | NomKV | NOMKV_FEEDER | Internals | Nominal feeder voltage level (kV). | Float | kV | kV | DPF |  |  | TRUE | 0.1 | 80 | 0.1 | 80 | VOLTAGE | Yes | Yes | Yes | Yes
404 | Feeder | PeakflowA | PEAKFLOWA_FEEDER | Internals | Feeder phase A peak flow in Amps. This value is used for the BLA/DPF validation inside the Converter. If this value is not defined, Converter uses the feeder breaker phase trip value (in Amps multiplied by the value in the Percentage of Phase Relay parameter). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 1000 | 0 | 1000 |  | Yes | Yes | Yes | Yes
405 | Feeder | PeakflowB | PEAKFLOWB_FEEDER | Internals | Feeder phase B peak flow in Amps. This value is used for the BLA/DPF validation inside the Converter. If this value is not defined, Converter uses the feeder breaker phase trip value (in Amps multiplied by the value in the Percentage of Phase Relay parameter). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 1000 | 0 | 1000 |  | Yes | Yes | Yes | Yes
406 | Feeder | PeakflowC | PEAKFLOWC_FEEDER | Internals | Feeder phase C peak flow in Amps. This value is used for the BLA/DPF validation inside the Converter. If this value is not defined, Converter uses the feeder breaker phase trip value (in Amps multiplied by the value in the Percentage of Phase Relay parameter). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 1000 | 0 | 1000 |  | Yes | Yes | Yes | Yes
407 | Feeder | PermitAreaId | PERMITAREAID_FEEDER | Internals | Permission area ID (8 character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
408 | Feeder | ProbFormuIndex | PROBFORMUINDEX_FEEDER | Internals | Number of LVM problem formulation in feeder REMOVE SOON | Integer | #N/A | #N/A | DPF, LVM | -1 |  | FALSE | -1 | 200 | -1 | 200 | LVMPROFORMINDEX | Yes | Yes | Yes | Yes
409 | Feeder | PRVEvaluation | PRVEVALUATION_FEEDER | Internals | Specifies the fault impedance evaluation type that is applied by the PRV application (NotSet = 0, BoltedFault = 1) | Integer | #N/A | #N/A | PRV | 0 | 0 : NotSet 1: Bolted Fault | FALSE | #N/A | #N/A | #N/A | #N/A | PRVEVALUATION | Yes | No | No | No
410 | Feeder | ScadaBreakerId |  | Internals | Id of breaker in SCADA that supplies the Feeder | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
411 | Feeder | ServiceCenter | SERVCNTR_FEEDER | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
412 | Feeder | State | STATE_FEEDER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
413 | Feeder | TargetPfSched | TARGETPF_FEEDER | Internals | Associated target power factor schedule name. | String | #N/A | #N/A | DPF |  | The target power factor schedule name must match a schedule given in the global resources file. (Optional for LVM application.) | FALSE | #N/A | #N/A | #N/A | #N/A | TARGETPF | Yes | Yes | Yes | Yes
414 | Feeder | ThirdPartyOwned | THIRDPARTYOWNED_FEEDER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
415 | Feeder | VoltFlattenLimit | VOLTFLATTENLIMIT_FEEDER | Internals | Voltage flattening limit. It is expressed as a percentage of the voltage base. For example, if the voltage flattening threshold is 1% and the voltage base is 120V, the voltage flattening threshold is 1.2V. For voltage flattening to be applied in the Heuristic LVM Capacitor Control function, the lowest estimated voltage from all telemetered points subtracted from the average estimated voltage from all telemetered points must be greater than this value. | Float | #N/A | % | DPF, LVM | 0.01 |  | FALSE | 0 | 10 | 0 | 10 | VOLTFLATTENLIMIT | Yes | Yes | Yes | Yes
416 | Feeder | #N/A | NUMLABELGEOM_FEEDER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
417 | Feeder | IsTapFeeder | ISTAP_FEEDER | Internals | Flag to indicate if this feeder is a tap feeder (True = tap feeder). Tap feeders start downstream of a primary feeder in the externals instead of inside a substation. This field is mainly used as a check for tracing functionality. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
418 | Feeder Block Trace Point | CompanyName | COMPANYNAME_DEVICE | Internals | Name of the company that is associated with the component (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
419 | Feeder Block Trace Point | County |  | Internals | The name of the associated county (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
420 | Feeder Block Trace Point | Feeder1 |  | Internals | ID of the nominal feeder of the feeder block (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
421 | Feeder Block Trace Point | Id |  | Internals | Feeder block unique Id | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
422 | Feeder Block Trace Point | LocationDescription |  | Internals | Information about the device location (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
423 | Feeder Block Trace Point | Municipality |  | Internals | The name of the associated municipality (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
424 | Feeder Block Trace Point | Name |  | Internals | Feeder block display name | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
425 | Feeder Block Trace Point | NodeId |  | Internals | Associated node Id | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
426 | Feeder Block Trace Point | PermitAreaId |  | Internals | Permission area ID (8 character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
427 | Feeder Block Trace Point | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
428 | Feeder Block Trace Point | State |  | Internals | The name of the associated state (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
429 | Feeder Block Trace Point | ThirdPartyOwned |  | Internals | Specifies whether a third-party company owns the component (not used for component) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
430 | Flagged Data | CompanyName | COMPANYNAME_DEVICE | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
431 | Flagged Data | ConnectedFeeder | CONNECTED_FEEDER |  | Connected Feeder | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
432 | Flagged Data | County | COUNTY_DEVICE | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
433 | Flagged Data | CustomField:IsString |  |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
434 | Flagged Data | CustomField:Name |  |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
435 | Flagged Data | CustomField:Value |  |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
436 | Flagged Data | DMSAttributeName | DMS_ATTRIBUTE_NAME |  | DMS attribute name | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
437 | Flagged Data | GISAttributeName | GIS_ATTRIBUTE_NAME |  | GIS Attribute name | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
438 | Flagged Data | GISDeviceType | TYPE_DEVICE |  | GIS device type | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
439 | Flagged Data | GivenValue | GIVEN_VALUE |  | Given value | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
440 | Flagged Data | Id | ID_DEVICE |  | ID | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
441 | Flagged Data | LocationDescription | LOCATIONDESCRIPTION_DEVICE | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
442 | Flagged Data | Municipality | MUNICIPALITY_DEVICE | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
443 | Flagged Data | Name | NAME_DEVICE |  | Name | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
444 | Flagged Data | RelatedObjectId | ID_RELATEDOBJECT |  | Related object ID | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
445 | Flagged Data | ReplacementValue | REPLACEMENT_VALUE |  | Replacement value | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
446 | Flagged Data | State | STATE_DEVICE | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
447 | Flagged Data | ThirdPartyOwned | THIRDPARTYOWNED_DEVICE | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
448 | Fuse | Address | ADDRESS_FUSE | Internals | Fuse address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
449 | Fuse | CompanyName | COMPANYNAME_FUSE | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
450 | Fuse | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID (for station internal devices only). | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
451 | Fuse | ComputeFlows | COMPUTEFLOWS_FUSE | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS, DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
452 | Fuse | County | COUNTY_FUSE | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
453 | Fuse | DSOOverride | DSOOVER_FUSE | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: Not Set 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
454 | Fuse | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_FUSE | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
455 | Fuse | ExternalInterfaceMember | EXTERNALINTERFACE_FUSE | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
456 | Fuse | FeedMainBound | FEEDMAINBOUND_FUSE | Externals | Flag indicating that the fuse is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS, NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
457 | Fuse | FromNode | FRNODE_FUSE | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
458 | Fuse | Future | FUTURE_FUSE | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
459 | Fuse | Id | ID_FUSE | Internals | Fuse unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
460 | Fuse | IncidentEnergyCat | INCIDENTENGCAT_FUSE | Internals | Fuse incident energy category. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENERGYCAT.NOAPPSTR | Yes | Yes | Yes | Yes
461 | Fuse | LabelPlacement:CharacterRotation | LABELCHRROTATION_FUSE | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
462 | Fuse | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_FUSE | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
463 | Fuse | LabelPlacement:FontSize | LABELSIZE_FUSE | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
464 | Fuse | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_FUSE | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
465 | Fuse | LabelPlacement:GeometryType | LABELGEOMTYPE_FUSE | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
466 | Fuse | LabelPlacement:Rotation | LABELROT_FUSE | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
467 | Fuse | LabelPlacement:Text | LABELTEXT_FUSE | Internals | Label Geometry Text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
468 | Fuse | LabelPlacement:X | LABELX_FUSE | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
469 | Fuse | LabelPlacement:Y | LABELY_FUSE | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
470 | Fuse | LocationDescription | LOCATIONDESCRIPTION_FUSE | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
471 | Fuse | Municipality | MUNICIPALITY_FUSE | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
472 | Fuse | Name | NAME_FUSE | Internals | Fuse display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
473 | Fuse | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_FUSE | Internals | Nominal feeder ID for the breaker. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for fuses marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
474 | Fuse | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
475 | Fuse | NormallyDeenergized | NORMDEENERGIZED_FUSE | Internals | Flag indicating that the fuse is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
476 | Fuse | NormallyLooped | NORMLOOPED_FUSE | Internals | Flag indicating that the fuse is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
477 | Fuse | NormallyNetworkLooped | NORMNETWORKLOOPED_FUSE | Internals | Flag indicating that the fuse is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
478 | Fuse | NormallyOpen | NOPEN_FUSE | Internals | Flag indicating the fuse is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | Not applicable | Not applicable | OPS, NTP, DPF |  |  | FALSE | Not applicable | Not applicable | Not applicable | Not applicable | NOPEN | Yes | Yes | Yes | Yes
479 | Fuse | NormallyParallelLooped | NORMPARALLELLOOPED_FUSE | Internals | Flag indicating that the fuse is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
480 | Fuse | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched fuses that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_FUSE field. | String | Not applicable | Not applicable | OPS, NTP, DPF |  | A, B, C, AB, BC, CA, ABC. | FALSE | Not applicable | Not applicable | Not applicable | Not applicable | NORMOPENPHASES | Yes | Yes | Yes | Yes
481 | Fuse | PermitAreaId | PERMITAREAID_FUSE | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
482 | Fuse | Phase | PHASE_FUSE | Internals | Fuse phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
483 | Fuse | PRVAppAreaBoundary | PRVAPPAREABOUNDARY_FUSE | Internals | This flag helps to know if fuse is a boundary in determining adaptive relaying Protection Validation (PRV) application zone. | Boolean | #N/A | #N/A | OPS | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A | PRVAPPBOUNDARY | Yes | Yes | No | No
484 | Fuse | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
485 | Fuse | SecondId | TROUBLECALLID_FUSE | Internals | Alternate switch ID. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
486 | Fuse | ServiceCenter | SERVCNTR_FUSE | Internals | Associated service center. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
487 | Fuse | SolidBlade | SOLIDBLADE_FUSE | Internals | Flag indicating if this device is a solid blade fuse (True = solid blade). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SOLIDBLADEFUSE | Yes | Yes | Yes | Yes
488 | Fuse | State | STATE_FUSE | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
489 | Fuse | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
490 | Fuse | SuppressFeeder |  | Internals | Flag indicating that the fuse name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
491 | Fuse | SwitchModel | SWMOD_FUSE | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
492 | Fuse | SwitchModelPhA | SWMODA_FUSE | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
493 | Fuse | SwitchModelPhB | SWMODB_FUSE | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
494 | Fuse | SwitchModelPhC | SWMODC_FUSE | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
495 | Fuse | SymbolPlacement:GeometryLevel | GEOMLEVEL_FUSE | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
496 | Fuse | SymbolPlacement:GeometryType | GEOMTYPE_FUSE | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
497 | Fuse | SymbolPlacement:Rotation | ROTATION_FUSE | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | SWPLACE.ROTATION | Yes | Yes | Yes | Yes
498 | Fuse | SymbolPlacement:Size | SIZE_FUSE | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SWPLACE.SIZE | Yes | Yes | Yes | Yes
499 | Fuse | SymbolPlacement:X | WCX_FUSE | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X | Yes | Yes | Yes | Yes
500 | Fuse | SymbolPlacement:X2 | WCX2_FUSE | Internals | 2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X2 | Yes | No | Yes | No
501 | Fuse | SymbolPlacement:Y | WCY_FUSE | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y | Yes | Yes | Yes | Yes
502 | Fuse | SymbolPlacement:Y2 | WCY2_FUSE | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y2 | Yes | No | Yes | No
503 | Fuse | ThirdPartyOwned | THIRDPARTYOWNED_FUSE | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
504 | Fuse | ToNode | TONODE_FUSE | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
505 | Fuse | ToStation | TOSUB_FUSE | Internals | Associated external substation name. This field should only be set if the fuse connects two substations together. | String | #N/A | #N/A | OPS, NTP, DPF |  | The station name is checked against the stations list read from the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
506 | Fuse | UrdLoopChecked | URDCHECKED_FUSE | Internals | Flag indicating that the associated URD loop has been checked. | Boolean | #N/A | #N/A | OPS, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
507 | Fuse | #N/A | NUMGEOM_FUSE | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
508 | Fuse | #N/A | NUMLABELGEOM_FUSE | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
509 | Fuse | BusTieSwitch | BUSTIESWITCH_FUSE | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
510 | Generator | Address | ADDRESS_GEN | Internals | Generator address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
511 | Generator | AutomaticReconnectCapable | AUTOMATICRECONNECTCAPABLE_GEN | Internals | Flag indicating whether generator can automatically reconnect to the system when the system voltage is restored. | Boolean | #N/A | #N/A | OPS, DPF, FISR | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
512 | Generator | AutomaticReconnectTimeDelay | AUTORECONNECTTIMEDELAY_GEN | Internals | Time delay that delays reconnection after the system voltage is restored if generator can automatically reconnect to the system when the system voltage is restored (seconds). | Float | #N/A | #N/A | OPS, DPF, FISR | 300 |  | FALSE | 0 | 10000 | 0 | 10000 | AUTORECONNECTTIMEDELAY | Yes | Yes | Yes | Yes
513 | Generator | CompanyName | COMPANYNAME_GEN | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
514 | Generator | County | COUNTY_GEN | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
515 | Generator | CustomField:IsString | CUSTOMFIELDISSTRING_GEN |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
516 | Generator | CustomField:Name | CUSTOMFIELDNAME_GEN |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
517 | Generator | CustomField:Value | CUSTOMFIELDVALUE_GEN |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
518 | Generator | DeviceType | DEVTYPE_GEN | Internals | Device type enumeration (Not_Set = 0, Co_Gen = 1, Wind = 2, Solar = 3, Micro_Turbine = 4, Fuel_Cell = 5, Battery_Storage = 6, Gas = 7, Biomass = 8, Hydro = 9, Others = 10). | Integer | enumeration | enumeration | OPS | Co-Generator by default | 0: Not Set 1: Co_generator 2: Wind 3: Solar (PV) 4: Micro-Turbine 5: Fuel Cell 6: Battery Storage 7: Gas 8: Biomass 9: Hydro 10: Others | FALSE | 0 | 10 | 0 | 10 | GDEVTYPE | Yes | Yes | Yes | Yes
519 | Generator | DSO Override | DSOOVER_GEN | Internals | Eligibility override of the normal rules for the advanced applications. | Integer | #N/A | #N/A | OPS | 2 | 0: Not Set 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
520 | Generator | FrequencyMaxSep | FREQUENCYMAXSEP_GEN | Internals | Maximum frequency before separation from the network (Hz). By default, 63 Hz. | Double | Hz | Hz | OPS | 63 |  | TRUE |  |  |  |  | FREQUENCYMAXSEP | Yes | Yes | Yes | Yes
521 | Generator | FrequencyMinSep | FREQUENCYMINSEP_GEN | Internals | Minimum frequency before separation from the network (Hz). By default, 56 Hz. | Double | Hz | Hz | OPS | 56 |  | TRUE |  |  |  |  | FREQUENCYMINSEP | Yes | Yes | Yes | Yes
522 | Generator | Future | FUTURE_GEN | Internals | Individual phases that are constructed but not energized.. | String | #N/A | #N/A | OPS | “” | ABC or blank. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
523 | Generator | GeneratorModel | GENMODEL_GEN | Internals | Associated generator model name (in the global resources file). | String | #N/A | #N/A | DPF |  | The generator model name must match a generator model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | GENMODEL.NAME | Yes | Yes | Yes | Yes
524 | Generator | GenPrimSource | PRIMSOURCE_GEN | Internals | Flag indicating the generator is considered a primary source (True = A primary energization source). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
525 | Generator | GenType | PVTYPE_GEN | Internals | Flag indicating the generator is Real Power and Voltage type (PV) or Real Power and Reactive Power type (PQ) (True = PV, false = PQ). | Boolean | #N/A | #N/A | OPS, DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GENTYPE | Yes | Yes | Yes | Yes
526 | Generator | Grounded | GROUNDED_GEN | Internals | Flag indicating generator is grounded (True = grounded). | String | #N/A | #N/A | OPS | User-configurable through Defaults File |  | TRUE | #N/A | #N/A | #N/A | #N/A | GROUNDED | Yes | Yes | Yes | Yes
527 | Generator | Id | ID_GEN | Internals | Generator unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
528 | Generator | KVA | KVA_GEN |  | Generator rating. | Float | kVA | kVA | DPF, LVM |  |  | TRUE |  |  |  |  | KVA | Yes | Yes | Yes | Yes
529 | Generator | LabelPlacement:CharacterRotation | LABELCHRROTATION_GEN | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
530 | Generator | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_GEN | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
531 | Generator | LabelPlacement:FontSize | LABELSIZE_GEN | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
532 | Generator | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_GEN | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
533 | Generator | LabelPlacement:GeometryType | LABELGEOMTYPE_GEN | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
534 | Generator | LabelPlacement:Rotation | LABELROT_GEN | Internals | Label rotation angle. | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
535 | Generator | LabelPlacement:Text | LABELTEXT_GEN | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
536 | Generator | LabelPlacement:X | LABELX_GEN | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
537 | Generator | LabelPlacement:Y | LABELY_GEN | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
538 | Generator | LocationDescription | LOCATIONDESCRIPTION_GEN | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
539 | Generator | LVMControlType |  | Internals | LVM control type value from enumeration | Integer | #N/A | #N/A | OPS, LVM | 2 | 0: Voltage control 1: VAR control 2: PF control | FALSE | 0 | 2 | 0 | 2 | LVMCONTROLTYPE | Yes | Yes | Yes | Yes
540 | Generator | Municipality | MUNICIPALITY_GEN | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
541 | Generator | Name | NAME_GEN | Internals | Generator display name. | String | kV | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
542 | Generator | Node | NODE_GEN | Internals | Associated node name. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODEID | Yes | Yes | Yes | Yes
543 | Generator | NOMINAL_FEEDER_ID_GEN | NOMINAL_FEEDER_ID_GENERATOR | Internals | Nominal feeder ID for the generator. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for permanent jumpers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
544 | Generator | NomKV | NOMKV_GEN | Internals | Rated voltage (kV). | Float | kV | kV | OPS |  |  | TRUE | 0.1 | 500 | 0.1 | 500 | NOMVOLT | Yes | Yes | Yes | Yes
545 | Generator | NormallyDeenergized | NORMDEENERGIZED_GEN | Internals | Flag indicating that the generator is normally de-energized. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
546 | Generator | PermitAreaId | PERMITAREAID_GEN | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
547 | Generator | PgenMax | PGENMAX_GEN |  | The maximum real power output. | Float | kW | kW | DPF, LVM |  |  | TRUE |  |  |  |  | PGENMAX | Yes | Yes | Yes | Yes
548 | Generator | PgenMin | PGENMIN_GEN |  | The minimum real power output. | Float | kW | kW | DPF, LVM |  |  | TRUE |  |  |  |  | PGENMIN | Yes | Yes | Yes | Yes
549 | Generator | Phase | PHASE_GEN | Internals | Phase connection flag – all generators are always three-phase. | String | #N/A | #N/A | OPS | “ABC” |  | FALSE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
550 | Generator | Phasesense | PHASESENSE_GEN | Internals | The phases that are measured for controlling the unit. | String | #N/A | #N/A | DPF |  | ABC, AB, BC, CA, A, B, or C. | FALSE | #N/A | #N/A | #N/A | #N/A | GENPHASESENSED | Yes | Yes | Yes | Yes
551 | Generator | PlannedRestorationTime | RESTORETIME_GEN | Internals | Planned restoration time after re-energization of the feeder (seconds). | Integer | Seconds | Seconds | DPF, FISR | 0 |  | TRUE | 0 | 18000 | 0 | 18000 | PLANNEDRESTORATIONTIME | Yes | Yes | Yes | Yes
552 | Generator | PowerSchedule | POWERSCH_GEN | Internals | Associated real power generation scheduled name (in the global resources file). | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | RPOWSCHD.NAME | Yes | Yes | Yes | Yes
553 | Generator | QgenMax | QGENMAX_GEN |  | The maximum reactive power output. | Float | kVAR | kVAR | DPF, LVM |  |  | TRUE |  |  |  |  | QGENMAX | Yes | Yes | Yes | Yes
554 | Generator | QgenMin | QGENMIN_GEN |  | The minimum reactive power output. | Float | kVAR | kVAR | DPF, LVM |  |  | TRUE |  |  |  |  | QGENMIN | Yes | Yes | Yes | Yes
555 | Generator | RatedAmps | RATEDAMPS_GENMOD |  | Rated stator current. | Float | Amps | Amps | DPF |  |  | FALSE |  |  |  |  | RATEDAMPS | Yes | Yes | Yes | Yes
556 | Generator | RatedPF | RATEDPF_GENMOD |  | Rated power factor. | Float | units | units | DPF |  |  | FALSE |  |  |  |  | RATEDPF | Yes | Yes | Yes | Yes
557 | Generator | ReactivePowerSchedule | REACTIVEPOWERSCH_GEN | Internals | Associated reactive power generation schedule name (in the global resources file). | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | REACPOWSCHD.NAME | Yes | Yes | Yes | Yes
558 | Generator | RegNode | REGNODE_GEN | Internals | Regulation voltage node name. | String | #N/A | #N/A | DPF, LVM |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | REGNODE.NAME | Yes | Yes | Yes | Yes
559 | Generator | RGround | RGROUND_GEN | Internals | Resistance to ground (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | TRUE | 0 | 100 | 0 | 100 | RGROUND | Yes | Yes | Yes | Yes
560 | Generator | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
561 | Generator | ServiceCenter | SERVCNTR_GEN | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
562 | Generator | SlackGen | SLACK_GEN | Internals | Flag indicating that the generator is a slack source (True = slack source, False = not a slack source). | Boolean | #N/A | #N/A | OPS, NTP, DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SLACKBUS | Yes | Yes | Yes | Yes
563 | Generator | State | STATE_GEN | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
564 | Generator | SymbolPlacement:GeometryLevel | GEOMLEVEL_GEN | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
565 | Generator | SymbolPlacement:GeometryType | GEOMTYPE_GEN | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
566 | Generator | SymbolPlacement:Rotation | ROTATION_GEN | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
567 | Generator | SymbolPlacement:Size | SIZE_GEN | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
568 | Generator | SymbolPlacement:X | WCX_GEN | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
569 | Generator | SymbolPlacement:X2 | WCX2_GEN | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
570 | Generator | SymbolPlacement:Y | WCY_GEN | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
571 | Generator | SymbolPlacement:Y2 | WCY2_GEN | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
572 | Generator | ThirdPartyOwned | THIRDPARTYOWNED_GEN | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
573 | Generator | VmaxSep | VMAXSEP_GEN | Internals | Maximum voltage before separation from the network (per unit or on a configurable voltage base depending on the flag set on the generator model). | Float | per unit or Volt | per unit or Volt | OPS | User-configurable through Defaults File |  | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VMAXSEP | Yes | Yes | Yes | Yes
574 | Generator | VminSep | VMINSEP_GEN | Internals | Minimum voltage before separation from the network (per unit or on a configurable voltage base depending on the flag set on the generator model). | Float | per unit or Volt | per unit or Volt | OPS | User-configurable through Defaults File |  | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VMINSEP | Yes | Yes | Yes | Yes
575 | Generator | VoltageBase | VOLTAGEBASE_GEN | Internals | Voltage base value (Volt). | Float | Volt | Volt | DPF | 120 |  | FALSE | 10 | 45000 | 10 | 45000 | VOLTAGEBASE | Yes | Yes | Yes | Yes
576 | Generator | VoltageSchedule | VOLTSCH_GEN | Internals | Associated voltage schedule name (in the global resources file). | String | #N/A | #N/A | DPF |  | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | VOLTSCHD.NAME | Yes | Yes | Yes | Yes
577 | Generator | VoltUnitsGen | VOLTUNITS_GEN |  | Enumerated flag indicating the voltage units that should be used. The following values are supported: 1 = Per unit voltage, 2 = Actual voltage (on a user-configured voltage base specified in VoltageBase field). | Integer | enumeration | enumeration | DPF |  |  | TRUE |  |  |  |  | VOLTUNIT | Yes | Yes | Yes | Yes
578 | Generator | VregLineline | VREGLINELINE_GEN | Internals | Flag that indicates whether the voltage for the regulated (sensed) phases is measured line to line or line to ground (True = line to line). | String | #N/A | #N/A | DPF |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | VREGLL | Yes | Yes | Yes | Yes
579 | Generator | VregLineline | VREGLINELINE_GEN |  |  | String |  |  | DPF |  |  | FALSE: TRUE; No: Yes; No: Yes; No: Yes; No: Yes
580 | Generator | XGround | XGROUND_GEN | Internals | Reactance to ground (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | TRUE | 0 | 100 | 0 | 100 | XGROUND | Yes | Yes | Yes | Yes
581 | Generator | Yconnected | WYECONN_GEN | Internals | Flag indicating generator is wye connected (True = wye connected). | String | #N/A | #N/A | OPS | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | WYE | Yes | Yes | Yes | Yes
582 | Generator | #N/A | NUMGEOM_GEN | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
583 | Generator | #N/A | NUMLABELGEOM_GEN | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
584 | Ground | CompanyName | COMPANYNAME_GROUND | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
585 | Ground | County | COUNTY_GROUND | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
586 | Ground | Future | FUTURE_GROUND | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FUTURE | Yes | Yes | Yes | Yes
587 | Ground | Id | ID_GROUND | Internals | Ground unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
588 | Ground | LabelPlacement:CharacterRotation | LABELCHRROTATION_GROUND | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
589 | Ground | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_GROUND | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
590 | Ground | LabelPlacement:FontSize | LABELSIZE_GROUND | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
591 | Ground | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_GROUND | Internals | Label geometry level | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
592 | Ground | LabelPlacement:GeometryType | LABELGEOMTYPE_GROUND | Internals | Label geometry type | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
593 | Ground | LabelPlacement:Rotation | LABELROT_GROUND | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
594 | Ground | LabelPlacement:Text | LABELTEXT_GROUND | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
595 | Ground | LabelPlacement:X | LABELX_GROUND | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
596 | Ground | LabelPlacement:Y | LABELY_GROUND | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
597 | Ground | LocationDescription | LOCATIONDESCRIPTION_GROUND | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
598 | Ground | Municipality | MUNICIPALITY_GROUND | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
599 | Ground | Name | NAME_GROUND | Internals | Ground display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
600 | Ground | Node | NODE_GROUND | Internals | Associated node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODEID | Yes | Yes | Yes | Yes
601 | Ground | PermitAreaId | PERMITAREAID_GROUND | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
602 | Ground | Phase | PHASE_GROUND | Internals | Ground phase connections. | String | #N/A | #N/A | OPS |  | N | FALSE | #N/A | #N/A | #N/A | #N/A | PHASE | Yes | Yes | Yes | Yes
603 | Ground | R | R_GROUND | Internals | Resistance to ground (ohms). | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 100 | 0 | 100 | RGROUND | Yes | Yes | Yes | Yes
604 | Ground | ServiceCenter | SERVCNTR_GROUND | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
605 | Ground | State | STATE_GROUND | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
606 | Ground | SymbolPlacement:GeometryLevel | GEOMLEVEL_GROUND | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
607 | Ground | SymbolPlacement:GeometryType | GEOMTYPE_GROUND | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
608 | Ground | SymbolPlacement:Rotation | ROTATION_GROUND | Internals | Rotation angle. | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
609 | Ground | SymbolPlacement:Size | SIZE_GROUND | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
610 | Ground | SymbolPlacement:X | WCX_GROUND | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
611 | Ground | SymbolPlacement:X2 | WCX2_GROUND | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
612 | Ground | SymbolPlacement:Y | WCY_GROUND | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
613 | Ground | SymbolPlacement:Y2 | WCY2_GROUND | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
614 | Ground | ThirdPartyOwned | THIRDPARTYOWNED_GROUND | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
615 | Ground | X | X_GROUND | Internals | Reactance to ground (ohms). | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 100 | 0 | 100 | XGROUND | Yes | Yes | Yes | Yes
616 | Ground | #N/A | NUMGEOM_GROUND | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
617 | Ground | #N/A | NUMLABELGEOM_GROUND | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
618 | Inverter | AmpRating | AMPRATING_INVERTER |  | The maximum nameplate AC current level of the DER (RMS Amps). | Float | RMS Amps | RMS Amps | DPF, SCC |  |  | FALSE | 0 | 5000 | 0 | 5000 | AMPRATING | Yes | Yes | Yes | No
619 | Inverter | CompanyName | COMPANYNAME_INVERTER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
620 | Inverter | County | COUNTY_INVERTER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
621 | Inverter | Geometries | NUMGEOM_INVERTER | Internals | Geometries | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SYMBOLPLACEMENT | Yes | Yes | Yes | Yes
622 | Inverter | Id | ID_INVERTER | Internals | Inverter ID | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
623 | Inverter | InverterModel | INVERTERMOD_INVERTER | Internals | Inverter model. | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | INVERTERMODEL | Yes | Yes | Yes | Yes
624 | Inverter | Label Geometries | NUMLABELGEOM_INVERTER | Internals | Label geometries | [6 empty] | ID: LABELPLACEMENT; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
625 | Inverter | LabelPlacement:CharacterRotation | LABLECHRROTATION_INVERTER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
626 | Inverter | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_INVERTER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
627 | Inverter | LabelPlacement:FontSize | LABELSIZE_INVERTER | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
628 | Inverter | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_INVERTER | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
629 | Inverter | LabelPlacement:GeometryType | LABELGEOMTYPE_INVERTER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
630 | Inverter | LabelPlacement:Rotation | LABELROT_INVERTER | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
631 | Inverter | LabelPlacement:Text | LABELTEXT_INVERTER | Internals | Label geometry text. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
632 | Inverter | LabelPlacement:X | LABELX_INVERTER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
633 | Inverter | LabelPlacement:Y | LABELY_INVERTER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
634 | Inverter | LocationDescription | LOCATIONDESCRIPTION_INVERTER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
635 | Inverter | Municipality | MUNICIPALITY_INVERTER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
636 | Inverter | Name | NAME_INVERTER | Internals | Name | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
637 | Inverter | Node | NODE_INVERTER | Internals | Node | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NODE | Yes | Yes | Yes | Yes
638 | Inverter | NumEnergyResource | NUMENERGYRESOURCE_INVERTERFUNC | Internals | The number of the associated energy resources. | Integer | #N/A | #N/A | DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NUMENERGYRESOURCE | Yes | Yes | Yes | Yes
639 | Inverter | NumEnergyResourceId | ENERGYRESOURCEIDn_INVERTER | Internals | Individual energy resource Id. |  |  |  | OPS, DPF |  |  | NAME NODE: ENERGYRESOURCEID; Yes Yes: Yes; Yes Yes: Yes; Yes Yes: Yes; Yes Yes: Yes
640 | Inverter | PeakPowerLimit | PEAKPOWERLIMIT_INVERTER |  | The peak power target power level limit (Watts). | Float | W | W | DPF |  |  | FALSE | 0 | 50000 | 0 | 50000 | PEAKPOWERLIMIT | Yes | Yes | Yes | Yes
641 | Inverter | Phase | PHASE_INVERTER | Internals | Inverter phasing | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PHASE | Yes | Yes | Yes | Yes
642 | Inverter | PointPlacement:Geometry Type | GEOMTYPE_INVERTER | Internals | Geometry type. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | GEOMETRYTYPE | Yes | Yes | Yes | Yes
643 | Inverter | PointPlacement:GeometryLevel | GEOMLEVEL_INVERTER | Internals | Geometry level. | Float | #N/A | #N/A | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
644 | Inverter | PointPlacement:Rotation | ROTATION_INVERTER | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
645 | Inverter | PointPlacement:Size | SIZE_INVERTER | Internals | Size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
646 | Inverter | PointPlacement:World Coordinate X | WCX_INVERTER | Internals | X coordinate. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | X | Yes | Yes | Yes | Yes
647 | Inverter | PointPlacement:World Coordinate X2 | WCX2_INVERTER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | X2 | Yes | No | Yes | No
648 | Inverter | PointPlacement:World Coordinate Y | WCY_INVERTER | Internals | Y coordinate. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y | Yes | Yes | Yes | Yes
649 | Inverter | PointPlacement:World Coordinate Y2 | WCY2_INVERTER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y2 | Yes | No | Yes | No
650 | Inverter | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
651 | Inverter | ShortCircuitRating | SHORTCIRCUITRATING_INVERTER |  | Short circuit rating (specified as multiplier of nameplate AC rating. | Float |  |  | DPF, SCC |  |  | FALSE | 0 | 15 | 0 | 15 | SHORTCIRCUITRATING | Yes | Yes | Yes | No
652 | Inverter | Size | SIZE_INVERTER | Internals | Inverter size | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SIZE | Yes | Yes | Yes | Yes
653 | Inverter | State | STATE_INVERTER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
654 | Inverter | ThirdPartyOwned | THIRDPARTYOWNED_INVERTER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
655 | Inverter | VaChargeMax | VACHARGEMAX_INVERTER |  | The maximum apparent power the DER can absorb from the grid (VA, for energy storage charging). | Float | kVA | kVA | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | VACHARGEMAX | Yes | Yes | Yes | Yes
656 | Inverter | VaMax | VAMAX_INVERTER |  | The maximum apparent power the DER can deliver to the grid (VA). | Float | kVA | kVA | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | VAMAX | Yes | Yes | Yes | Yes
657 | Inverter | VarChargeMax | VARCHARGEMAX_INVERTER |  | The maximum reactive power the DER can absorb from the grid (VAR), for energy storage charging). | Float | kVAR | kVAR | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | VARCHARGEMAX | Yes | Yes | Yes | Yes
658 | Inverter | VarMax | VARMAX_INVERTER |  | The maximum reactive power the DER can deliver to the grid (VAR). | Float | kVAR | kVAR | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | VARMAX | Yes | Yes | Yes | Yes
659 | Inverter | VoltRef | VOLTREF_INVERTER |  | The normal operating voltage for the DER site/service connection (V). | Float | V | V | DPF |  |  | FALSE | 0 | 500 | 0 | 500 | VOLTREF | Yes | Yes | Yes | Yes
660 | Inverter | VoltRefOffset | VOLTREFOFFSET_INVERTER |  | An offset voltage that represents an adjustment for this DER, relative to VRef, in Volts. VRefOfs is defined as the voltage at the ECP, relative to the PCC. For example, if the PCC VRef is 120 V, and the nominal voltage at the DER’s ECP is 123 V, then VRefOfs = +3V. All inverters behind one Point of Common Coupling (PCC) have a common reference voltage, but may differ in the voltage between their own Electrical Connection Point (ECP) and the PCC due to instrumentation errors or voltage shifts within a plant. These differences can be corrected by the parameter VRefOfs that is to be applied by each inverter. | Float | V | V | DPF, LVM |  |  | FALSE | 0 | 7 | 0 | 7 | VOLTREFOFFSET | Yes | Yes | Yes | Yes
661 | Inverter | WChargeMax | WCHARGEMAX_INVERTER |  | The maximum real power the DER can absorb from the grid (W, for energy storage charging). | Float | kW | kW | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | WCHARGEMAX | Yes | Yes | Yes | Yes
662 | Inverter | Wmax | WMAX_INVERTER |  | The maximum real power the DER can deliver to the grid (W). | Float | kW | kW | DPF, FISR |  |  | FALSE | 0 | 50000 | 0 | 50000 | WMAX | Yes | Yes | Yes | Yes
663 | InverterGroup | InverterId | INVERTERIDn_INVERTERFUNC | Internals | Inverter ID | [6 empty] | SIZE STATE: INVERTERID; Yes No: Yes; Yes No: Yes; Yes No: Yes; Yes No: Yes
664 | InverterGroup | Inverters | NUMINVERTERS_INVERTERFUNC | Internals | The number of inverters in the group | [6 empty] | SIZE STATE: NUMINVERTERS; Yes No: Yes; Yes No: Yes; Yes No: Yes; Yes No: Yes
665 | Jumper | Address | ADDRESS_JUMPER | Internals | Jumper address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
666 | Jumper | CompanyName | COMPANYNAME_JUMPER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
667 | Jumper | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID (for station internal devices only). | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
668 | Jumper | ComputeFlows | COMPUTEFLOWS_JUMPER | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
669 | Jumper | County | COUNTY_JUMPER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
670 | Jumper | CustomField:IsString | CUSTOMFIELDISSTRING_JUMPER |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
671 | Jumper | CustomField:Name | CUSTOMFIELDNAME_JUMPER |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
672 | Jumper | CustomField:Value | CUSTOMFIELDVALUE_JUMPER |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
673 | Jumper | DSOOverride | DSOOVER_JUMPER | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
674 | Jumper | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_JUMPER | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
675 | Jumper | ExternalInterfaceMember | EXTERNALINTERFACE_JUMPER | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
676 | Jumper | FeedMainBound | FEEDMAINBOUND_JUMPER | Externals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
677 | Jumper | FromNode | FRNODE_JUMPER | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
678 | Jumper | Future | FUTURE_JUMPER | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
679 | Jumper | Id | ID_JUMPER | Internals | Jumper unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
680 | Jumper | LabelPlacement:CharacterRotation | LABELCHRROTATION_JUMPER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
681 | Jumper | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_JUMPER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
682 | Jumper | LabelPlacement:FontSize | LABELSIZE_JUMPER | Internals | Font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
683 | Jumper | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_JUMPER | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
684 | Jumper | LabelPlacement:GeometryType | LABELGEOMTYPE_JUMPER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
685 | Jumper | LabelPlacement:Rotation | LABELROT_JUMPER | Internals | Lasbel rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
686 | Jumper | LabelPlacement:Text | LABELTEXT_JUMPER | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
687 | Jumper | LabelPlacement:X | LABELX_JUMPER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
688 | Jumper | LabelPlacement:Y | LABELY_JUMPER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
689 | Jumper | LocationDescription | LOCATIONDESCRIPTION_JUMPER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
690 | Jumper | Municipality | MUNICIPALITY_JUMPER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
691 | Jumper | Name | NAME_JUMPER | Internals | Jumper display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
692 | Jumper | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_JUMPER | Internals | Nominal feeder ID for the breaker. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for permanent jumpers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
693 | Jumper | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
694 | Jumper | NormallyDeenergized | NORMDEENERGIZED_JUMPER | Internals | Flag indicating that the jumper is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
695 | Jumper | NormallyLooped | NORMLOOPED_JUMPER | Internals | Flag indicating that the jumper is normally looped (True = looped). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
696 | Jumper | NormallyNetworkLooped | NORMNETWORKLOOPED_JUMPER | Internals | Flag indicating that the jumper is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | fasle | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
697 | Jumper | NormallyOpen | NOPEN_JUMPER | Internals | Flag indicating the jumper is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A | NOPEN | Yes | Yes | Yes | Yes
698 | Jumper | NormallyParallelLooped | NORMPARALLELLOOPED_JUMPER | Internals | Flag indicating that the jumper is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
699 | Jumper | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched fuses that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_FUSE field. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
700 | Jumper | PermitAreaId | PERMITAREAID_JUMPER | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
701 | Jumper | Phase | PHASE_JUMPER | Internals | Jumper phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
702 | Jumper | PolyPlacement:GeometryLevel | POLYGEOMLEVEL_JUMPER | Internals | Geometry level. | String | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
703 | Jumper | PolyPlacement:GeometryType | POLYGEOMTYPE_JUMPER | Internals | Geometry type. | String | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
704 | Jumper | PolyPlacement:Vertex:X | WCXn_JUMPER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE |  |  |  |  | AX | Yes | Yes | Yes | Yes
705 | Jumper | PolyPlacement:Vertex:X2 | WCX2n_JUMPER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE |  |  |  |  | AX2 | Yes | No | Yes | No
706 | Jumper | PolyPlacement:Vertex:Y | WCYn_JUMPER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE |  |  |  |  | AY | Yes | Yes | Yes | Yes
707 | Jumper | PolyPlacement:Vertex:Y2 | WCY2n_JUMPER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE |  |  |  |  | AY2 | Yes | No | Yes | No
708 | Jumper | SecondId | TROUBLECALLID_JUMPER | Internals | Alternate switch ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
709 | Jumper | ServiceCenter | SERVCNTR_JUMPER | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
710 | Jumper | State | STATE_JUMPER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
711 | Jumper | SuppressFeeder |  | Internals | Flag indicating that the jumper name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
712 | Jumper | SwitchModel | SWMOD_JUMPER | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
713 | Jumper | SwitchModelPhA | SWMODA_JUMPER | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
714 | Jumper | SwitchModelPhB | SWMODB_JUMPER | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
715 | Jumper | SwitchModelPhC | SWMODC_JUMPER | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
716 | Jumper | SymbolPlacement:GeometryLevel | GEOMLEVEL_JUMPER | Internals | Geometry level. | String | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
717 | Jumper | SymbolPlacement:GeometryType | GEOMTYPE_JUMPER | Internals | Geometry type. | String | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
718 | Jumper | SymbolPlacement:Rotation | ROTATION_JUMPER | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
719 | Jumper | SymbolPlacement:Size | SIZE_JUMPER | Internals | Size. | Integer | points | points | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
720 | Jumper | SymbolPlacement:X | WCX_JUMPER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
721 | Jumper | SymbolPlacement:X2 | WCX2_JUMPER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
722 | Jumper | SymbolPlacement:Y | WCY_JUMPER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
723 | Jumper | SymbolPlacement:Y2 | WCY2_JUMPER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  | Symbol placement information is only one set filled in for a given jumper | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
724 | Jumper | ThirdPartyOwned | THIRDPARTYOWNED_JUMPER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
725 | Jumper | ToNode | TONODE_JUMPER | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
726 | Jumper | ToStation | TOSUB_JUMPER | Internals | Associated external substation name. This field should only be set if the jumper connects two substations together. | String | #N/A | #N/A | OPS |  | The station name is checked against the stations list read from the global resources file (global.csv or global_internals.xml) | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
727 | Jumper | #N/A | NUMGEOM_JUMPER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
728 | Jumper | #N/A | NUMLABELGEOM_JUMPER | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
729 | Jumper | #N/A | NUMPOLYGEOM_JUMPER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
730 | Jumper | #N/A | NUMVERT_JUMPER | Externals | Number of vertices. | Integer | count | count | OPS |  | Polyplacement information is only one set filled in for a given jumper | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
731 | Jumper | BusTieSwitch | BUSTIESWITCH_JUMPER | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
732 | Line | BCH0 | #N/A | Internals | Transmission line zero sequence charging susceptance (MVAR). | Float | MVAR | MVAR | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
733 | Line | BCH1 | #N/A | Internals | Transmission line positive sequence charging susceptance (MVAR) | Float | MVAR | MVAR | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
734 | Line | CompanyName | COMPANYNAME_LINE | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
735 | Line | ConductorModelA | CONDMODA_LINE | Internals | Associated phase A conductor model name. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The conductor model name must match a conductor model listed in the global resources file. Required for an A phase line. | TRUE | #N/A | #N/A | #N/A | #N/A | LINECONDMODA | Yes | Yes | Yes | Yes
736 | Line | ConductorModelB | CONDMODB_LINE | Internals | Associated phase B conductor model name. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The conductor model name must match a conductor model listed in the global resources file. Required for a B phase line. | TRUE | #N/A | #N/A | #N/A | #N/A | LINECONDMODB | Yes | Yes | Yes | Yes
737 | Line | ConductorModelC | CONDMODC_LINE | Internals | Associated phase C conductor model name. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The conductor model name must match a conductor model listed in the global resources file. Required for a C phase line. | TRUE | #N/A | #N/A | #N/A | #N/A | LINECONDMODC | Yes | Yes | Yes | Yes
738 | Line | ConductorModelN | CONDMODN_LINE | Internals | Associated phase N conductor model name. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The conductor model name must match a conductor model listed in the global resources file. Required for a neutral conductor. | TRUE | #N/A | #N/A | #N/A | #N/A | LINECONDMODN | Yes | Yes | Yes | Yes
739 | Line | ConstructionModel | CONSTMOD_LINE | Internals | Associated construction type model name. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The construction type name must match a construction type given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | FRAMEMODNAME | Yes | Yes | Yes | Yes
740 | Line | County | COUNTY_LINE | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
741 | Line | CustomField:IsString | CUSTOMFIELDISSTRING_LINE |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
742 | Line | CustomField:Name | CUSTOMFIELDNAME_LINE |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
743 | Line | CustomField:Value | CUSTOMFIELDVALUE_LINE |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
744 | Line | FromNode | FRNODE_LINE | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
745 | Line | Future | FUTURE_LINE | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABC, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | LINEFUTURE | Yes | Yes | Yes | Yes
746 | Line | Id | ID_LINE | Internals | Line unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
747 | Line | LabelPlacement:CharacterRotation | LABELCHRROTATION_LINE | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
748 | Line | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_LINE | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
749 | Line | LabelPlacement:FontSize | LABELSIZE_LINE | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
750 | Line | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_LINE | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
751 | Line | LabelPlacement:GeometryType | LABELGEOMTYPE_LINE | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
752 | Line | LabelPlacement:Rotation | LABELROT_LINE | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
753 | Line | LabelPlacement:Text | LABELTEXT_LINE | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LINELABELPLACEMENTTXT | Yes | Yes | Yes | Yes
754 | Line | LabelPlacement:X | LABELX_LINE | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
755 | Line | LabelPlacement:Y | LABELY_LINE | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
756 | Line | Length | LENGTH_LINE | Internals | The length of a line. | Float | feet | meter | DPF, LVM, FISR, SCC |  | The length is set to this value if less than 0.5 ft (or 0.1524 m) and a warning message is issued by the model management application. | TRUE | 0.5 | 100000 | 0.1524 | 30480 | LENGTH | Yes | Yes | Yes | Yes
757 | Line | LinePlacement:GeometryLevel | GEOMLEVEL_LINE | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
758 | Line | LinePlacement:GeometryType | GEOMTYPE_LINE | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | LNPLACE.GEOMETRY | Yes | Yes | Yes | Yes
759 | Line | LinePlacement:X | WCXn_LINE | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | LNPLACE.X | Yes | Yes | Yes | Yes
760 | Line | LinePlacement:X2 | WCX2n_LINE | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | LNPLACE.X2 | Yes | No | Yes | No
761 | Line | LinePlacement:Y | WCYn_LINE | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | LNPLACE.Y | Yes | Yes | Yes | Yes
762 | Line | LinePlacement:Y2 | WCY2n_LINE | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | LNPLACE.Y2 | Yes | No | Yes | No
763 | Line | LnLimit1 | #N/A | Internals | Level 1 transmission line flow limit. | Float | Amps | Amps | DPF, LVM, FISR |  | This field is only supported for lines modeled in the station internals file. | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
764 | Line | LnLimit2 | #N/A | Internals | Level 2 transmission line flow limit. | Float | Amps | Amps | DPF, LVM, FISR |  | This field is only supported for lines modeled in the station internals file. | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
765 | Line | LnLimit3 | #N/A | Internals | Level 3 transmission line flow limit. | Float | Amps | Amps | DPF, LVM, FISR |  | This field is only supported for lines modeled in the station internals file. | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
766 | Line | LocationDescription | LOCATIONDESCRIPTION_LINE | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
767 | Line | MomFRate | MOMFRATE_LINE | Internals | Momentary interruption frequency (failures/unit length-year). This field should be left blank if the default is taken from the conductor model. | Float | #N/A | #N/A | DPF |  |  | FALSE | 0 | 100 | 0 | 100 | TMPFRATE | Yes | Yes | Yes | Yes
768 | Line | Municipality | MUNICIPALITY_LINE | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
769 | Line | Name | NAME_LINE | Internals | Line display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
770 | Line | Nominal_Feeder_Id_Line | NOMINAL_FEEDER_ID_LINE | Externals | Nominal feeder ID for the line. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for lines marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
771 | Line | NormallyDeenergized | NORMDEENERGIZED_LINE | Internals | Flag indicating that the line is normally de-energized. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
772 | Line | NormallyLooped | NORMLOOPED_LINE | Internals | Flag indicating that the line is normally looped. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
773 | Line | NormallyNetworkLooped | NORMNETWORKLOOPED_LINE | Internals | Flag indicating that the jumper is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
774 | Line | NormallyParallelLooped | NORMPARALLELLOOPED_LINE | Internals | Flag indicating that the jumper is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
775 | Line | NumCircuits | NUMCIRCUITS_LINE | Internals | The number of cables in a duct bank (set for underground cables only for ampacity limit monitoring). | Integer | count | count | DPF, LVM, FISR, SCC | 0 |  | FALSE | 0 | 30 | 0 | 30 | NUMCIRC | Yes | Yes | Yes | Yes
776 | Line | PermitAreaId | PERMITAREAID_LINE | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
777 | Line | Phase | PHASE_LINE | Internals | Line phase connection flag. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABC, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
778 | Line | R0 | #N/A | Internals | Transmission line zero sequence resistance (ohms). | Float | ohms | ohms | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
779 | Line | R1 | #N/A | Internals | Transmission line positive sequence resistance (ohms). | Float | ohms | ohms | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
780 | Line | Repair | REPAIR_LINE | Internals | Mean time to repair (hours). This field should be left blank if the default is taken from the conductor model. | Float | hour | hour | DPF |  |  | FALSE | 0 | 500 | 0 | 500 | REPAIRTM | Yes | Yes | Yes | Yes
781 | Line | ServiceCenter | SERVCNTR_LINE | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
782 | Line | State | STATE_LINE | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
783 | Line | SuppressFeeder |  | Internals | Flag indicating that the jumper name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
784 | Line | SustFRate | SUSTFRATE_LINE | Internals | Sustained interruption frequency (failures/unit length-year). This field should be blank if the default is taken from the conductor model. | Float | #N/A | #N/A | DPF |  |  | FALSE | 0 | 100 | 0 | 100 | PRMFRATE | Yes | Yes | Yes | Yes
785 | Line | ThirdPartyOwned | THIRDPARTYOWNED_LINE | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
786 | Line | ToNode | TONODE_LINE | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
787 | Line | ToStation | TOSUB_LINE | Internals | Associated external substation name. This field should only be set if the line connects two stations together such as a sub-transmission line. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
788 | Line | X0 | #N/A | Internals | Transmission line zero sequence reactance (ohms). | Float | ohms | ohms | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | FALSE | 0 | 100 | 0 | 100 |  | Yes | Yes | Yes | Yes
789 | Line | X1 | #N/A | Internals | Transmission line positive sequence reactance (ohms). | Float | ohms | ohms | DPF, LVM, FISR, SCC |  | This field is only supported for lines modeled in the station internals file. | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
790 | Line | #N/A | NUMGEOM_LINE | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
791 | Line | #N/A | NUMVERT_LINE | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
792 | Line | #N/A | NUMLABELGEOM_LINE | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
793 | Load | Address | ADDRESS_LOAD | Internals | Address of load. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
794 | Load | CompanyName | COMPANYNAME_LOAD | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
795 | Load | County | COUNTY_LOAD | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
796 | Load | CriticalCustNum | CRITICALCUSTNUM_LOAD | Internals | The number of critical customers for this load. | Integer | #N/A | #N/A | OPS |  |  | FALSE | 0 | 20000 | 0 | 20000 | CRITICALCUSTNUM | Yes | Yes | Yes | Yes
797 | Load | Customer | CUSTOMER_LOAD | Internals | Number of customers the load represents. For example, four residential customers fed from the same distribution transformer may be aggregated into a single load. | Integer | count | count | OPS |  |  | TRUE | 1 | 20000 | 1 | 20000 | CUSTOMERCOUNT | Yes | Yes | Yes | Yes
798 | Load | CustomField:IsString | CUSTOMFIELDISSTRING_LOAD |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
799 | Load | CustomField:Name | CUSTOMFIELDNAME_LOAD |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
800 | Load | CustomField:Value | CUSTOMFIELDVALUE_LOAD |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
801 | Load | DRRatio | DRRATIO_LOAD | Internals | Demand response component of the load (in percent). This field is optional. | Float | #N/A | #N/A | DPF | 0 |  | FALSE | 0 | 100 | 0 | 100 | DRRATIO | Yes | Yes | Yes | Yes
802 | Load | Future | FUTURE_LOAD | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FUTUREPHASES | Yes | Yes | Yes | Yes
803 | Load | GenRating | GENRATING_LOAD | Internals | Nameplate kVA rating of the generation component of the load. This field is optional since it is based on the existence of a generation component of the load. | Float | kVA | kVA | OPS |  |  | FALSE | 1 | 500 | 1 | 500 | GENRATING | Yes | Yes | Yes | Yes
804 | Load | GenType | GENTYPE_LOAD | Internals | User defined generation type enumeration.This field is optional since it is based on the existence of a generation component of the load. These user defined enumerations need to be defined in the global file enumerations table. This field does not have any impact on the network applications. Some examples include the following: 0: “Solar” 1: “Wind” 2: “Battery” | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GENTYPE | Yes | Yes | Yes | Yes
805 | Load | Grounded | GROUNDED_LOAD | Internals | Flag indicating load is grounded (True = grounded). | String | #N/A | #N/A | DPF | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | GROUNDED | Yes | Yes | Yes | Yes
806 | Load | Id | ID_LOAD | Internals | Load unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
807 | Load | LabelPlacement:CharacterRotation | LABELCHRROTATION_LOAD | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
808 | Load | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_LOAD | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
809 | Load | LabelPlacement:FontSize | LABELSIZE_LOAD | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
810 | Load | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_LOAD | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
811 | Load | LabelPlacement:GeometryType | LABELGEOMTYPE_LOAD | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
812 | Load | LabelPlacement:Rotation | LABELROT_LOAD | Internals | Label rotation angle. | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
813 | Load | LabelPlacement:Text | LABELTEXT_LOAD | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
814 | Load | LabelPlacement:X | LABELX_LOAD | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
815 | Load | LabelPlacement:Y | LABELY_LOAD | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
816 | Load | LoadCategory | LOADCAT_LOAD | Internals | Associated load category name. | String | #N/A | #N/A | DPF |  | The load category name must match a load category given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | LOADCAT.NAME | Yes | Yes | Yes | Yes
817 | Load | LocationDescription | LOCATIONDESCRIPTION_LOAD | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
818 | Load | Municipality | MUNICIPALITY_LOAD | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
819 | Load | Name | NAME_LOAD | Internals | Load display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
820 | Load | Node | NODE_LOAD | Internals | Associated node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
821 | Load | NOMINAL_FEEDER_ID_LOAD | NOMINAL_FEEDER_ID_LOAD | Internals | Nominal feeder ID for the load This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for loads marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
822 | Load | NonConforming | NONCONFORMING_LOAD | Internals | Flag indicating that the load is a non-conforming load (True = non-conforming). Non-conforming loads do not participate in the Bus Load Allocation (BLA) load adjustment function. | Boolean | #N/A | #N/A | DPF | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NONCONFORMING | Yes | Yes | Yes | Yes
823 | Load | NormallyDeenergized | NORMDEENERGIZED_LOAD | Internals | Flag indicating that the load is normally de-energized. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
824 | Load | NumDRCustomer | NUMDRCUSTOMER_LOAD | Internals | The number of customers participating in demand response program (must be less than or equal to the CUSTOMER_LOAD value). This field is optional. | Integer | #N/A | #N/A | OPS | 0 |  | FALSE | 0 | 1000 | 0 | 1000 | NUMDRCUSTOMER | Yes | Yes | Yes | Yes
825 | Load | NumGenCustomer | NUMGENCUSTOMER_LOAD | Internals | The number of customers that have generation (if the load represents one customer and this customer has generation, then this field has a value of 1). This field is optional. | Integer | #N/A | #N/A | OPS | 0 |  | FALSE | 0 | 1000 | 0 | 1000 | NUMGENCUSTOMER | Yes | Yes | Yes | Yes
826 | Load | PermitAreaId | PERMITAREAID_LOAD | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
827 | Load | Phase | PHASE_LOAD | Internals | Load phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | CONSTRUCTPHASES | Yes | Yes | Yes | Yes
828 | Load | PNomA | PNOMA_LOAD | Internals | Nominal real power of Phase A (or AB if delta connected) in kW. | Float | kW | kW | DPF, LVM, FISR, SCC |  |  | FALSE | 0 | 3000 | 0 | 3000 | PNOMA | Yes | Yes | Yes | Yes
829 | Load | PNomB | PNOMB_LOAD | Internals | Nominal real power of Phase B (or BC if delta connected) in kW. | Float | kW | kW | DPF, LVM, FISR, SCC |  |  | FALSE | 0 | 3000 | 0 | 3000 | PNOMB | Yes | Yes | Yes | Yes
830 | Load | PNomC | PNOMC_LOAD | Internals | Nominal real power of Phase C (or CA if delta connected) in kW. | Float | kW | kW | DPF, LVM, FISR, SCC |  |  | FALSE | 0 | 3000 | 0 | 3000 | PNOMC | Yes | Yes | Yes | Yes
831 | Load | Primary | PRIMARY_LOAD | Internals | Flag indicating load represents a primary meter customer (True = primary customer). A primary meter customer has a different symbol than a non-primary meter load. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | PRIMMETLOAD | Yes | Yes | Yes | Yes
832 | Load | Priority | PRIORITY_LOAD | Internals | Load priority. The Number of Priority Cusomters can be calculated by two fields : "Priority" * "Customer" | Integer | #N/A | #N/A | OPS | 0 | 0…7 | FALSE | #N/A | #N/A | #N/A | #N/A | LOADPRIORITY | Yes | Yes | Yes | No
833 | Load | QNomA | QNOMA_LOAD | Internals | Nominal reactive power of Phase A (or AB if delta connected). This field should be blank if a power factor is used (based on the QNOMFLAG field set in the associated load category). | Float | kVAR | kVAR | DPF, LVM, FISR, SCC |  | This field is only validated when reactive power schedules are provided. | FALSE | 0 | 3000 | 0 | 3000 | QNOMA | Yes | Yes | Yes | Yes
834 | Load | QNomB | QNOMB_LOAD | Internals | Nominal reactive power of Phase B (or BC if delta connected). This field should be blank if a power factor is used (based on the QNOMFLAG field set in the associated load category). | Float | kVAR | kVAR | DPF, LVM, FISR, SCC |  | This field is only validated when reactive power schedules are provided. | FALSE | 0 | 3000 | 0 | 3000 | QNOMB | Yes | Yes | Yes | Yes
835 | Load | QNomC | QNOMC_LOAD | Internals | Nominal reactive power of Phase C (or CA if delta connected). This field should be blank if a power factor is used (based on the QNOMFLAG field set in the associated load category). | Float | kVAR | kVAR | DPF, LVM, FISR, SCC |  | This field is only validated when reactive power schedules are provided. | FALSE | 0 | 3000 | 0 | 3000 | QNOMC | Yes | Yes | Yes | Yes
836 | Load | Regular | REGULAR_LOAD | Internals | Flag indicating that the load is a conventional load (True means it does not inject energy into the network). | Boolean | #N/A | #N/A | OPS | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A | REGULAR | Yes | Yes | Yes | Yes
837 | Load | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
838 | Load | ServiceCenter | SERVCNTR_LOAD | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
839 | Load | State | STATE_LOAD | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
840 | Load | Supplier | SUPPLIER_LOAD | Internals | Energy supplier (enumeration). This field has the following values: 1 = Utility, 2 = Other. | Integer | #N/A | #N/A | OPS | User-configurable through Defaults File | 1: Utility 2: Other | FALSE | 1 | 2 | #N/A | #N/A | SUPPLIER | Yes | Yes | Yes | Yes
841 | Load | SymbolPlacement:GeometryLevel | GEOMLEVEL_LOAD | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
842 | Load | SymbolPlacement:GeometryType | GEOMTYPE_LOAD | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
843 | Load | SymbolPlacement:Rotation | ROTATION_LOAD | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
844 | Load | SymbolPlacement:Size | SIZE_LOAD | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
845 | Load | SymbolPlacement:X | WCX_LOAD | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
846 | Load | SymbolPlacement:X2 | WCX2_LOAD | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
847 | Load | SymbolPlacement:Y | WCY_LOAD | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
848 | Load | SymbolPlacement:Y2 | WCY2_LOAD | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
849 | Load | ThirdPartyOwned | THIRDPARTYOWNED_LOAD | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
850 | Load | Type | TYPE_LOAD | Internals | User defined numerated type field. These user defined enumerations need to be defined in the global file enumerations table. This is informative information only but it could potentially be used for symbology. This field does not have any impact on the network applications. Some examples include the following: 1: “Small Residential with Solar” 2: “Large Residential with Solar” 3: “Commercial” 4: “Small Commercial with Solar” 5: “Large Commercial with Solar” 6: “Wind” | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CUSTOMERLOADTYPE | Yes | Yes | Yes | Yes
851 | Load | Yconnected | WYECONN_LOAD | Internals | Flag indicating load is wye connected (True = wye connected). A load that is connected from phase to neutral is considered a wye load. | String | #N/A | #N/A | DPF | User-configurable through Defaults File |  | TRUE | #N/A | #N/A | #N/A | #N/A | WYE | Yes | Yes | Yes | Yes
852 | Load | #N/A | NUMGEOM_LOAD | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
853 | Load | #N/A | NUMLABELGEOM_LOAD | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
854 | Loop End Label | CompanyName | COMPANYNAME_LPLABEL | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
855 | Loop End Label | County | COUNTY_LPLABEL | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
856 | Loop End Label | CustomField:IsString | CUSTOMFIELDISSTRING_LPLABEL |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
857 | Loop End Label | CustomField:Name | CUSTOMFIELDNAME_LPLABEL |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
858 | Loop End Label | CustomField:Value | CUSTOMFIELDVALUE_LPLABEL |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
859 | Loop End Label | FuseId | FUSE_LPLABEL | Internals | The index of the starting loop fuse. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | LPFUSE | Yes | Yes | Yes | Yes
860 | Loop End Label | Id | ID_LPLABEL | Internals | Loop end label unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
861 | Loop End Label | LabelPlacement:CharacterRotation | LABELCHRROTATION_LPLABEL | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
862 | Loop End Label | LabelPlacement:FontSize | LABELSIZE_LPLABEL | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
863 | Loop End Label | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_LPLABEL | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
864 | Loop End Label | LabelPlacement:GeometryType | LABELGEOMTYPE_LPLABEL | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
865 | Loop End Label | LabelPlacement:Rotation | LABELROT_LPLABEL | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
866 | Loop End Label | LabelPlacement:Text | LABELTEXT_LPLABEL | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
867 | Loop End Label | LabelPlacement:Text | LABELTEXT_LPLABEL | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
868 | Loop End Label | LabelPlacement:X | LABELX_LPLABEL | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
869 | Loop End Label | LabelPlacement:Y | LABELY_LPLABEL | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  | If the label coordinate information is not given, then the label is not displayed. The label coordinates correspond to a given geometry type. | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
870 | Loop End Label | LocationDescription | LOCATIONDESCRIPTION_LPLABEL | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
871 | Loop End Label | Municipality | MUNICIPALITY_LPLABEL | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
872 | Loop End Label | Name | NAME_LPLABEL | Internals | This name can be displayed in the loop symbol on geographic displays. The purpose of the Loop End Label is to facilitate navigation from geographic displays to loop diagrams. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
873 | Loop End Label | PermitAreaId | PERMITAREAID_LPLABEL | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
874 | Loop End Label | SchematicId | SCHEMATICID_LPLABEL | Internals | Display call-up parameter identifying the specific loop diagram to be called up when the loop label is selected. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SCHEMEID | Yes | Yes | Yes | Yes
875 | Loop End Label | State | STATE_LPLABEL | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
876 | Loop End Label | ThirdPartyOwned | THIRDPARTYOWNED_LPLABEL | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
877 | Loop End Label | #N/A | NUMLABELGEOM_LPLABEL | Externals | Number of label geometries. | Integer | #N/A | #N/A | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
878 | Manhole | Address | ADDRESS_MANHOLE | Internals | Non-electrical device address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
879 | Manhole | CompanyName | COMPANYNAME_MANHOLE | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
880 | Manhole | County | COUNTY_MANHOLE | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
881 | Manhole | CustomField:IsString | CUSTOMFIELDISSTRING_MANHOLE |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
882 | Manhole | CustomField:Name | CUSTOMFIELDNAME_MANHOLE |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
883 | Manhole | CustomField:Value | CUSTOMFIELDVALUE_MANHOLE |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
884 | Manhole | Id | ID_MANHOLE | Internals | Manhole unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
885 | Manhole | LabelPlacement:CharacterRotation | LABELCHRROTATION_MANHOLE | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
886 | Manhole | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_MANHOLE | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
887 | Manhole | LabelPlacement:FontSize | LABELSIZE_MANHOLE | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
888 | Manhole | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_MANHOLE | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
889 | Manhole | LabelPlacement:GeometryType | LABELGEOMTYPE_MANHOLE | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
890 | Manhole | LabelPlacement:Rotation | LABELROT_MANHOLE | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
891 | Manhole | LabelPlacement:Text | LABELTEXT_MANHOLE | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
892 | Manhole | LabelPlacement:X | LABELX_MANHOLE | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
893 | Manhole | LabelPlacement:Y | LABELY_MANHOLE | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
894 | Manhole | LocationDescription | LOCATIONDESCRIPTION_MANHOLE | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
895 | Manhole | Municipality | MUNICIPALITY_MANHOLE | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
896 | Manhole | Name | NAME_MANHOLE | Internals | Manhole display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
897 | Manhole | Objects:ID | OBJECTn_MANHOLE | Internals | Collection of object device IDs in the manhole. | String | #N/A | #N/A | OPS |  | Each object must be found in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
898 | Manhole | Objects:Ivalue | #N/A | Internals | Collection of object functions (enumeration) in the manhole. | Integer | enumeration | enumeration | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
899 | Manhole | Objects:string |  | Internals | Collection of object device names in the manhole. | String | #N/A | #N/A | OPS |  | Each object must be found in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
900 | Manhole | Objects:Type | OBJECTTYPEn_MANHOLE | Internals | The type of objects in the manhole (such as SWITCH, FUSE, BREAKER, or others). | String | #N/A | #N/A | OPS |  | The object type must be defined in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
901 | Manhole | PermitAreaId | PERMITAREAID_MANHOLE | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
902 | Manhole | Refdwg | REFDWG_MANHOLE | Internals | Associated reference drawing. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | REFDRAW | Yes | Yes | Yes | Yes
903 | Manhole | State | STATE_MANHOLE | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
904 | Manhole | SymbolPlacement:GeometryLevel | GEOMLEVEL_MANHOLE | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
905 | Manhole | SymbolPlacement:GeometryType | GEOMTYPE_MANHOLE | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
906 | Manhole | SymbolPlacement:Rotation | ROTATION_MANHOLE | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
907 | Manhole | SymbolPlacement:Size | SIZE_MANHOLE | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
908 | Manhole | SymbolPlacement:X | WCX_MANHOLE | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
909 | Manhole | SymbolPlacement:X2 | WCX2_MANHOLE | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
910 | Manhole | SymbolPlacement:Y | WCY_MANHOLE | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
911 | Manhole | SymbolPlacement:Y2 | WCY2_MANHOLE | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
912 | Manhole | ThirdPartyOwned | THIRDPARTYOWNED_MANHOLE | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
913 | Manhole | Types | TYPE_MANHOLE | Internals | Manhole type (enumeration to be worked out). | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENUMTYPE | Yes | Yes | Yes | Yes
914 | Manhole | #N/A | NUMOBJECT_MANHOLE | Externals | The number of objects in the manhole | Integer | count | count | OPS |  |  | FALSE | 1 | 100 | 1 | 100 | NUMOBJ | Yes | Yes | Yes | Yes
915 | Manhole | #N/A | NUMGEOM_MANHOLE | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
916 | Manhole | #N/A | NUMLABELGEOM_MANHOLE | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
917 | Measurement | IsMultiPhaseMeas |  | Internals | The flag indicates if the measurement is multi-phase measurement. | Boolean | #N/A | #N/A | DPF, LVM, FISR, SCC | FALSE | TRUE,FALSE | TRUE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
918 | Network Protector | Address | ADDRESS_NETPROT | Internals | Network protector address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
919 | Network Protector | CloseLatchAmp | CLOSELATCHAMP_NETPROT | Internals | The network protector may have a spring-close mechanism or stored energy mechanism controlled by a toggle-cam device which will not allow closure of the contacts until the springs contain sufficient energy to close and latch (Amps). This field is for information purposes only. | Float | Amps | Amps | OPS |  |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
920 | Network Protector | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID (for station internal devices only). | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
921 | Network Protector | ComputeFlows | COMPUTEFLOWS_NETPROT | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
922 | Network Protector | CustomField:IsString | CUSTOMFIELDISSTRING_NETPROT |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
923 | Network Protector | CustomField:Name | CUSTOMFIELDNAME_NETPROT |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
924 | Network Protector | CustomField:Value | CUSTOMFIELDVALUE_NETPROT |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
925 | Network Protector | DSOOverride | DSOOVER_NETPROT | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
926 | Network Protector | ExternalId | EXTERNALID_NETPROT |  | External Id for the network protector.This information currently is not used in the DMS. It is provided to be used by another application that might utilize the source data. | String | #N/A | #N/A | OPS |  |  | No: Yes; No: Yes; No: Yes; No: Yes
927 | Network Protector | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_NETPROT | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
928 | Network Protector | ExternalInterfaceMember | EXTERNALINTERFACE_NETPROT | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
929 | Network Protector | FeedMainBound | FEEDMAINBOUND_NETPROT | Internals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
930 | Network Protector | FromNode | FRNODE_NETPROT | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
931 | Network Protector | Future | FUTURE_NETPROT | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
932 | Network Protector | Grid | GRID_NETPROT | Internals | Secondary feeder name. | String | #N/A | #N/A | OPS |  |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
933 | Network Protector | GridColor | GRIDCOLOR_NETPROT | Internals | Secondary feeder color. | Integer | #N/A | #N/A | OPS |  |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
934 | Network Protector | Id | ID_NETPROT | Internals | Network protector unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
935 | Network Protector | LabelPlacement:CharacterRotation | LABELCHRROTATION_NETPROT | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
936 | Network Protector | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_NETPROT | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
937 | Network Protector | LabelPlacement:FontSize | LABELSIZE_NETPROT | Internals | Label font size. | Integer | points | points | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
938 | Network Protector | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_NETPROT | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
939 | Network Protector | LabelPlacement:GeometryType | LABELGEOMTYPE_NETPROT | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
940 | Network Protector | LabelPlacement:Rotation | LABELROT_NETPROT | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
941 | Network Protector | LabelPlacement:Text | LABELTEXT_NETPROT | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
942 | Network Protector | LabelPlacement:X | LABELX_NETPROT | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
943 | Network Protector | LabelPlacement:Y | LABELY_NETPROT | Internals | Label Y coordinate | Float | #N/A | #N/A | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
944 | Network Protector | MasterRcl | MASTERRCL_NETPROT | Internals | Master relay reclose pick-up setting (Volts). The minimum voltage by which the network transformer secondary voltage must exceed the network voltage to permit reclosing when restoration. This field is for information purposes only. | Float | Volts | Volts | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
945 | Network Protector | MasterTrip | MASTERTRIP_NETPROT | Internals | The reverse-power function operates only for real power (Watt) flow in the reverse direction (i.e., flow from the low-voltage network toward the transformer). The reverse power pickup settings of the master relays are very sensitive.This field is for information purposes only. | Float | Watt | Watt | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
946 | Network Protector | MaxInt | MAXINT_NETPROT | Internals | Maximum interruption rating (Amps). | Float | Amps | Amps | OPS |  |  | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
947 | Network Protector | Name | NAME_NETPROT | Internals | Network protector display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
948 | Network Protector | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_NETPROT | Internals | Nominal feeder ID for the network protector. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for network protectors marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
949 | Network Protector | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
950 | Network Protector | NormallyDeenergized | NORMDEENERGIZED_NETPROT | Internals | Flag indicating that the network protector is normally de-energized. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
951 | Network Protector | NormallyLooped | NORMLOOPED_NETPROT | Internals | Flag indicating that the network protector is normally looped. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
952 | Network Protector | NormallyNetworkLooped | NORMNETWORKLOOPED_NETPROT | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
953 | Network Protector | NormallyOpen | NOPEN_NETPROT | Internals | Flag indicating the fuse is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES_NETPROT is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
954 | Network Protector | NormallyParallelLooped | NORMPARALLELLOOPED_NETPROT | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
955 | Network Protector | NormOpenPhases | NORM_OPEN_PHASES_NETPROT | Internals | Normally open phases. This phase is set for phase independently switched network protectors that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_FUSE field. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
956 | Network Protector | OperatingState | OPERSTATE_NETPROT | Internals | Operation state. The enumeration has the following values: 1: Automatic 2: Manual | Integer | #N/A | #N/A | OPS |  | 1: Automatic 2: Manual | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
957 | Network Protector | PermitAreaId | PERMITAREAID_NETPROT | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
958 | Network Protector | Phase | PHASE_NETPROT | Internals | Network protector phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
959 | Network Protector | PhaseAngRcl | PHASEANGRCL_NETPROT | Internals | Phase relay reclose pick-up (degrees). The angle by which the distribution transformer secondary voltage must lead the network voltage to ensure that real power will flow from the transformer to the network when the network protector is closed. This field is for information purposes only. | Float | degrees | degrees | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
960 | Network Protector | PhaseAngTrip | PHASEANGTRIP_NETPROT | Internals | The minimum angle setting for reverse power operation (degrees). This field is for information purposes only. | Float | degrees | degrees | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
961 | Network Protector | Rating | RATING_NETPROT | Internals | Continuous current rating (Amps). | Float | Amps | Amps | OPS |  |  | TRUE | 1 | 5000 | 1 | 5000 |  | Yes | Yes | Yes | Yes
962 | Network Protector | RelayType | RELAYTYPE_NETPROT | Internals | User defined relay type enumeration defined in the global.csv file Enumerations table. | Integer | #N/A | #N/A | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
963 | Network Protector | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
964 | Network Protector | SecondId | TROUBLECALLID_NETPROT | Internals | Network protector Second ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
965 | Network Protector | ServiceCenter | SERVCNTR_NETPROT | Internals | Associated service center | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
966 | Network Protector | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
967 | Network Protector | SuppressFeeder |  | Internals | Flag indicating that the device name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
968 | Network Protector | SwitchModel | SWMOD_NETPROT | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
969 | Network Protector | SwitchModelPhA | SWMODA_NETPROT | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
970 | Network Protector | SwitchModelPhB | SWMODB_NETPROT | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
971 | Network Protector | SwitchModelPhC | SWMODC_NETPROT | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
972 | Network Protector | SymbolPlacement:GeometryLevel | GEOMLEVEL_NETPROT | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
973 | Network Protector | SymbolPlacement:GeometryType | GEOMTYPE_NETPROT | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
974 | Network Protector | SymbolPlacement:Rotation | ROTATION_NETPROT | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
975 | Network Protector | SymbolPlacement:Size | SIZE_NETPROT | Internals | Size. | Integer | points | points | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
976 | Network Protector | SymbolPlacement:X | WCX_NETPROT | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
977 | Network Protector | SymbolPlacement:X2 | WCX2_NETPROT | Internals | X2 coordinate. | Double | [5 empty] | NAME: X2; Yes: Yes; Yes: No; Yes: Yes; Yes: No
978 | Network Protector | SymbolPlacement:Y | WCY_NETPROT | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
979 | Network Protector | SymbolPlacement:Y2 | WCY2_NETPROT | Internals | Y2 coordinate. | Double | [5 empty] | NAME: Y2; Yes: Yes; Yes: No; Yes: Yes; Yes: No
980 | Network Protector | Telemetered | TELEMETERED_NETPROT | Internals | Flag indicating that the network protector is telemetered. If not defined, the default value is false, meaning the device is not telemetered in SCADA. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
981 | Network Protector | ToNode | TONODE_NETPROT | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
982 | Network Protector | ToStation | TOSUB_NETPROT | Internals | Associated external substation name. This field should only be set if the switch connects two substations together. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
983 | Network Protector | #N/A | NUMGEOM_NETPROT | Externals | Number of geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
984 | Network Protector | #N/A | NUMLABELGEOM_NETPROT | Externals | Number of label geometries. | Integer | #N/A | #N/A | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
985 | NetworkProtector | CompanyName | COMPANYNAME_NETPROT | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
986 | NetworkProtector | County | COUNTY_NETPROT | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
987 | NetworkProtector | LocationDescription | LOCATIONDESCRIPTION_NETPROT | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
988 | NetworkProtector | Municipality | MUNICIPALITY_NETPROT | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
989 | NetworkProtector | State | STATE_NETPROT | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
990 | NetworkProtector | ThirdPartyOwned | THIRDPARTYOWNED_NETPROT | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
991 | NetworkProtector | BusTieSwitch | BUSTIESWITCH_NETPROT | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
992 | Project | CUDAttribute |  | Internals | Create/Update/Delete attribute. Used for incemental updates of substation SSG files. | String | #N/A | #N/A |  |  |  | No: Yes; No: No; No: No; No: No
993 | Project | CUDAttributeSpecified |  | Internals | Specifies whether the Create/Update/Delete attribute has been specified. Used for incemental updates of substation SSG files. | Boolean | #N/A | #N/A |  |  |  | No: Yes; No: No; No: No; No: No
994 | Project | Id | ID_PROJECT | Internals | Commissioning/decommissioning project ID | String | #N/A | #N/A |  |  |  | No: Yes; No: No; No: No; No: No
995 | Project | Stage | NUMSTAGES_PROJECT | Internals | The number of stages in the project | Integer | #N/A | #N/A |  |  |  | No: Yes; No: No; No: No; No: No
996 | Project | Stage Component | NUMCOMPONENTS_PROJECT | Internals | The number of components in the stage | Integer | #N/A | #N/A |  |  |  | No: Yes; No: No; No: No; No: No
997 | Project | Stage Component Future | COMPONENTFUTURE_PROJECT | Internals | Specifies whether the component that is associated with the project stage is in the Future state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NEWATMSK3 | Yes | No | No | No
998 | Project | Stage Component FutureRemove | COMPONENTFUTUREREMOVE_PROJECT | Internals | Specifies whether the component that is associated with the project stage is in the FutureRemoved state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NEWATMSK3 | Yes | No | No | No
999 | Project | Stage Component Id | COMPONENTID_PROJECT | Internals | ID of the component that is associated with the project stage | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1000 | Project | Stage Component Remove | COMPONENTREMOVE_PROJECT | Internals | Specifies whether the component that is associated with the project stage is in the Removed state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NEWATMSK3 | Yes | No | No | No
1001 | Project | Stage Component Type | COMPONENTTYPE_PROJECT | Internals | Type of the component that is associated with the project stage | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1002 | Project | Stage Id | STAGEID_PROJECT | Internals | Commissioning/decommissioning project stage ID | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PROJECTSTAGE | Yes | No | No | No
1003 | Recloser | Address | ADDRESS_RECLOSER | Internals | Recloser address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
1004 | Recloser | AltGrdtrp | ALTGRDTRP_RECLOSER | Internals | Alternate ground trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 5000 | 0 | 5000 | GRDTRIPALT | Yes | Yes | Yes | Yes
1005 | Recloser | AltPhTrip | ALTPHTRIP_RECLOSER | Internals | Alternate phase trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 5000 | 0 | 5000 | PHTRIPALT | Yes | Yes | Yes | Yes
1006 | Recloser | CompanyName | COMPANYNAME_RECLOSER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1007 | Recloser | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID. | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1008 | Recloser | ComputeFlows | COMPUTEFLOWS_RECLOSER | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
1009 | Recloser | County | COUNTY_RECLOSER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1010 | Recloser | CustomField:IsString | CUSTOMFIELDISSTRING_RECLOSER |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1011 | Recloser | CustomField:Name | CUSTOMFIELDNAME_RECLOSER |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1012 | Recloser | CustomField:Value | CUSTOMFIELDVALUE_RECLOSER |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1013 | Recloser | DERId | DERID_RECLOSER |  | The ID of the Distributed Energy Resource (DER) that this protective device connects/disconnects from the electrical network. It is used by the FISR DER blocking functionality. | String | #N/A | #N/A | FISR |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONDER | No | No | No | No
1014 | Recloser | DSOOverride | DSOOVER_RECLOSER | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
1015 | Recloser | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_RECLOSER | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
1016 | Recloser | ExternalInterfaceMember | EXTERNALINTERFACE_RECLOSER | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
1017 | Recloser | FeedMainBound | FEEDMAINBOUND_RECLOSER | Externals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
1018 | Recloser | FromNode | FRNODE_RECLOSER | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
1019 | Recloser | Future | FUTURE_RECLOSER | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
1020 | Recloser | Grdcapbl | GRDCAPBL_RECLOSER | Internals | Flag indicating device has ground trip capability (True = has ground trip capability). | Boolean | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GRDCAP | Yes | Yes | Yes | Yes
1021 | Recloser | Grdtrp | GRDTRP_RECLOSER | Internals | Ground trip rating (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 1 | 5000 | 1 | 5000 | RECGRTRIPAMPS | Yes | Yes | Yes | Yes
1022 | Recloser | Gtnorm | GTNORM_RECLOSER | Internals | Normal status of ground trip (True = enabled). | Boolean | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMGDTRP | Yes | Yes | Yes | Yes
1023 | Recloser | Id | ID_RECLOSER | Internals | Recloser unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1024 | Recloser | IncidentEnergyCat | INCIDENTENERGYCAT_RECLOSER | Internals | Recloser incident energy category. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENERGYCAT.NOAPPSTR | Yes | Yes | Yes | Yes
1025 | Recloser | LabelPlacement:CharacterRotation | LABELCHRROTATION_RECLOSER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1026 | Recloser | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_RECLOSER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1027 | Recloser | LabelPlacement:FontSize | LABELSIZE_RECLOSER | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1028 | Recloser | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_RECLOSER | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1029 | Recloser | LabelPlacement:GeometryType | LABELGEOMTYPE_RECLOSER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1030 | Recloser | LabelPlacement:Rotation | LABELROT_RECLOSER | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1031 | Recloser | LabelPlacement:Text | LABELTEXT_RECLOSER | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1032 | Recloser | LabelPlacement:X | LABELX_RECLOSER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1033 | Recloser | LabelPlacement:Y | LABELY_RECLOSER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1034 | Recloser | LargestCoordFuse | LARGESTCOORDFUSE_RECLOSER | Internals | Largest coordination fuse size (Amps). This field is used in the upstream device coordination check executed in the Protection Validation (PRV) application. | Float | Amps | Amps | OPS |  |  | FALSE | 1 | 600 | 1 | 600 |  | Yes | Yes | Yes | Yes
1035 | Recloser | LoadShedDefaultCircuitClass | LSDEFCLASS_RECLOSER | Internals | Device specific load shed classification | Integer | #N/A | #N/A | SLS | 10 | 0: Ignore 1: Do Not Shed 2-10: Circuit Classification | FALSE | 0 | 10 | 0 | 10 | LOADSHEDDEFCLASS | Yes | Yes | Yes | Yes
1036 | Recloser | LocationDescription | LOCATIONDESCRIPTION_RECLOSER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1037 | Recloser | Maxint | MAXINT_RECLOSER | Internals | Maximum interruption rating (Amps). | Float | Amps | Amps | DPF | User-configurable through Defaults File | Required for DPF. | FALSE | 1 | 50000 | 1 | 50000 | RECINTERRUPTAMPS | Yes | Yes | Yes | Yes
1038 | Recloser | Municipality | MUNICIPALITY_RECLOSER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1039 | Recloser | Name | NAME_RECLOSER | Internals | Recloser display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1040 | Recloser | NeutralCurrentTrip | NEUTRALCURRENTTRIP_RECLOSER | Internals | This field is the neutral trip setting (in Amps) which is checked by the protection validation functions. | Float | Amps | Amps | DPF | 0 |  | FALSE | 0 | 3000 | 0 | 3000 | NEUTRALRELAYTRIPCURRENT | Yes | No | No | No
1041 | Recloser | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_RECLOSER | Internals | Nominal feeder ID for the recloser. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for reclosers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1042 | Recloser | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1043 | Recloser | NomOpMode | NOMOPMODE_RECLOSER | Internals | Nominal operation mode enumeration. | Integer | enumeration | enumeration | OPS | 2 | 0: None 1: Switch_Mode 2: Recloser_Mode 3: Sectionalizer_Mode | FALSE | 0 | 3 | 0 | 3 | RECNOMOPMODE | Yes | Yes | Yes | Yes
1044 | Recloser | NormallyDeenergized | NORMDEENERGIZED_RECLOSER | Internals | Flag indicating that the recloser is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
1045 | Recloser | NormallyLooped | NORMLOOPED_RECLOSER | Internals | Flag indicating that the recloser is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
1046 | Recloser | NormallyNetworkLooped | NORMNETWORKLOOPED_RECLOSER | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1047 | Recloser | NormallyOpen | NOPEN_RECLOSER | Internals | Flag indicating the recloser is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A | NOPEN | Yes | Yes | Yes | Yes
1048 | Recloser | NormallyParallelLooped | NORMPARALLELLOOPED_RECLOSER | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | fasle | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1049 | Recloser | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched reclosers that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_RECLOSER field. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
1050 | Recloser | NoteTCMS | NOTETCMS_RECLOSER | Internals | Notify Outage Management System (OMS) flag. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1051 | Recloser | NumbOps | NUMBOPS_RECLOSER | Internals | Total number of phase reclose operations. | Integer | count | count | DPF | User-configurable through Defaults File | Required for DPF. | FALSE | 1 | 5 | 1 | 5 | NUMPHOPS | Yes | Yes | Yes | Yes
1052 | Recloser | PermitAreaId | PERMITAREAID_RECLOSER | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1053 | Recloser | Phase | PHASE_RECLOSER | Internals | Recloser phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
1054 | Recloser | PhTrip | PHTRIP_RECLOSER | Internals | Phase trip rating (Amps). | Float | Amps | Amps | DPF | User-configurable through Defaults File | Required for DPF. | FALSE | 0 | 3000 | 0 | 3000 | PHTRPAMP | Yes | Yes | Yes | Yes
1055 | Recloser | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1056 | Recloser | SecondId | TROUBLECALLID_RECLOSER | Internals | Alternate recloser ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
1057 | Recloser | ServiceCenter | SERVCNTR_RECLOSER | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
1058 | Recloser | SGTemplate | SGTEMPLATE_RECLOSER | Internals | The associated settings group template | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ASSOCSGTEMPLATE | Yes | Yes | Yes | No
1059 | Recloser | State | STATE_RECLOSER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1060 | Recloser | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
1061 | Recloser | SuppressFeeder |  | Internals | Flag indicating that the device name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1062 | Recloser | SwitchModel | SWMOD_RECLOSER | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
1063 | Recloser | SwitchModelPhA | SWMODA_RECLOSER | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
1064 | Recloser | SwitchModelPhB | SWMODB_RECLOSER | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
1065 | Recloser | SwitchModelPhC | SWMODC_RECLOSER | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
1066 | Recloser | SymbolPlacement:GeometryLevel | GEOMLEVEL_RECLOSER | Internals | Geometry Level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1067 | Recloser | SymbolPlacement:GeometryType | GEOMTYPE_RECLOSER | Internals | Geometry Type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
1068 | Recloser | SymbolPlacement:Rotation | ROTATION_RECLOSER | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | SWPLACE.ROTATION | Yes | Yes | Yes | Yes
1069 | Recloser | SymbolPlacement:Size | SIZE_RECLOSER | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SWPLACE.SIZE | Yes | Yes | Yes | Yes
1070 | Recloser | SymbolPlacement:X | WCX_RECLOSER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X | Yes | Yes | Yes | Yes
1071 | Recloser | SymbolPlacement:X2 | WCX2_RECLOSER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X2 | Yes | No | Yes | No
1072 | Recloser | SymbolPlacement:Y | WCY_RECLOSER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y | Yes | Yes | Yes | Yes
1073 | Recloser | SymbolPlacement:Y2 | WCY2_RECLOSER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y2 | Yes | No | Yes | No
1074 | Recloser | ThirdPartyOwned | THIRDPARTYOWNED_RECLOSER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1075 | Recloser | ToNode | TONODE_RECLOSER | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
1076 | Recloser | ToStation | TOSUB_RECLOSER | Internals | Associated external substation name. This field should only be set if the recloser connects two substations together. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
1077 | Recloser | #N/A | NUMGEOM_RECLOSER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1078 | Recloser | #N/A | NUMLABELGEOM_RECLOSER | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1079 | Recloser | BusTieSwitch | BUSTIESWITCH_RECLOSER | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
1080 | RefBusInterface | CustomField:IsString |  |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1081 | RefBusInterface | CustomField:Name |  |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1082 | RefBusInterface | CustomField:Value |  |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1083 | RefBusInterface | Future | #N/A | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1084 | RefBusInterface | Id | #N/A | Internals | Reference bus unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1085 | RefBusInterface | InterfaceBusVoltage | #N/A | Internals | The default reference bus voltage magnitude in % V. This value is used in the network applications if a voltage magnitude measurement (invalid quality or the measurement does not exist) or a manually entered voltage magnitude value is not available. This value overrides the default voltage magnitude provided in the Converter Options tab. | Float | % | % | DPF, FISR, LVM |  | 80% - 120% | FALSE | 80 | 120 | 80 | 120 | DEINTVOL | Yes | Yes | Yes | Yes
1086 | RefBusInterface | InterfaceBusVoltageAngle | #N/A | Internals | Default interface bus voltange angle (degrees) | Float | #N/A | #N/A | DPF, FISR, LVM |  | -180 - 180 degrees | FALSE | -180 | 180 | -180 | 180 | DINTVANG | Yes | Yes | Yes | Yes
1087 | RefBusInterface | InterfaceBusVoltageRange | #N/A | Internals | Interface Bus Voltage range ( in percentage) | Float | #N/A | #N/A | DPF, FISR, LVM | User-configurable through Converter options. | 0-10% | FALSE | #N/A | #N/A | #N/A | #N/A | INTVOLTRANGE | Yes | Yes | Yes | Yes
1088 | RefBusInterface | InterfaceR0 | #N/A | Internals | System equivalent zero sequence resistance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1089 | RefBusInterface | InterfaceR1 | #N/A | Internals | System equivalent positive sequence resistance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1090 | RefBusInterface | InterfaceR2 | #N/A | Internals | System equivalent negative sequence resistance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1091 | RefBusInterface | InterfaceX0 | #N/A | Internals | System equivalent zero sequence reactance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1092 | RefBusInterface | InterfaceX1 | #N/A | Internals | System equivalent positive sequence reactance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1093 | RefBusInterface | InterfaceX2 | #N/A | Internals | System equivalent negative sequence reactance. | Double | ohms | ohms | DPF |  | If left zero then no interface impedance values in the station will be used for DNAF apps. | FALSE | 0 | 300 | 0 | 300 |  | Yes | Yes | Yes | Yes
1094 | RefBusInterface | IsInterfacewithSwitch | #N/A | Internals | Flag indiactes if the energization status of the sub-station is being determined by SCADA device (switch) connnected to it. | Boolean | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | INTFCSWitch | Yes | Yes | Yes | Yes
1095 | RefBusInterface | IsStudyInterface | #N/A | Internals | Flag indicating the interface is a study only interface. | Boolean | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISSTUDYREFINTFC | Yes | Yes | Yes | Yes
1096 | RefBusInterface | LabelPlacement:FontSize | #N/A | Internals | Font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1097 | RefBusInterface | LabelPlacement:GeometryLevel | #N/A | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1098 | RefBusInterface | LabelPlacement:GeometryType | #N/A | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1099 | RefBusInterface | LabelPlacement:Rotation | #N/A | Internals | Lasbel rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1100 | RefBusInterface | LabelPlacement:Text | #N/A | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1101 | RefBusInterface | LabelPlacement:X | #N/A | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1102 | RefBusInterface | LabelPlacement:Y | #N/A | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1103 | RefBusInterface | Name | #N/A | Internals | Reference bus display name. | String | #N/A | #N/A | OPS |  |  |  | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1104 | RefBusInterface | Node | #N/A | Internals | Associated node name. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NODEID | Yes | Yes | Yes | Yes
1105 | RefBusInterface | PermitAreaId | #N/A | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1106 | RefBusInterface | Phase | #N/A | Internals | Interface phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
1107 | RefBusInterface | ServiceCenter | #N/A | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1108 | RefBusInterface | SymbolPlacement:GeometryLevel | #N/A | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1109 | RefBusInterface | SymbolPlacement:GeometryType | #N/A | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1110 | RefBusInterface | SymbolPlacement:Rotation | #N/A | Internals | Rotation angle. | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1111 | RefBusInterface | SymbolPlacement:Size | #N/A | Internals | Placement size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1112 | RefBusInterface | SymbolPlacement:X | #N/A | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1113 | RefBusInterface | SymbolPlacement:Y | #N/A | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1114 | Regulator Group | CompanyName | COMPANYNAME_REGROUP | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1115 | Regulator Group | County | COUNTY_REGROUP | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1116 | Regulator Group | CustomField:IsString | CUSTOMFIELDISSTRING_REGROUP |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1117 | Regulator Group | CustomField:Name | CUSTOMFIELDNAME_REGROUP |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1118 | Regulator Group | CustomField:Value | CUSTOMFIELDVALUE_REGROUP |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1119 | Regulator Group | Id | ID_REGGROUP | Internals | Regulator group unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1120 | Regulator Group | LabelPlacement:FontSize | LABELSIZE_REGGROUP | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1121 | Regulator Group | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_REGGROUP | Internals | Label geometry level | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1122 | Regulator Group | LabelPlacement:GeometryType | LABELGEOMTYPE_REGGROUP | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1123 | Regulator Group | LabelPlacement:Rotation | LABELROT_REGGROUP | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1124 | Regulator Group | LabelPlacement:Text | LABELTEXT_REGGROUP | Internals | Label geometry text. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1125 | Regulator Group | LabelPlacement:X | LABELX_REGGROUP | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1126 | Regulator Group | LabelPlacement:Y | LABELY_REGGROUP | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1127 | Regulator Group | LocationDescription | LOCATIONDESCRIPTION_REGROUP | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1128 | Regulator Group | Municipality | MUNICIPALITY_REGROUP | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1129 | Regulator Group | Name | NAME_REGGROUP | Internals | Regulator group display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1130 | Regulator Group | NOMINAL_FEEDER_ID_REGROUP | NOMINAL_FEEDER_ID_REGROUP | Internals | Nominal feeder ID for the regulator group. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for regulator groups marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1131 | Regulator Group | PermitAreaId | PERMITAREAID_REGGROUP | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1132 | Regulator Group | State | STATE_REGROUP | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1133 | Regulator Group | SymbolPlacement:GeometryLevel | GEOMLEVEL_REGGROUP | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1134 | Regulator Group | SymbolPlacement:GeometryType | GEOMTYPE_REGGROUP | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1135 | Regulator Group | SymbolPlacement:Rotation | ROTATION_REGGROUP | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1136 | Regulator Group | SymbolPlacement:Size | SIZE_REGGROUP | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1137 | Regulator Group | SymbolPlacement:X | WCX_REGGROUP | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1138 | Regulator Group | SymbolPlacement:X2 | WCX2_REGGROUP | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1139 | Regulator Group | SymbolPlacement:Y | WCY_REGGROUP | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1140 | Regulator Group | SymbolPlacement:Y2 | WCY2_REGGROUP | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1141 | Regulator Group | TfIds | TFIDS_REGGROUP | Internals | Collection of transformer IDs. | String | #N/A | #N/A | DPF |  | Each transformer must exist in the file. | TRUE | #N/A | #N/A | #N/A | #N/A | REGULATORGROUP | Yes | Yes | Yes | Yes
1142 | Regulator Group | ThirdPartyOwned | THIRDPARTYOWNED_REGROUP | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1143 | Regulator Group | #N/A | NUMREG_REGGROUP | Externals | The number of regulators in the group. | Integer | count | count | DPF |  |  | FALSE | 2 | 9 | 2 | 9 | NUMTF | Yes | Yes | Yes | Yes
1144 | Regulator Group | #N/A | NUMGEOM_REGGROUP | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1145 | Regulator Group | #N/A | NUMLABELGEOM_REGGROUP | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1146 | ReservedCapacity | AddReserveCapOnCommonPath | ADDRESERVECAPONCOMMON_RESCAP | Externals | Flag indicating whether the reserved capacity on a device on a path common to both the primary and the alternate feed should be the sum of both reserves combined (True = sum of both reserves). | Boolean | #N/A | #N/A | OPS | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRCONCOMMONPATH | Yes | Yes | Yes | Yes
1147 | ReservedCapacity | CompanyName | COMPANYNAME_RESCAP | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1148 | ReservedCapacity | County | COUNTY_RESCAP | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1149 | ReservedCapacity | FeedResvCap:FeedDeviceId | FEEDDEVICEIDn_RESCAP | Externals | Device Id associated with the feed. The device specified by this field is used as the starting point for upstream trace for that feed. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDDEVICEID | Yes | Yes | Yes | Yes
1150 | ReservedCapacity | FeedResvCap:FeedFirmCommitment | FEEDFIRMCOMMITMENTn_RESCAP | Externals | Flag indicating whether the commitment is firm or not (True = firm).. | Boolean | #N/A | #N/A | OPS | TRUE |  | FALSE |  |  |  |  | FEEDFIRMCOMMITMENT | Yes | Yes | Yes | Yes
1151 | ReservedCapacity | FeedResvCap:FeedLineResvCap | FEEDLINERESVCAPn_RESCAP | Externals | The capacity to be reserved on lines, switching devices, series reactors, and inline-transformers for the corresponding feed. The units are specified in the field FEEDRESVUNIT_RESCAP. | Float | #N/A | #N/A | OPS |  |  | TRUE | 0 | 100000 | 0 | 100000 | FEEDLINERESVCAP | Yes | Yes | Yes | Yes
1152 | ReservedCapacity | FeedResvCap:FeedPowerFactor | FEEDPOWERFACTORn_RESCAP | Externals | The power factor associated with the feed. This value is used only if reserved capacity is specified in kW. | Float | #N/A | #N/A | OPS |  |  | TRUE | 0 | 1 | 0 | 1 | FEEDPOWERFACTOR | Yes | Yes | Yes | Yes
1153 | ReservedCapacity | FeedResvCap:FeedStationResvCap | FEEDSTATIONRESVCAPn_RESCAP | Externals | The capacity to be reserved on the station power transformer for the corresponding feed. The units are specified in the field FEEDRESVUNIT_RESCAP. | Float | #N/A | #N/A | OPS |  |  | TRUE | 0 | 100000 | 0 | 100000 | FEEDSTATIONRESVCAP | Yes | Yes | Yes | Yes
1154 | ReservedCapacity | FeedResvUnit | FEEDRESVUNIT_RESCAP | Externals | Enumerated units for the specified reserved capacities. 1 = kW; 2 = kVA. The default value is 1. | Integer | #N/A | #N/A | OPS | 1 | 1: kW 2: kVA | FALSE | #N/A | #N/A | #N/A | #N/A | UNITS | Yes | Yes | Yes | Yes
1155 | ReservedCapacity | FullReserveCapOnParallelPaths | FULLRESERVECAPONPARALLELPATHS_RESCAP | Externals | Flag indicating whether the full reserved capacity should be considered on all branches of a parallel upstream supply path (True = consider parallel supply path). | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FULLRCONPARALLELPATH | Yes | Yes | Yes | Yes
1156 | ReservedCapacity | Future | FUTURE_RESCAP | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1157 | ReservedCapacity | Id | ID_RESCAP | Internals | Reserved capacity unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1158 | ReservedCapacity | LabelPlacement:CharacterRotation | LABELCHRROTATION_RESCAP | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1159 | ReservedCapacity | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_RESCAP | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1160 | ReservedCapacity | LabelPlacement:FontSize | LABELSIZE_RESCAP | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1161 | ReservedCapacity | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_RESCAP | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1162 | ReservedCapacity | LabelPlacement:GeometryType | LABELGEOMTYPE_RESCAP | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1163 | ReservedCapacity | LabelPlacement:Rotation | LABELROT_RESCAP | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1164 | ReservedCapacity | LabelPlacement:Text | LABELTEXT_RESCAP | Internals | Label geometry text. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1165 | ReservedCapacity | LabelPlacement:X | LABELX_RESCAP | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1166 | ReservedCapacity | LabelPlacement:Y | LABELY_RESCAP | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1167 | ReservedCapacity | LoadIds | LOADIDSn_RESCAP | Externals | The load IDs associated with the reserved capacity feeds. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOADIDS | Yes | Yes | Yes | Yes
1168 | ReservedCapacity | LocationDescription | LOCATIONDESCRIPTION_RESCAP | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1169 | ReservedCapacity | Municipality | MUNICIPALITY_RESCAP | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1170 | ReservedCapacity | Name | NAME_RESCAP | Internals | Reserved capacity display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1171 | ReservedCapacity | NOMINAL_FEEDER_ID_RESCAP | NOMINAL_FEEDER_ID_RESCAP | Internals | Nominal feeder ID for the reserve capacity. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for reserved capacity objects marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1172 | ReservedCapacity | PermitAreaId | PERMITAREAID_RESCAP | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1173 | ReservedCapacity | Phase | PHASE_RESCAP | Internals | Phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, or ABCN. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1174 | ReservedCapacity | ServiceCenter | SERVCNTR_RESCAP | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1175 | ReservedCapacity | State | STATE_RESCAP | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1176 | ReservedCapacity | SymbolPlacement:GeometryLevel | GEOMLEVEL_RESCAP | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1177 | ReservedCapacity | SymbolPlacement:GeometryType | GEOMTYPE_RESCAP | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1178 | ReservedCapacity | SymbolPlacement:Rotation | ROTATION_RESCAP | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1179 | ReservedCapacity | SymbolPlacement:Size | SIZE_RESCAP | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1180 | ReservedCapacity | SymbolPlacement:X | WCX_RESCAP | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1181 | ReservedCapacity | SymbolPlacement:X2 | WCX2_RESCAP | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1182 | ReservedCapacity | SymbolPlacement:Y | WCY_RESCAP | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1183 | ReservedCapacity | SymbolPlacement:Y2 | WCY2_RESCAP | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1184 | ReservedCapacity | ThirdPartyOwned | THIRDPARTYOWNED_RESCAP | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1185 | ReservedCapacity | #N/A | NUMGEOM_RESCAP | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1186 | ReservedCapacity | #N/A | NUMLABELGEOM_RESCAP | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1187 | Sectionalizer | Address | ADDRESS_SECT | Internals | Sectionalizer address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
1188 | Sectionalizer | CompanyName | COMPANYNAME_SECT | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1189 | Sectionalizer | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1190 | Sectionalizer | ComputeFlows | COMPUTEFLOWS_SECT | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
1191 | Sectionalizer | County | COUNTY_SECT | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1192 | Sectionalizer | CustomField:IsString | CUSTOMFIELDISSTRING_SECT |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1193 | Sectionalizer | CustomField:Name | CUSTOMFIELDNAME_SECT |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1194 | Sectionalizer | CustomField:Value | CUSTOMFIELDVALUE_SECT |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1195 | Sectionalizer | DSOOverride | DSOOVER_SECT | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
1196 | Sectionalizer | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_SECT | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
1197 | Sectionalizer | ExternalInterfaceMember | EXTERNALINTERFACE_SECT | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
1198 | Sectionalizer | FeedMainBound | FEEDMAINBOUND_SECT | Externals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS, NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
1199 | Sectionalizer | Future | FUTURE_SECT | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
1200 | Sectionalizer | Id | ID_SECT | Internals | Sectionalizer unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1201 | Sectionalizer | LabelPlacement:CharacterRotation | LABELCHRROTATION_SECT | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1202 | Sectionalizer | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SECT | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1203 | Sectionalizer | LabelPlacement:FontSize | LABELSIZE_SECT | Internals | Label fFont size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1204 | Sectionalizer | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SECT | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1205 | Sectionalizer | LabelPlacement:GeometryType | LABELGEOMTYPE_SECT | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1206 | Sectionalizer | LabelPlacement:Rotation | LABELROT_SECT | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1207 | Sectionalizer | LabelPlacement:Text | LABELTEXT_SECT | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1208 | Sectionalizer | LabelPlacement:X | LABELX_SECT | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1209 | Sectionalizer | LabelPlacement:Y | LABELY_SECT | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1210 | Sectionalizer | LocationDescription | LOCATIONDESCRIPTION_SECT | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1211 | Sectionalizer | Municipality | MUNICIPALITY_SECT | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1212 | Sectionalizer | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_SECT | Internals | Nominal feeder ID for the sectionalizer. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for sectionalizers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1213 | Sectionalizer | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1214 | Sectionalizer | NormallyDeenergized | NORMDEENERGIZED_SECT | Internals | Flag indicating that the sectionalizer is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
1215 | Sectionalizer | NormallyLooped | NORMLOOPED_SECT | Internals | Flag indicating that the sectionalizer is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
1216 | Sectionalizer | NormallyNetworkLooped | NORMNETWORKLOOPED_SECT | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1217 | Sectionalizer | NormallyParallelLooped | NORMPARALLELLOOPED_SECT | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1218 | Sectionalizer | PermitAreaId | PERMITAREAID_SECT | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1219 | Sectionalizer | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1220 | Sectionalizer | SecondId | TROUBLECALLID_SECT | Internals | Alternate sectionalizer ID. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
1221 | Sectionalizer | ServiceCenter | SERVCNTR_SECT | Internals | Associated service center. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
1222 | Sectionalizer | State | STATE_SECT | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1223 | Sectionalizer | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
1224 | Sectionalizer | SuppressFeeder |  | Internals | Flag indicating that the device name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1225 | Sectionalizer | SymbolPlacement:GeometryLevel | GEOMLEVEL_SECT | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1226 | Sectionalizer | SymbolPlacement:GeometryType | GEOMTYPE_SECT | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
1227 | Sectionalizer | SymbolPlacement:Rotation | ROTATION_SECT | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | SWPLACE.ROTATION | Yes | Yes | Yes | Yes
1228 | Sectionalizer | SymbolPlacement:Size | SIZE_SECT | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SWPLACE.SIZE | Yes | Yes | Yes | Yes
1229 | Sectionalizer | SymbolPlacement:X | WCX_SECT | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X | Yes | Yes | Yes | Yes
1230 | Sectionalizer | SymbolPlacement:X2 | WCX2_SECT | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X2 | Yes | No | Yes | No
1231 | Sectionalizer | SymbolPlacement:Y | WCY_SECT | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y | Yes | Yes | Yes | Yes
1232 | Sectionalizer | SymbolPlacement:Y2 | WCY2_SECT | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y2 | Yes | No | Yes | No
1233 | Sectionalizer | ThirdPartyOwned | THIRDPARTYOWNED_SECT | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1234 | Sectionalizer | ToStation | TOSUB_SECT | Internals | Associated external substation name. This field should only be set if the sectionalizer connects two substations together. | String | #N/A | #N/A | OPS |  | The station name is checked against the stations list read from the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
1235 | Sectionalizer | #N/A | NUMGEOM_SECT | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1236 | Sectionalizer | #N/A | NUMLABELGEOM_SECT | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1237 | Sectionalizer | Counts | COUNTS_SECT | Internals | Counts (reclose operations) before device opens. | Integer | count | count | DPF | User-configurable through Defaults File |  | FALSE |  |  |  |  | COUNT | Yes | Yes | Yes | Yes
1238 | Sectionalizer | FromNode | FRNODE_SECT | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
1239 | Sectionalizer | Name | NAME_SECT | Internals | Sectionalizer display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1240 | Sectionalizer | NormallyOpen | NOPEN_SECT | Internals | Flag indicating the sectionalizer is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS, NTP |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A | NOPEN | Yes | Yes | Yes | Yes
1241 | Sectionalizer | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched sectionalizers that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_SECT field. | String | #N/A | #N/A | OPS, NTP |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
1242 | Sectionalizer | Phase | PHASE_SECT | Internals | Sectionalizer phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
1243 | Sectionalizer | SwitchModel | SWMOD_SECT | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
1244 | Sectionalizer | SwitchModelPhA | SWMODA_SECT | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
1245 | Sectionalizer | SwitchModelPhB | SWMODB_SECT | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
1246 | Sectionalizer | SwitchModelPhC | SWMODC_SECT | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
1247 | Sectionalizer | ToNode | TONODE_SECT | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
1248 | Sectionalizer | BusTieSwitch | BUSTIESWITCH_SECT | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
1249 | SensorLocation | CustomField:IsString | CUSTOMFIELDISSTRING_SENLOC |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1250 | SensorLocation | CustomField:Name | CUSTOMFIELDNAME_SENLOC |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1251 | SensorLocation | CustomField:Value | CUSTOMFIELDVALUE_SENLOC |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1252 | SensorLocation | FlowBranchId | FLOWBRANCHID_SENLOC | Internals | Branch ID used for measurements. The input branch must match the input node above. | String | #N/A | #N/A | OPS |  |  | MODEL: FLOWBRANCHID; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1253 | SensorLocation | Future | FUTURE_SENLOC | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BC, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1254 | SensorLocation | Id | ID_SENLOC | Internals | SensorLocation unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1255 | SensorLocation | LabelPlacement:FontSize | LABELSIZE_SENLOC | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1256 | SensorLocation | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SENLOC | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1257 | SensorLocation | LabelPlacement:GeometryType | LABELGEOMTYPE_SENLOC | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1258 | SensorLocation | LabelPlacement:Rotation | LABELROT_SENLOC | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1259 | SensorLocation | LabelPlacement:Text | LABELTEXT_SENLOC | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1260 | SensorLocation | LabelPlacement:X | LABELX_SENLOC | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1261 | SensorLocation | LabelPlacement:Y | LABELY_SENLOC | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1262 | SensorLocation | Name | NAME_SENLOC | Internals | SensorLocation display name. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1263 | SensorLocation | Node | NODE_SENLOC | Internals | Associated node ID. | [6 empty] | NAME: NODENUM; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1264 | SensorLocation | PermitAreaId | PERMITAREAID_SENLOC | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1265 | SensorLocation | Phase | PHASE_SENLOC | Internals | SensorLocation phase connections. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PHASING | Yes | Yes | Yes | Yes
1266 | SensorLocation | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1267 | SensorLocation | SensorType | SENSORTYPE_SENLOC | Internals | SensorLocation type enumeration. The following values are used: 0 = normal sensor, 1 = sensor with fault status measurement. | Integer | #N/A | #N/A | OPS |  | 0: Normal Sensor 1: Sensor with Fault Status Measurement | FALSE | 0 | 1 | 0 | 1 | SENSORTYPE | Yes | Yes | Yes | Yes
1268 | SensorLocation | ServiceCenter | SERVCNTR_SENLOC | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1269 | SensorLocation | SymbolPlacement:GeometryLevel | GEOMLEVEL_SENLOC | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1270 | SensorLocation | SymbolPlacement:GeometryType | GEOMTYPE_SENLOC | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1271 | SensorLocation | SymbolPlacement:Rotation | ROTATION_SENLOC | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1272 | SensorLocation | SymbolPlacement:Size | SIZE_SENLOC | Internals | Size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1273 | SensorLocation | SymbolPlacement:X | WCX_SENLOC | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1274 | SensorLocation | SymbolPlacement:X2 | WCX2_SENLOC | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X2 | Yes | No | Yes | No
1275 | SensorLocation | SymbolPlacement:Y | WCY_SENLOC | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1276 | SensorLocation | SymbolPlacement:Y2 | WCY2_SENLOC | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y2 | Yes | No | Yes | No
1277 | SensorLocation | #N/A | NUMGEOM_SENLOC | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1278 | SensorLocation | #N/A | NUMLABELGEOM_SENLOC | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1279 | Series Reactor | Address | ADDRESS_SERIES | Internals | Series reactor address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
1280 | Series Reactor | CompanyName | COMPANYNAME_SERIES | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1281 | Series Reactor | County | COUNTY_SERIES | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1282 | Series Reactor | CustomField:IsString | CUSTOMFIELDISSTRING_SERIES |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1283 | Series Reactor | CustomField:Name | CUSTOMFIELDNAME_SERIES |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1284 | Series Reactor | CustomField:Value | CUSTOMFIELDVALUE_SERIES |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1285 | Series Reactor | FromNode | FRNODE_SERIES | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
1286 | Series Reactor | Future | FUTURE_SERIES | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank | FALSE | #N/A | #N/A | #N/A | #N/A | FUTUREPHASES | Yes | Yes | Yes | Yes
1287 | Series Reactor | Id | ID_SERIES | Internals | Series reactor unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1288 | Series Reactor | KV_UNITS | #N/A | Internals | Enumeration indicating voltage is measured line to line or line to neutral. In the Converter, the NomKV field is adjusted to a line to ground value if it is provided Line-to-Line. | String | enumeration | enumeration | OPS | Line_to_Line | Line_to_Line or Line_to_Ground | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1289 | Series Reactor | LabelPlacement:CharacterRotation | LABELCHRROTATION_SERIES | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1290 | Series Reactor | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SERIES | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1291 | Series Reactor | LabelPlacement:FontSize | LABELSIZE_SERIES | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1292 | Series Reactor | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SERIES | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1293 | Series Reactor | LabelPlacement:GeometryType | LABELGEOMTYPE_SERIES | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1294 | Series Reactor | LabelPlacement:Rotation | LABELROT_SERIES | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1295 | Series Reactor | LabelPlacement:Text | LABELTEXT_SERIES | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1296 | Series Reactor | LabelPlacement:X | LABELX_SERIES | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1297 | Series Reactor | LabelPlacement:Y | LABELY_SERIES | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1298 | Series Reactor | LocationDescription | LOCATIONDESCRIPTION_SERIES | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1299 | Series Reactor | Municipality | MUNICIPALITY_SERIES | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1300 | Series Reactor | Name | NAME_SERIES | Internals | Series reactor display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1301 | Series Reactor | NomKV | NOMKV_SERIES | Internals | Rated voltage (kV). | Float | kV | kV | DPF |  |  | TRUE | 1 | 40 | 1 | 40 | NOMVOLT | Yes | Yes | Yes | Yes
1302 | Series Reactor | NormallyDeenergized | NORMDEENERGIZED_SERIES | Internals | Flag indicating that the series reactor is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
1303 | Series Reactor | NormallyLooped | NORMLOOPED_SERIES | Internals | Flag indicating that the series reactor is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
1304 | Series Reactor | NormallyNetworkLooped | NORMNETWORKLOOPED_SERIES | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1305 | Series Reactor | NormallyParallelLooped | NORMPARALLELLOOPED_SERIES | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1306 | Series Reactor | PermitAreaId | PERMITAREAID_SERIES | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1307 | Series Reactor | Phase | PHASE_SERIES | Internals | Series reactor phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
1308 | Series Reactor | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1309 | Series Reactor | SeriesModel | SERIESMOD_SERIES | Internals | Associated series reactor model name. | String | #N/A | #N/A | DPF |  | The series reactor model name must match a series reactor model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL.NAME | Yes | Yes | Yes | Yes
1310 | Series Reactor | ServiceCenter | SERVCNTR_SERIES | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1311 | Series Reactor | State | STATE_SERIES | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1312 | Series Reactor | SuppressFeeder |  | Internals | Flag indicating that the device name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1313 | Series Reactor | SymbolPlacement:GeometryLevel | GEOMLEVEL_SERIES | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1314 | Series Reactor | SymbolPlacement:GeometryType | GEOMTYPE_SERIES | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1315 | Series Reactor | SymbolPlacement:Rotation | ROTATION_SERIES | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1316 | Series Reactor | SymbolPlacement:Size | SIZE_SERIES | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1317 | Series Reactor | SymbolPlacement:X | WCX_SERIES | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1318 | Series Reactor | SymbolPlacement:X2 | WCX2_SERIES | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1319 | Series Reactor | SymbolPlacement:Y | WCY_SERIES | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1320 | Series Reactor | SymbolPlacement:Y2 | WCY2_SERIES | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1321 | Series Reactor | ThirdPartyOwned | THIRDPARTYOWNED_SERIES | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1322 | Series Reactor | ToNode | TONODE_SERIES | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
1323 | Series Reactor | ToStation | TOSUB_TF | Internals | Associated external substation name. This field should only be set if the transformer connects two substations together. | String | #N/A | #N/A | OPS |  | The station name is checked against the stations list read from the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | EXTSBNME | Yes | Yes | Yes | Yes
1324 | Series Reactor | #N/A | NUMGEOM_SERIES | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1325 | Series Reactor | #N/A | NUMLABELGEOM_SERIES | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1326 | ServicePoint | CustomerCount | CUSTOMER_SERVPNT | Internals | Customer count. | Integer | #N/A | #N/A | OPS |  |  | FALSE | 1 | 5000 | 1 | 5000 | SPNUMCST | Yes | Yes | Yes | Yes
1327 | ServicePoint | CustomField:IsString | CUSTOMFIELDISSTRING_SERVPNT |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1328 | ServicePoint | CustomField:Name | CUSTOMFIELDNAME_SERVPNT |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1329 | ServicePoint | CustomField:Value | CUSTOMFIELDVALUE_SERVPNT |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1330 | ServicePoint | Id | ID_SERVPNT | Internals | Service Point ID. | String | #N/A | #N/A | OPS |  | It must match the ID in customer file. | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1331 | ServicePoint | Name | NAME_SERVPNT | Internals | Service Point name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1332 | ServicePoint | Node | NODE_SERVPNT | Internals | Connection node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | CNCTNODE | Yes | Yes | Yes | Yes
1333 | ServicePoint | PermitAreaId | PERMITAREAID_SERVPNT | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1334 | ServicePoint | Wcx | WCX_SERVPNT | Internals | World X coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | X | Yes | Yes | Yes | Yes
1335 | ServicePoint | Wcx2 | WCX2_SERVPNT | Internals | World X2 coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | X2 | Yes | No | Yes | No
1336 | ServicePoint | Wcy | WCY_SERVPNT | Internals | World Y coordinate. | Double | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y | Yes | Yes | Yes | Yes
1337 | ServicePoint | Wcy2 | WCY2_SERVPNT | Internals | World Y2 coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y2 | Yes | No | Yes | No
1338 | SettingGroupTemplate | GroundTrip | SGGROUNDTRIPn_SGTEMPLATE | Internals | Ground trip rating (Amps). | Float | Amps | Amps |  |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1339 | SettingGroupTemplate | Id | SETGRPIDn_SGTEMPLATE | Internals | ID of the associated settings group | Integer | #N/A | #N/A |  |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1340 | SettingGroupTemplate | PhaseTrip | SGPHASETRIPn_SGTEMPLATE | Internals | Phase trip rating (Amps). | Float | Amps | Amps |  |  |  |  | 0 | 3000 | 0 | 3000 |  | Yes | Yes | Yes | No
1341 | SettingGroupTemplate | ProtectionSettingGroups | NUMSETTINGSGROUPS_SGTEMPLATE | Internals | Number of settings groups associated with the template | Integer | #N/A | #N/A |  |  |  | Y: NUMSETTINGGROUPS; Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1342 | SettingGroupTemplate | ScadaIndex | SCINDEXn_SGTEMPLATE | Internals | Settings group value (index) | Integer | #N/A | #N/A |  |  |  |  | 0 | 3000 | 0 | 3000 |  | Yes | Yes | Yes | No
1343 | SettingGroupTemplate | SettingName | SETGRPNAMEn_SGTEMPLATE | Internals | Name of the associated settings group | String | #N/A | #N/A |  |  |  | Y: SETTINGGROUPS; Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1344 | SettingGroupTemplate | SGDescription | DESCRIPTION_SGTEMPLATE | Internals | Template description | String | #N/A | #N/A |  |  |  | Y: SGTDESCRIPTION; Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1345 | SettingGroupTemplate | SGID | ID_SGTEMPLATE | Internals | Template ID | Integer | #N/A | #N/A |  |  |  | Y: ID; Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1346 | SettingGroupTemplate | SGMode | MODEn_SGTEMPLATE | Internals | Settings group mode (unknown, switch, sectionalizer, recloser, or custom) | Integer | #N/A | #N/A |  |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1347 | SettingGroupTemplate | SGName | NAME_SGTEMPLATE | Internals | Template name | String | #N/A | #N/A |  |  |  | Y: NAME; Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1348 | SettingGroupTemplate | SGTransition | TRANSITIONn_SGTEMPLATE | Internals | Settings group possible transitions | Integer | #N/A | #N/A |  |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: No
1349 | Shunt Impedance | Address | ADDRESS_SHIMP | Internals | Address for shunt impedance. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
1350 | Shunt Impedance | CapacitorBankLinkID | #N/A | Internals | Linked capacitor bank ID. | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a capacitor bank The format is ID=LinkNumber where the ID is the ID given in the CapacitorBankLinkID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1351 | Shunt Impedance | CapControlSystem | CAPCONTROLSYSTEM_SHIMP | Internals | Enumeration indicating the type of contol communicationmechanism ( 0 - None, 1 - 1 way Communication Capacitors , 2 - 2-Way Communication Capacitors). | Integer | enumeration | enumeration | DPF |  |  | FALSE | 0 | 2 | 0 | 2 | CAPCONTROLSYSTEM | Yes | Yes | Yes | Yes
1352 | Shunt Impedance | CellSize | CELLSIZE_SHIMP | Internals | The size of the individual units that make up the bank (kVAR). | Float | kVAR | kVAR | DPF, LVM |  |  | FALSE | 0 | Qtotal | 0 | Qtotal | CELLSIZE | Yes | Yes | Yes | Yes
1353 | Shunt Impedance | CompanyName | COMPANYNAME_SHIMP | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1354 | Shunt Impedance | Consecsw | CONSECSW_SHIMP | Internals | Time interval between consecutive switching operations (hours). | Float | hour | hour | DPF | User-configurable through Defaults File |  | FALSE | 0 | 48 | 0 | 48 | CONSSWIT | Yes | Yes | Yes | Yes
1355 | Shunt Impedance | Controllable | CONTROLABLE_SHIMP | Internals | Control capability enumeration (if any). The field has the following values: 0 = Fixed, 1 = Local only, 2 = Remote only, 3 = Remote with local override. | Integer | enumeration | enumeration | DPF, LVM |  | 0: Fixed 1: Local Only 2: Remote Only 3: Reote with Local | FALSE | 0 | 3 | 0 | 3 | CONTROL | Yes | Yes | Yes | Yes
1356 | Shunt Impedance | ControlOverrideType | CTRLOVERRIDETYPE_SHIMP | Internals | Enumeration indicating the type of local controller override capability (0 - None, 1 - Voltage, 2 - Time, 3 - Temperature). | String | #N/A | #N/A | OPS, DPF, LVM |  | 0: None 1: Voltage 2: Time 3: Temperature | FALSE | #N/A | #N/A | #N/A | #N/A | CTRLOVERTYPE | Yes | Yes | Yes | Yes
1357 | Shunt Impedance | County | COUNTY_SHIMP | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1358 | Shunt Impedance | CtrlType | CTRLTYPE_SHIMP | Internals | Associated local controller type enumeration. The field has the following values: 0 = none, 1 = power factor, 2 = time dependent, 3 = temperature dependent, 4 = VAR dependent, 5 = current dependent, 6 = voltage dependent, 7 = Time Remote. | Integer | enumeration | enumeration | DPF, LVM |  | 0: None 1: Power Factor 2: Time 3: Temperature 4: VAR 5: Current (Amps) 6: Voltage 7: Time (Remote) | FALSE | 1 | 7 | 1 | 7 | LOCLCTRL | Yes | Yes | Yes | Yes
1359 | Shunt Impedance | CustomField:IsString | CUSTOMFIELDISSTRING_SHIMP |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1360 | Shunt Impedance | CustomField:Name | CUSTOMFIELDNAME_SHIMP |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1361 | Shunt Impedance | CustomField:Value | CUSTOMFIELDVALUE_SHIMP |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1362 | Shunt Impedance | DSOOverride | DSOOVER_SHIMP | Internals | Eligibility override enumeration of the normal rules for the advanced applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
1363 | Shunt Impedance | ExternalId | EXTERNALID_SHIMP | Internals | External Id of Capacitor.This information currently is not used by DMS Application. It is provided to be used by any other application that might uses the source data. | String | #N/A | #N/A | OPS |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1364 | Shunt Impedance | Future | FUTURE_SHIMP | Internals | Individual phases that are constructed but not energized. | String | hour | #N/A | OPS, NTP | “” | A, B, C, AB, BC, CA, ABC, or blank. | FALSE | 0 | 48 | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1365 | Shunt Impedance | Grounded | GROUNDED_SHIMP | Internals | Flag indicating load is grounded (True = grounded). | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPGROUNDED | Yes | Yes | Yes | Yes
1366 | Shunt Impedance | HighOverride | HIGHTLEVELOVER_SHIMP | Internals | The high time or temperature override value for locally controlled shunt impedances that have an override feature. If the control value is above this value, the shunt impedance is turned on regardless of other controller settings. | Float | #N/A | #N/A | OPS, LVM |  |  | FALSE |  |  |  |  | HTLEVOVER | Yes | Yes | Yes | Yes
1367 | Shunt Impedance | HighVoltOverride | HIGHLEVELOVER_SHIMP | Internals | The high voltage override value (in per unit) for locally controlled shunt impedances that have an override feature. If the control value is above this value, the shunt impedance is turned on regardless of other controller settings. CONFIRM | Float | per unit volt | per unit volt | OPS, DPF, LVM |  |  | FALSE | 0.8 | 1.2 | 0.8 | 1.2 | HLEVOVER | Yes | Yes | Yes | Yes
1368 | Shunt Impedance | Id | ID_SHIMP | Internals | Shunt impedance (capacitor or inductor) unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1369 | Shunt Impedance | KV_UNITS | #N/A | Internals | Enumeration indicating voltage is measured line to line or line to neutral. In the Converter, the NomKV field is adjusted to a line to ground value if it is provided Line-to-Line. | String | enumeration | enumeration | OPS | Line_to_Line | Line_to_Line or Line_to_Ground | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1370 | Shunt Impedance | LabelPlacement:CharacterRotation | LABELCHRROTATION_SHIMP | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1371 | Shunt Impedance | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SHIMP | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1372 | Shunt Impedance | LabelPlacement:FontSize | LABELSIZE_SHIMP | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1373 | Shunt Impedance | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SHIMP | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1374 | Shunt Impedance | LabelPlacement:GeometryType | LABELGEOMTYPE_SHIMP | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1375 | Shunt Impedance | LabelPlacement:Rotation | LABELROT_SHIMP | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1376 | Shunt Impedance | LabelPlacement:Text | LABELTEXT_SHIMP | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1377 | Shunt Impedance | LabelPlacement:X | LABELX_SHIMP | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1378 | Shunt Impedance | LabelPlacement:Y | LABELY_SHIMP | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1379 | Shunt Impedance | LocalOverride | LOCALOVERRIDE_SHIMP | Internals | Flag indicating the locally controlled capacitor has voltage override capability (True = has override capability). Note : Now this field is deprecated for capacitor. | Boolean | #N/A | #N/A | OPS, DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | HLLEVOVER | Yes | Yes | Yes | Yes
1380 | Shunt Impedance | LocalPerm | LOCALPERM_SHIMP | Internals | Enumeration indicating the type of local controller permissive operation (0 - None, 1 - Time, 2 - Temperature). | Integer | #N/A | #N/A | OPS |  | 0: None 1: Time 2: Temperature | FALSE | #N/A | #N/A | #N/A | #N/A | PERMCTRLTYPE | Yes | Yes | Yes | Yes
1381 | Shunt Impedance | LocationDescription | LOCATIONDESCRIPTION_SHIMP | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1382 | Shunt Impedance | LowOverride | LOWTLEVELOVER_SHIMP | Internals | The low time or temperature override value for locally controlled shunt impedances that have an override feature. If the control value is below this value, the shunt impedance is turned on regardless of other controller settings. | Float | #N/A | #N/A | OPS, LVM |  |  | FALSE |  |  |  |  | LTLEVOVER | Yes | Yes | Yes | Yes
1383 | Shunt Impedance | LowVoltOverride | LOWLEVELOVER_SHIMP | Internals | The low voltage override value (in per unit) for locally controlled shunt impedances that have an override feature. If the control value is below this value, the shunt impedance is turned on regardless of other controller settings. CONFIRM | Float | per unit volt | per unit volt | OPS, DPF, LVM |  |  | FALSE | 0.8 | 1.2 | 0.8 | 1.2 | LLEVOVER | Yes | Yes | Yes | Yes
1384 | Shunt Impedance | MaxSwitches | MAXSWITCHES_SHIMP | Internals | Maximum number of daily switching operations. | Integer | #N/A | #N/A | DPF, LVM | User-configurable through Defaults File |  | FALSE | 0 | 20 | 0 | 20 | MAXSWIT | Yes | Yes | Yes | Yes
1385 | Shunt Impedance | Municipality | MUNICIPALITY_SHIMP | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1386 | Shunt Impedance | Name | NAME_SHIMP | Internals | Shunt impedance display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1387 | Shunt Impedance | Node | NODE_SHIMP | Internals | Associated node ID. | String | #N/A | #N/A | OPS |  | A node ID must be given. | TRUE | #N/A | #N/A | #N/A | #N/A | NODENUM | Yes | Yes | Yes | Yes
1388 | Shunt Impedance | NOMINAL_FEEDER_ID_SHIMP | NOMINAL_FEEDER_ID_SHIMP | Internals | Nominal feeder ID for the capacitor. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for capacitors marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1389 | Shunt Impedance | NomKV | NOMKV_SHIMP | Internals | Rated voltage (kV). | Float | kV | kV | DPF, LVM |  |  | TRUE | 1 | 300 | 1 | 300 | NOMVOLT | Yes | Yes | Yes | Yes
1390 | Shunt Impedance | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. | String | #N/A | #N/A | OPS, NTP |  | A, B, C, AB, AC, BC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
1391 | Shunt Impedance | NumSteps | NUMSTEPS_SHIMP | Internals | The number of steps for the controller. A fixed bank has one step. A switched bank that is either all on or all off also has one step. | Integer | count | count | DPF, LVM | User-configurable through Defaults File |  | FALSE | 1 | 50 | 1 | 50 | NUMSTEPS | Yes | Yes | Yes | Yes
1392 | Shunt Impedance | OffLevel | OFFLEVEL_SHIMP | Internals | Upper control setting for controller types 1, 3, 4, 5, and 6. For Amp and VAR capacitors, OFFLEVEL is the sum of OFF Amp / VAR values for the sensing phases. For PF capacitors, the resultant OFFLEVEL PF is calculated only for the OFF values of the sensing phases as follows (assuming ABC is the sensing phase): ± (PA + PB + PC) / √((PA + PB + PC)2 + (QA + QB + QC)2) For Voltage capacitors, the OFFLEVEL is the average of the sensing phase OFF voltages (p.u.). Please note that the state of the shunt device above and below the ON level and OFF level thresholds can be configured using the DNAF Configuration Editor. Please refer to chapter 5 of the Distribution Network Analysis Functions (DNAF) Analyst and Configuration Editor User's Guide for more details. | String | Amps, kVAR, Volt p.u., or PFactor | Amps, kVAR, Volt p.u., or PFactor | DPF, LVM |  | For voltage controller, set the OFFLEVEL in p.u. | FALSE | -1.0/0.8/0:00 | 1.0/1.2/23:00 | -1.0/0.8/0:00 | 1.0/1.2/23:00 | OFFLEVEL | Yes | Yes | Yes | Yes
1393 | Shunt Impedance | OnLevel | ONLEVEL_SHIMP | Internals | Lower control setting for controller types 1, 3, 4, 5, and 6. For Amp and VAR capacitors, ONLEVEL is the sum of ON Amp / VAR values of the sensing phases. For PF capacitors, the resultant ONLEVEL PF is calculated ONLY for the ON values of sensing phases as follows (assuming ABC is the sensing phase): ± (PA + PB + PC) / √((PA + PB + PC)2 + (QA + QB + QC)2) For Voltage capacitors, the ONLEVEL is the average of the sensing phase ON voltages (p.u.). Please note that the state of the shunt device above and below the ON level and OFF level thresholds can be configured using the DNAF Configuration Editor. Please refer to chapter 5 of the Distribution Network Analysis Functions (DNAF) Analyst and Configuration Editor User's Guide for more details. | String | Amps, kVAR, Volt p.u., or PFactor | Amps, kVAR, Volt p.u., or PFactor | DPF, LVM |  | For voltage controller, set the ONLEVEL in p.u. | FALSE | -1.0/0.8/0:00 | 1.0/1.2/23:00 | -1.0/0.8/0:00 | 1.0/1.2/23:00 | ONLEVEL | Yes | Yes | Yes | Yes
1394 | Shunt Impedance | OpenFixed | OPENFIXED_SHIMP | Internals | Connection status for fixed capacitors (True = open). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | OPENFIX | Yes | Yes | Yes | Yes
1395 | Shunt Impedance | OverrideSchedule | OVERRIDESCHED_SHIMP | Internals | For time or temperature override control, the associated on/off schedule name (in the global resources data). | String | #N/A | #N/A | DPF, LVM | “” | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPOVERSCHEDULE | Yes | Yes | Yes | Yes
1396 | Shunt Impedance | PermCtrlLevel1 | PERMCTRLLEVEL1_SHIMP | Internals | The permissive control level 1 value for locally controlled shunt impedances that have a permissive feature. If the control value is out of the range defined by level 1 and level 2, the device is OFF. | Float | #N/A | #N/A | OPS, LVM |  |  | FALSE | -100 | 200 | -100 | 200 | PERMCTRLLEV1 | Yes | Yes | Yes | Yes
1397 | Shunt Impedance | PermCtrlLevel2 | PERMCTRLLEVEL2_SHIMP | Internals | The permissive control level 2 value for locally controlled shunt impedances that have a permissive feature. If the control value is out of the range defined by level 1 and level 2, the device is OFF. | Float | #N/A | #N/A | OPS, LVM |  |  | FALSE | -100 | 200 | -100 | 200 | PERMCTRLLEV2 | Yes | Yes | Yes | Yes
1398 | Shunt Impedance | PermitAreaId | PERMITAREAID_SHIMP | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1399 | Shunt Impedance | PermSchedule | PERMSCHED_SHIMP | Internals | For time or temperature permissive control, the associated on/off schedule name (in the global resources data). | String | #N/A | #N/A | DPF | “” | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPPERMSCHEDULE | Yes | Yes | Yes | Yes
1400 | Shunt Impedance | Phase | PHASE_SHIMP | Internals | Shunt impedance phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, or ABC. | TRUE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
1401 | Shunt Impedance | Phasesense | PHASESENSE_SHIMP | Internals | The phases that are measured for the local controller. | String | #N/A | #N/A | DPF, LVM |  | except for capacitors with Local control scheme. | FALSE | #N/A | #N/A | #N/A | #N/A | PHSENSED | Yes | Yes | Yes | Yes
1402 | Shunt Impedance | Qtotal | QTOTAL_SHIMP | Internals | Total kVAR size (for three-phase units, enter 3-phase kVAR value). | Float | kVAR | kVAR | DPF, LMV |  |  | TRUE | -90000 | 90000 | -90000 | 90000 |  | Yes | Yes | Yes | Yes
1403 | Shunt Impedance | RegBranch | REGBRANCH_SHIMP | Internals | For VAR, Amp, or power factor locally controlled shunt impedances, the ID of the regulation branch. | String | #N/A | #N/A | OPD, DPF, LVM |  | See Description column. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPREGBR | Yes | Yes | Yes | Yes
1404 | Shunt Impedance | RegBrDirect | REGBRANCHDIRECT_SHIMP | Internals | For VAR, Amp, or power factor locally controlled shunt impedances, the flow direction (enumeration). The field has the following values: 1 = out of device, 2 = into device. | Integer | enumeration | enumeration | OPS, DPF, LVM |  | See Description column. | FALSE | 1 | 2 | 1 | 2 | REGBRDIR | Yes | Yes | Yes | Yes
1405 | Shunt Impedance | RegBrEnd | REGBRANCHEND_SHIMP | Internals | For VAR, Amp, or power factor locally controlled shunt impedances, the end of the branch that is regulated (enumeration). The field has the following values: 0 = from side, 1 = to side, and 2 = tertiary (only if the branch is a three-winding transformer). | Integer | enumeration | enumeration | OPS, DPF, LVM |  | See Description column. | FALSE | 0 | 2 | 0 | 2 | REGEND | Yes | Yes | Yes | Yes
1406 | Shunt Impedance | RegBrType | REGBRANCHTYPE_SHIMP | Internals | For VAR, Amp, or power factor locally controlled shunt impedances, the type of regulation branch (Line, Transformer, Switch, Breaker, Recloser, Fuse, Sectionalizer). | String | #N/A | #N/A | OPS, DPF, LVM |  | See Description column. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPREGBRTYPE | Yes | Yes | Yes | Yes
1407 | Shunt Impedance | Regnode | REGNODE_SHIMP | Internals | Voltage regulation node ID. | String | #N/A | #N/A | DPF, LVM |  | A node ID must be given if a local voltage controller exists. | TRUE | #N/A | #N/A | #N/A | #N/A | SHIMPREGNODE | Yes | Yes | Yes | Yes
1408 | Shunt Impedance | RegTransformer | REGTF_SHIMP | Internals | For capacitors that sense the unregulated node voltage, this field is the associated transformer ID. Otherwise, this field can be left blank. | String | #N/A | #N/A | OPS, DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | REGTF | Yes | Yes | Yes | Yes
1409 | Shunt Impedance | RegUseUnRegulatedNode | REGUSEUNREGULATEDNODE_SHIMP | Internals | Flag indicating the capacitor senses the unregulated node voltage (True = use unregulated voltage). This voltage is effectively located at the transformer secondary terminal which is not modeled, typically upstream of the Load Tap Changer and the transformer secondary node (ToNode). | Boolean | #N/A | #N/A | OPS, DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | REGUSEUNREGULATEDNODE | Yes | Yes | Yes | Yes
1410 | Shunt Impedance | RGround | RGROUND_SHIMP | Internals | Equipment grounding resistance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | FALSE | 0 | 100 | 0 | 100 | RGROUND | Yes | Yes | Yes | Yes
1411 | Shunt Impedance | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1412 | Shunt Impedance | ServiceCenter | SERVCNTR_SHIMP | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1413 | Shunt Impedance | ShuntModel | SWMOD_SHIMP | Internals | Associated shunt impedance model name. | String | #N/A | #N/A | DPF |  | The shunt impedance model name must match a shunt impedance model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL.NAME | Yes | Yes | Yes | Yes
1414 | Shunt Impedance | State | STATE_SHIMP | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1415 | Shunt Impedance | StepSize | STEPSIZE_SHIMP | Internals | Step size (kVAR). If the device is either all on or all off, then this field has the same value as QTOTAL_SHIMP. | Float | kVAR | kVAR | DPF, LVM |  |  | TRUE | 1 | Qtotal | 1 | Qtotal | STEPSIZE | Yes | Yes | Yes | Yes
1416 | Shunt Impedance | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS, NTP |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
1417 | Shunt Impedance | SymbolPlacement:GeometryLevel | GEOMLEVEL_SHIMP | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1418 | Shunt Impedance | SymbolPlacement:GeometryType | GEOMTYPE_SHIMP | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1419 | Shunt Impedance | SymbolPlacement:Rotation | ROTATION_SHIMP | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1420 | Shunt Impedance | SymbolPlacement:Size | SIZE_SHIMP | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1421 | Shunt Impedance | SymbolPlacement:X | WCX_SHIMP | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1422 | Shunt Impedance | SymbolPlacement:X2 | WCX2_SHIMP | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1423 | Shunt Impedance | SymbolPlacement:Y | WCY_SHIMP | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1424 | Shunt Impedance | SymbolPlacement:Y2 | WCY2_SHIMP | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1425 | Shunt Impedance | Tdelay | TDELAY_SHIMP | Internals | Controller time delay setting (seconds). | Float | seconds | seconds | DPF, LVM | User-configurable through Defaults File |  | FALSE | 0 | 600 | 0 | 600 | TMDELAY | Yes | Yes | Yes | Yes
1426 | Shunt Impedance | Telemetered | TELEMETERED_SHIMP | Internals | If not defined, the default value is false, meaning the device is not telemetered in SCADA. This information currently is not used by any DMS application. It is provided to be used by any other application that might uses the source data. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1427 | Shunt Impedance | ThirdPartyOwned | THIRDPARTYOWNED_SHIMP | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1428 | Shunt Impedance | TimeSchedule | TIMESCHED_SHIMP | Internals | For time controlled banks, the associated on/off schedule name (in the global resources data). | String | #N/A | #N/A | DPF, LVM | “” | The schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPREGSCHEDULE | Yes | Yes | Yes | Yes
1429 | Shunt Impedance | VARSupport | VARSUPPORT_SHIMP | Internals | For Heuristic LVM, this flag Indicates if the capacitor is used in problem formulations that require VAR support (maintain power factor at a location in the network). | Boolean | #N/A | #N/A | DPF, LVM | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | VARSUPPORT | Yes | Yes | Yes | Yes
1430 | Shunt Impedance | Volt_Units | #N/A | Internals | Enumeration indicating voltage is measured line to line or line to neutral. The enumeration has the following values: 0 - Line to Line, 1 - Line to Ground | Integer | enumeration | enumeration | OPS |  |  | FALSE | 0 | 1 | 0 | 1 | SHIMPVOLTREGTYPE | Yes | Yes | Yes | Yes
1431 | Shunt Impedance | Vreglineline | VREGLINELINE_SHIMP | Internals | Flag that indicates whether the voltage for the regulated (sensed) phases is measured line to line or line to ground (True = line to line). | Boolean | #N/A | #N/A | OPS, LVM |  | Required for locally controlled voltage (Type 6) capacitors. | FALSE | #N/A | #N/A | #N/A | #N/A | VREGLINE | Yes | Yes | Yes | Yes
1432 | Shunt Impedance | Wyeconnected | WYECONN_SHIMP | Internals | Flag indicating shunt impedance is wye connected. A wye connected shunt impedance is a connection from phase to neutral. | String | #N/A | #N/A | DPF | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | WYE | Yes | Yes | Yes | Yes
1433 | Shunt Impedance | XGround | XGROUND_SHIMP | Internals | Equipment grounding reactance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File |  | FALSE | 0 | 100 | 0 | 100 | XGROUND | Yes | Yes | Yes | Yes
1434 | Shunt Impedance | #N/A | NUMGEOM_SHIMP | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1435 | Shunt Impedance | #N/A | NUMLABELGEOM_SHIMP | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1436 | Splice Box | Address | ADDRESS_SPLBOX | Internals | Non-electrical device address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
1437 | Splice Box | CompanyName | COMPANYNAME_SPLBOX | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1438 | Splice Box | County | COUNTY_SPLBOX | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1439 | Splice Box | CustomField:IsString | CUSTOMFIELDISSTRING_SPLBOX |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1440 | Splice Box | CustomField:Name | CUSTOMFIELDNAME_SPLBOX |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1441 | Splice Box | CustomField:Value | CUSTOMFIELDVALUE_SPLBOX |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1442 | Splice Box | Id | ID_SPLBOX | Internals | Splice box unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1443 | Splice Box | LabelPlacement:CharacterRotation | LABELCHRROTATION_SPLBOX | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1444 | Splice Box | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SPLBOX | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1445 | Splice Box | LabelPlacement:FontSize | LABELSIZE_SPLBOX | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1446 | Splice Box | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SPLBOX | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1447 | Splice Box | LabelPlacement:GeometryType | LABELGEOMTYPE_SPLBOX | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1448 | Splice Box | LabelPlacement:Rotation | LABELROT_SPLBOX | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1449 | Splice Box | LabelPlacement:Text | LABELTEXT_SPLBOX | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1450 | Splice Box | LabelPlacement:X | LABELX_SPLBOX | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1451 | Splice Box | LabelPlacement:Y | LABELY_SPLBOX | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1452 | Splice Box | LocationDescription | LOCATIONDESCRIPTION_SPLBOX | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1453 | Splice Box | Municipality | MUNICIPALITY_SPLBOX | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1454 | Splice Box | Name | NAME_SPLBOX | Internals | Splice box display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1455 | Splice Box | Objects:ContainerObject:ID | OBJECTn_SPLBOX | Internals | Collection of object IDs in the splice box. | String | #N/A | #N/A | OPS |  | Each object must be found in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1456 | Splice Box | Objects:ContainerObject:Ivalue | #N/A | Internals | Collection of object functions (enumeration) in the splice box. | Integer | enumeration | enumeration | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1457 | Splice Box | Objects:ContainerObject:Type | OBJECTTYPEn_SPLBOX | Internals | The type of objects in the splice box (such as SWITCH, FUSE, BREAKER, or others). | String | #N/A | #N/A | OPS |  | The object type must be defined in the file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1458 | Splice Box | PermitAreaId | PERMITAREAID_SPLBOX | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1459 | Splice Box | Refdwg | REFDWG_SPLBOX | Internals | Associated reference drawing. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | REFDRAW | Yes | Yes | Yes | Yes
1460 | Splice Box | State | STATE_SPLBOX | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1461 | Splice Box | SymbolPlacement:GeometryLevel | GEOMLEVEL_SPLBOX | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1462 | Splice Box | SymbolPlacement:GeometryType | GEOMTYPE_SPLBOX | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1463 | Splice Box | SymbolPlacement:Vertex:X | WCXn_SPLBOX | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1464 | Splice Box | SymbolPlacement:Vertex:X2 | WCX2n_SPLBOX | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1465 | Splice Box | SymbolPlacement:Vertex:Y | WCYn_SPLBOX | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1466 | Splice Box | SymbolPlacement:Vertex:Y2 | WCY2n_SPLBOX | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1467 | Splice Box | ThirdPartyOwned | THIRDPARTYOWNED_SPLBOX | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1468 | Splice Box | Types | TYPE_SPLBOX | Internals | Splice box type (enumeration to be determined). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENUMTYPE | Yes | Yes | Yes | Yes
1469 | Splice Box | #N/A | NUMOBJECT_SPLBOX | Externals | The number of objects in the splice box. | Integer | count | count | OPS |  |  | FALSE | 1 | 100 | 1 | 100 | NUMOBJ | Yes | Yes | Yes | Yes
1470 | Splice Box | #N/A | NUMGEOM_SPLBOX | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1471 | Splice Box | #N/A | NUMVERT_SPLBOX | Externals | Number of vertices. At least one vertex must be specified. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
1472 | Splice Box | #N/A | NUMLABELGEOM_SPLBOX | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1473 | Static VAR Compensator | Address | #N/A | Internals | SVC address. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
1474 | Static VAR Compensator | Contmode | #N/A | Internals | Control mode (1 = VAR or 2 = Voltage). | Integer | enumeration | enumeration | DPF |  | 1: VAR 2: Voltage | FALSE |  |  |  |  | CTRLMODE | Yes | Yes | Yes | Yes
1475 | Static VAR Compensator | CustomField:IsString |  |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1476 | Static VAR Compensator | CustomField:Name |  |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1477 | Static VAR Compensator | CustomField:Value |  |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1478 | Static VAR Compensator | Future | #N/A | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1479 | Static VAR Compensator | Id | #N/A | Internals | Static VAR compensator unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1480 | Static VAR Compensator | LabelPlacement:FontSize | #N/A | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1481 | Static VAR Compensator | LabelPlacement:GeometryLevel | #N/A | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1482 | Static VAR Compensator | LabelPlacement:GeometryType | #N/A | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1483 | Static VAR Compensator | LabelPlacement:Rotation | #N/A | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1484 | Static VAR Compensator | LabelPlacement:Text | #N/A | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1485 | Static VAR Compensator | LabelPlacement:X | #N/A | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1486 | Static VAR Compensator | LabelPlacement:Y | #N/A | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1487 | Static VAR Compensator | Name | #N/A | Internals | Static VAR compensator display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1488 | Static VAR Compensator | Node | #N/A | Internals | Associated node ID | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NODENUM | Yes | Yes | Yes | Yes
1489 | Static VAR Compensator | PermitAreaId | PERMITAREAID_SV | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PAREANME | Yes | Yes | Yes | Yes
1490 | Static VAR Compensator | Phase | #N/A | Internals | SVC phase connections. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
1491 | Static VAR Compensator | Regnode | #N/A | Internals | Regulation node ID. | String | #N/A | #N/A | DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | REGNODE | Yes | Yes | Yes | Yes
1492 | Static VAR Compensator | RegSchedule | #N/A | Internals | Associated regulation schedule name. | String | #N/A | #N/A | DPF |  | The regulation schedule name must match a schedule given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | REGSCHD | Yes | Yes | Yes | Yes
1493 | Static VAR Compensator | ServiceCenter | #N/A | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1494 | Static VAR Compensator | SVCModel | #N/A | Internals | SVC model name. | String | #N/A | #N/A | OPS |  | The SVC model name must match an SVC model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | MODEL.NAME | Yes | Yes | Yes | Yes
1495 | Static VAR Compensator | SymbolPlacement:GeometryLevel | #N/A | Internals | Geometry Level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1496 | Static VAR Compensator | SymbolPlacement:GeometryType | #N/A | Internals | Geometry Type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1497 | Static VAR Compensator | SymbolPlacement:Rotation | #N/A | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1498 | Static VAR Compensator | SymbolPlacement:Size | #N/A | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1499 | Static VAR Compensator | SymbolPlacement:X | #N/A | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1500 | Static VAR Compensator | SymbolPlacement:X2 | #N/A | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | No | No
1501 | Static VAR Compensator | SymbolPlacement:Y | #N/A | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1502 | Static VAR Compensator | SymbolPlacement:Y2 | #N/A | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | No | No
1503 | Static VAR Compensator | #N/A | #N/A | Externals | Number of geometries. | Integer | count | count | OPS |  |  | FALSE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1504 | Static VAR Compensator | #N/A | #N/A | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1505 | Substation | Address | ADDRESS_SUB | Internals | Substation address. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
1506 | Substation | AltName | ALTNAME_SUB | Internals | Substation alternate name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ALTNAME | Yes | Yes | Yes | Yes
1507 | Substation | AreaName | AREA_SUB | Internals | Associated operational area name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | AREANAME | Yes | Yes | Yes | Yes
1508 | Substation | CompanyName | COMPANYNAME_SUB | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1509 | Substation | County | COUNTY_SUB | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1510 | Substation | CustomField:IsString | CUSTOMFIELDISSTRING_SUB |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1511 | Substation | CustomField:Name | CUSTOMFIELDNAME_SUB |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1512 | Substation | CustomField:Value | CUSTOMFIELDVALUE_SUB |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1513 | Substation | EMSName | #N/A | Internals | EMS Substation Name. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | EMSNAME | Yes | Yes | Yes | Yes
1514 | Substation | Id | ID_SUB | Internals | Substation unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1515 | Substation | Impedance_R0 | #N/A | Internals | Substation equivalent source zero sequence resistance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCZOSSQR | Yes | Yes | Yes | Yes
1516 | Substation | Impedance_R1 | #N/A | Internals | Substation equivalent source positive sequence resistance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCPOSSQR | Yes | Yes | Yes | Yes
1517 | Substation | Impedance_R2 | #N/A | Internals | Substation equivalent source negative sequence resistance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCNEGSQR | Yes | Yes | Yes | Yes
1518 | Substation | Impedance_X0 | #N/A | Internals | Substation equivalent source zero sequence reactance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCZOSSQX | Yes | Yes | Yes | Yes
1519 | Substation | Impedance_X1 | #N/A | Internals | Substation equivalent source positive sequence reactance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCPOSSQX | Yes | Yes | Yes | Yes
1520 | Substation | Impedance_X2 | #N/A | Internals | Substation equivalent source negative sequence reactance used in fault analysis. | Float | ohms | ohms | DPF |  |  | FALSE | 0 | 300 | 0 | 100 | SCNEGSQX | Yes | Yes | Yes | Yes
1521 | Substation | IsMobileSub |  | Internals | Flag indicating the substation is a mobile substation (True = mobile). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISMBLSUB | Yes | Yes | Yes | Yes
1522 | Substation | IsSubFed |  | Internals | Flag indicating that the substation is fed from another distribution substation and does not have a reference bus interface (True = subfed). This flag MUST be set for a station which is sub-fed. Not setting this flag for a sub-fed station will result in slower NTP processing. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISSUBFED | Yes | Yes | Yes | Yes
1523 | Substation | LabelPlacement:CharacterRotation | LABELCHRROTATION_SUB | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1524 | Substation | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SUB | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1525 | Substation | LabelPlacement:FontSize | LABELSIZE_SUB | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1526 | Substation | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SUB | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1527 | Substation | LabelPlacement:GeometryType | LABELGEOMTYPE_SUB | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1528 | Substation | LabelPlacement:Rotation | LABELROT_SUB | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1529 | Substation | LabelPlacement:Text | LABELTEXT_SUB | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1530 | Substation | LabelPlacement:X | LABELX_SUB | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1531 | Substation | LabelPlacement:Y | LABELY_SUB | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1532 | Substation | LocationDescription | LOCATIONDESCRIPTION_SUB | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1533 | Substation | Municipality | MUNICIPALITY_SUB | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1534 | Substation | Name | NAME_SUB | Internals | Substation display name. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1535 | Substation | PermitAreaId | PERMITAREAID_SUB | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PAREANME | Yes | Yes | Yes | Yes
1536 | Substation | ServiceCenter | SERVCNTR_SUB | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
1537 | Substation | State | STATE_SUB | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1538 | Substation | strInternalName | #N/A | Internals | Substation internal name. If modeler does not fill in this field, Substation Editor (SSE) will use the main view's display name to fill it during the export of the internal file. This field will be used as the Geometry name and the EMS name (SCADA name) for the substation. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1539 | Substation | SymbolPlacement:GeometryLevel | GEOMLEVEL_SUB | Internals | Geometry level. Note there is an option to display a bitmap instead of the default circle configured in VCE. Other shapes are not supported. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1540 | Substation | SymbolPlacement:GeometryType | GEOMTYPE_SUB | Internals | Geometry type. Note there is an option to display a bitmap instead of the default circle configured in VCE. Other shapes are not supported. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1541 | Substation | SymbolPlacement:X | WCXn_SUB | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1542 | Substation | SymbolPlacement:X2 | WCX2n_SUB | Internals | Secondary X coordinate (has more precision). | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1543 | Substation | SymbolPlacement:Y | WCYn_SUB | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1544 | Substation | SymbolPlacement:Y2 | WCY2n_SUB | Internals | Secondary Y coordinate (has more precision). | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1545 | Substation | ThirdPartyOwned | THIRDPARTYOWNED_SUB | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1546 | Substation | VVCStatGroup | VVCSTATGROUP_SUB | Internals | Associated Voltage/VAR control substation group (in the global resources file). If this field is left blank, a default LVM objective function schedule is assigned to the station. | String | #N/A | #N/A | DPF |  | The LVM station group must match a LVM station group given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | VVCSTATGROUP | Yes | Yes | Yes | Yes
1547 | Substation | #N/A | NUMGEOM_SUB | Externals | Number of geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1548 | Substation | #N/A | NUMVERT_SUB | Externals | Number of vertices. Note there is an option to display a bitmap instead of the default circle configured in VCE. Other shapes are not supported. Other shapes are not supported. At least one vertex must be specified. | Integer | count | count | OPS | 1 | If the substation is to be displayed as a rectangle, four vertices are required. | TRUE | 0 | 100 | 0 | 100 | NUMVERT | Yes | Yes | Yes | Yes
1549 | Substation | #N/A | NUMLABELGEOM_SUB | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1550 | Switch | Address | ADDRESS_SWITCH | Internals | Switch address | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS | Yes | Yes | Yes | Yes
1551 | Switch | CompanyName | COMPANYNAME_SWITCH | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1552 | Switch | CompositeSwitchLinkID | #N/A | Internals | Linked composite switch ID. | String | #N/A | #N/A | OPS |  | This should be filled for devices that are part of a Station Internal Composite Switch. The format is ID=LinkNumber where the ID is the ID given in the CompositeSwitchLinkMasterID field. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1553 | Switch | ComputeFlows | COMPUTEFLOWS_SWITCH | Internals | Compute flows flag (False = collapse connection nodes internally). If set to False, the flow through the device is not calculated by the Distribution Power Flow (DPF). | Boolean | #N/A | #N/A | OPS, DPF |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CALCULATEFLOW | Yes | Yes | Yes | Yes
1554 | Switch | County | COUNTY_SWITCH | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1555 | Switch | CustomField:IsString | CUSTOMFIELDISSTRING_SWITCH |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1556 | Switch | CustomField:Name | CUSTOMFIELDNAME_SWITCH |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1557 | Switch | CustomField:Value | CUSTOMFIELDVALUE_SWITCH |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1558 | Switch | DSOOverride | DSOOVER_SWITCH | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | #N/A | #N/A | OPS |  | 0: NotSet 1: AllowDSO 2: DisableDSO | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
1559 | Switch | ExternalInterfaceExternallyOwned | EXTERNALLYOWNED_SWITCH | Internals | Flag indicating if the switch's status is provided by the external system | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALLYOWNED | Yes | Yes | Yes | Yes
1560 | Switch | ExternalInterfaceMember | EXTERNALINTERFACE_SWITCH | Internals | Flag indicating if the switch is membership in external interface | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTERNALINTERFACE | Yes | Yes | Yes | Yes
1561 | Switch | Feeder1 |  | Externals | ID of the nominal feeder of the switch. (Used for informational purpose at Converter level. Does not get added into the DNOM model.) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1562 | Switch | Feeder2 |  | Externals | ID of the second feeder that the switch is associated with. This field is applicable to switches that connect two feeders. (Used for informational purpose at Converter level. Does not get added into the DNOM model.) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1563 | Switch | FeedMainBound | FEEDMAINBOUND_SWITCH | Externals | Flag indicating that the switching device is a boundary between the feeder main and lateral. This flag takes priority over the normal rules for assigning the feeder main flag. | Boolean | #N/A | #N/A | OPS, NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDMAINBOUND | Yes | Yes | Yes | Yes
1564 | Switch | FromNode | FRNODEID_SWITCH | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
1565 | Switch | Future | FUTURE_SWITCH | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, ABCN, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | SWTFUTURE | Yes | Yes | Yes | Yes
1566 | Switch | Id | ID_SWITCH | Internals | Switch unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1567 | Switch | LabelPlacement:CharacterRotation | LABELCHRROTATION_SWITCH | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1568 | Switch | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SWITCH | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1569 | Switch | LabelPlacement:FontSize | LABELSIZE_SWITCH | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1570 | Switch | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SWITCH | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1571 | Switch | LabelPlacement:GeometryType | LABELGEOMTYPE_SWITCH | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1572 | Switch | LabelPlacement:Rotation | LABELROT_SWITCH | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1573 | Switch | LabelPlacement:Text | LABELTEXT_SWITCH | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1574 | Switch | LabelPlacement:X | LABELX_SWITCH | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1575 | Switch | LabelPlacement:Y | LABELY_SWITCH | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1576 | Switch | LocationDescription | LOCATIONDESCRIPTION_SWITCH | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1577 | Switch | Municipality | MUNICIPALITY_SWITCH | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1578 | Switch | Name | NAME_SWITCH | Internals | Switch display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1579 | Switch | NOMINAL_FEEDER_ID_SWITCH | NOMINAL_FEEDER_ID_SWITCH | Internals | Nominal feeder ID for the switch. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for switches marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1580 | Switch | NominalFeederBoundary |  | Internals | Flag indicating that a switching device is a boundary for a nominal feeder. This field is applicable if the switch is normally closed. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1581 | Switch | NormallyDeenergized | NORMDEENERGIZED_SWITCH | Internals | Flag indicating that the recloser is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
1582 | Switch | NormallyLooped | NORMLOOPED_SWITCH | Internals | Flag indicating that the recloser is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
1583 | Switch | NormallyNetworkLooped | NORMNETWORKLOOPED_SWITCH | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1584 | Switch | NormallyOpen | NOPEN_SWITCH | Internals | Flag indicating the switch is normally open (True = open). This field is set if all phases are either normally open or normally closed. The field is optional when NORM_OPEN_PHASES is filled in (Defaults to False = Closed). | Boolean | #N/A | #N/A | OPS, NTP |  | If both NOPEN and NORM_OPEN_PHASES fields are left unfilled, the switching device will be treated as Closed. | FALSE | #N/A | #N/A | #N/A | #N/A | NOPEN | Yes | Yes | Yes | Yes
1585 | Switch | NormallyParallelLooped | NORMPARALLELLOOPED_SWITCH | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1586 | Switch | NormOpenPhases | NORM_OPEN_PHASES | Internals | Normally open phases. This phase is set for phase independently switched devices that may have a combination of normally open and normally closed phases. This field overrides the NOPEN_SWITCH field. | String | #N/A | #N/A | OPS, NTP |  | A, B, C, AB, BC, AC, ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | NORMOPENPHASES | Yes | Yes | Yes | Yes
1587 | Switch | PermitAreaId | PERMITAREAID_SWITCH | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1588 | Switch | Phase | PHASE_SWICTH | Internals | Switch phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AB, BC, CA, AN, BN, CN, ABN, BCN, CAN, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A | DEVICEPHASE | Yes | Yes | Yes | Yes
1589 | Switch | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1590 | Switch | SecondId | TROUBLECALLID_SWITCH | Internals | Alternate switch ID. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
1591 | Switch | ServiceCenter | SERVCNTR_SWITCH | Internals | Associated service center. | String | #N/A | #N/A | OPS, OMS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR | Yes | Yes | Yes | Yes
1592 | Switch | State | STATE_SWITCH | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1593 | Switch | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
1594 | Switch | SuppressFeeder |  | Internals | Flag indicating that the feeder name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1595 | Switch | SwitchModel | SWMOD_SWITCH | Internals | Associated switch model name. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL | Yes | Yes | Yes | Yes
1596 | Switch | SwitchModelPhA | SWMODA_SWITCH | Internals | Associated switch model name for phase A. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHA | Yes | Yes | Yes | Yes
1597 | Switch | SwitchModelPhB | SWMODB_SWITCH | Internals | Associated switch model name for phase B. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHB | Yes | Yes | Yes | Yes
1598 | Switch | SwitchModelPhC | SWMODC_SWITCH | Internals | Associated switch model name for phase C. | String | #N/A | #N/A | DPF |  | The switch model name must match a switch mode given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWITCHMODPHC | Yes | Yes | Yes | Yes
1599 | Switch | SymbolPlacement:GeometryLevel | GEOMLEVEL_SWITCH | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1600 | Switch | SymbolPlacement:GeometryType | GEOMTYPE_SWITCH | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SWPLACE.GEOMETRY | Yes | Yes | Yes | Yes
1601 | Switch | SymbolPlacement:Rotation | ROTATION_SWITCH | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | SWPLACE.ROTATION | Yes | Yes | Yes | Yes
1602 | Switch | SymbolPlacement:Size | SIZE_SWITCH | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SWPLACE.SIZE | Yes | Yes | Yes | Yes
1603 | Switch | SymbolPlacement:X | WCX_SWITCH | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X | Yes | Yes | Yes | Yes
1604 | Switch | SymbolPlacement:X2 | WCX2_SWITCH | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.X2 | Yes | No | Yes | No
1605 | Switch | SymbolPlacement:Y | WCY_SWITCH | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y | Yes | Yes | Yes | Yes
1606 | Switch | SymbolPlacement:Y2 | WCY2_SWITCH | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | SWPLACE.Y2 | Yes | No | Yes | No
1607 | Switch | ThirdPartyOwned | THIRDPARTYOWNED_SWITCH | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1608 | Switch | ToNode | TONODEID_SWITCH | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
1609 | Switch | ToStation | TOSUB_SWITCH | Internals | Associated external substation name. This field should only be set if the switch connects two substations together. | String | #N/A | #N/A | OPS, NTP |  | The station name is checked against the stations list read from the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | BOUNDSWSUB1 | Yes | Yes | Yes | Yes
1610 | Switch | #N/A | NUMGEOM_SWITCH | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1611 | Switch | #N/A | NUMLABELGEOM_SWITCH | Externals | Number of label geometries. | Integer | #N/A | #N/A | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1612 | Switch | BusTieSwitch | BUSTIESWITCH_SWITCH | Internals | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | No | No | No | No
1613 | Switch Cabinet | Address | ADDRESS_SWCAB | Internals | Non-electrical device address. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
1614 | Switch Cabinet | AlternateName | ALTNAME_SWCAB | Internals | Alternate name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ALTERNATENAME | Yes | Yes | Yes | Yes
1615 | Switch Cabinet | CompanyName | COMPANYNAME_SWCAB | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1616 | Switch Cabinet | County | COUNTY_SWCAB | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1617 | Switch Cabinet | CustomField:IsString | CUSTOMFIELDISSTRING_SWCAB |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1618 | Switch Cabinet | CustomField:Name | CUSTOMFIELDNAME_SWCAB |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1619 | Switch Cabinet | CustomField:Value | CUSTOMFIELDVALUE_SWCAB |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1620 | Switch Cabinet | Id | ID_SWCAB | Internals | Switch cabinet unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1621 | Switch Cabinet | LabelPlacement:CharacterRotation | LABELCHRROTATION_SWCAB | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1622 | Switch Cabinet | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_SWCAB | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1623 | Switch Cabinet | LabelPlacement:FontSize | LABELSIZE_SWCAB | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1624 | Switch Cabinet | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_SWCAB | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1625 | Switch Cabinet | LabelPlacement:GeometryType | LABELGEOMTYPE_SWCAB | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1626 | Switch Cabinet | LabelPlacement:Rotation | LABELROT_SWCAB | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1627 | Switch Cabinet | LabelPlacement:Text | LABELTEXT_SWCAB | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1628 | Switch Cabinet | LabelPlacement:X | LABELX_SWCAB | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1629 | Switch Cabinet | LabelPlacement:Y | LABELY_SWCAB | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1630 | Switch Cabinet | LocationDescription | LOCATIONDESCRIPTION_SWCAB | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1631 | Switch Cabinet | Municipality | MUNICIPALITY_SWCAB | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1632 | Switch Cabinet | Name | NAME_SWCAB | Internals | Switch cabinet display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1633 | Switch Cabinet | NOMINAL_FEEDER_ID_SWCAB | NOMINAL_FEEDER_ID_SWCAB | Internals | Nominal feeder ID for the switch cabinet. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for switch cabinets marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1634 | Switch Cabinet | Objects:ID | OBJECTn_SWCAB | Internals | Collection of object IDs in the cabinet. | String | #N/A | #N/A | OPS |  | Each object must be found in the file. Required if objects are defined. | FALSE | #N/A | #N/A | #N/A | #N/A | SWCABOBJ.ID | Yes | Yes | Yes | Yes
1635 | Switch Cabinet | Objects:Ivalue | #N/A | Internals | Collection of object functions (enumeration) in the cabinet | Integer | enumeration | enumeration | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1636 | Switch Cabinet | Objects:Type | OBJECTTYPEn_SWCAB | Internals | The type of objects in the cabinet (such as SWITCH, FUSE, BREAKER, or others). | String | #N/A | #N/A | OPS |  | The object type must be defined in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | SWCABOBJ.TYPE | Yes | Yes | Yes | Yes
1637 | Switch Cabinet | PermitAreaId | PERMITAREAID_SWCAB | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1638 | Switch Cabinet | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1639 | Switch Cabinet | State | STATE_SWCAB | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1640 | Switch Cabinet | SymbolPlacement:GeometryLevel | GEOMLEVEL_SWCAB | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1641 | Switch Cabinet | SymbolPlacement:GeometryType | GEOMTYPE_SWCAB | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PLACEMNT.GEOMETRY | Yes | Yes | Yes | Yes
1642 | Switch Cabinet | SymbolPlacement:IsPoint | ISPOINT_SWCAB | Internals | Flag indicating it is a point placement. | Boolean | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1643 | Switch Cabinet | SymbolPlacement:Rotation | ROTATION_SWCAB | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.ROTATION | Yes | Yes | Yes | Yes
1644 | Switch Cabinet | SymbolPlacement:Size | SIZE_SWCAB | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.SIZE | Yes | Yes | Yes | Yes
1645 | Switch Cabinet | SymbolPlacement:Vertex:X | WCXn_SWCAB | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX | Yes | Yes | Yes | Yes
1646 | Switch Cabinet | SymbolPlacement:Vertex:X2 | WCX2n_SWCAB | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX2 | Yes | No | Yes | No
1647 | Switch Cabinet | SymbolPlacement:Vertex:Y | WCYn_SWCAB | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY | Yes | Yes | Yes | Yes
1648 | Switch Cabinet | SymbolPlacement:Vertex:Y2 | WCY2n_SWCAB | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY2 | Yes | No | Yes | No
1649 | Switch Cabinet | SymbolPlacement:X | WCX_SWCAB | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X | Yes | Yes | Yes | Yes
1650 | Switch Cabinet | SymbolPlacement:X2 | WCX2_SWCAB | Internals | X coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X2 | Yes | No | Yes | No
1651 | Switch Cabinet | SymbolPlacement:Y | WCY_SWCAB | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y | Yes | Yes | Yes | Yes
1652 | Switch Cabinet | SymbolPlacement:Y2 | WCY2_SWCAB | Internals | Y coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y2 | Yes | No | Yes | No
1653 | Switch Cabinet | ThirdPartyOwned | THIRDPARTYOWNED_SWCAB | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1654 | Switch Cabinet | Type | TYPE_SWCAB | Internals | User defined switch cabinet type enumeration defined in the global reosurces file. | String | #N/A | #N/A | OPS |  | Please refer to global.csv file | FALSE | 0 | 27 | 0 | 27 | SWCABTYPE | Yes | Yes | Yes | Yes
1655 | Switch Cabinet | #N/A | NUMOBJECT_SWCAB | Externals | The number of objects in the cabinet. | Integer | count | count | OPS |  |  | FALSE | 1 | 100 | 1 | 100 | NUMOBJ | Yes | Yes | Yes | Yes
1656 | Switch Cabinet | #N/A | NUMGEOM_SWCAB | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1657 | Switch Cabinet | #N/A | NUMVERT_SWCAB | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | PLACEMNT.NUMVERT | Yes | Yes | Yes | Yes
1658 | Switch Cabinet | #N/A | NUMLABELGEOM_SWCAB | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1659 | Time Overcurrent Relay | AltGrTrip | ALTPHTRIP_OCRELAY | Internals | Relay alternate ground trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 25000 | 0 | 25000 | GRDTRIPALT | Yes | Yes | Yes | Yes
1660 | Time Overcurrent Relay | AltPhTrip | ALTGRTRIP_OCRELAY | Internals | Relay alternate phase trip setting (Amps). | Float | Amps | Amps | DPF |  |  | FALSE | 0 | 25000 | 0 | 25000 | PHTRIPALT | Yes | Yes | Yes | Yes
1661 | Time Overcurrent Relay | CompanyName | COMPANYNAME_OCRELAY | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1662 | Time Overcurrent Relay | County | COUNTY_OCRELAY | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1663 | Time Overcurrent Relay | CtRatio | CTRATIO_OCRELAY | Internals | Primary winding CT ratio. | Float | ratio | ratio | DPF |  | Required if transformer has tap changers on primary. | TRUE | 1 | 15000 | 1 | 15000 | PRTAP.CTRATIO | Yes | Yes | Yes | Yes
1664 | Time Overcurrent Relay | CustomField:IsString | CUSTOMFIELDISSTRING_OCRELAY |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1665 | Time Overcurrent Relay | CustomField:Name | CUSTOMFIELDNAME_OCRELAY |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1666 | Time Overcurrent Relay | CustomField:Value | CUSTOMFIELDVALUE_OCRELAY |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1667 | Time Overcurrent Relay | GrTrip | GRTRIP_OCRELAY | Internals | Relay normal ground trip setting (Amps). | Float | Amps | Amps | DPF | User-configurable through Defaults File |  | TRUE | 0 | 25000 | 0 | 25000 | GRDTRIP | Yes | Yes | Yes | Yes
1668 | Time Overcurrent Relay | Id |  | Internals | ID of the relay. | String | [5 empty] | FALSE: TRUE; No: Yes; No: Yes; No: Yes; No: Yes
1669 | Time Overcurrent Relay | LabelPlacement:FontSize | LABELSIZE_OCRELAY | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1670 | Time Overcurrent Relay | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_OCRELAY | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1671 | Time Overcurrent Relay | LabelPlacement:GeometryType | LABELGEOMTYPE_OCRELAY | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1672 | Time Overcurrent Relay | LabelPlacement:Rotation | LABELROT_OCRELAY | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1673 | Time Overcurrent Relay | LabelPlacement:Text | LABELTEXT_OCRELAY | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1674 | Time Overcurrent Relay | LabelPlacement:X | LABELX_OCRELAY | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1675 | Time Overcurrent Relay | LabelPlacement:Y | LABELY_OCRELAY | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1676 | Time Overcurrent Relay | LocationDescription | LOCATIONDESCRIPTION_OCRELAY | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1677 | Time Overcurrent Relay | Municipality | MUNICIPALITY_OCRELAY | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1678 | Time Overcurrent Relay | Name |  | Internals | Name of the relay. | String | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1679 | Time Overcurrent Relay | PermitAreaId | PERMITAREAID_OCRELAY | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PAREANME | Yes | Yes | Yes | Yes
1680 | Time Overcurrent Relay | PhTrip | PHTRIP_OCRELAY | Internals | Relay normal phase trip setting (Amps). | Float | Amps | Amps | DPF | User-configurable through Defaults File |  | TRUE | 0 | 25000 | 0 | 25000 | PHTRIP | Yes | Yes | Yes | Yes
1681 | Time Overcurrent Relay | ServiceCenter | SERVCNTR_OCRELAY | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1682 | Time Overcurrent Relay | State | STATE_OCRELAY | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1683 | Time Overcurrent Relay | SymbolPlacement:GeometryLevel | GEOMLEVEL_OCRELAY | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1684 | Time Overcurrent Relay | SymbolPlacement:GeometryType | GEOMTYPE_OCRELAY | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1685 | Time Overcurrent Relay | SymbolPlacement:Rotation | ROTATION_OCRELAY | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1686 | Time Overcurrent Relay | SymbolPlacement:Size | SIZE_OCRELAY | Internals | Size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1687 | Time Overcurrent Relay | SymbolPlacement:X | WCX_OCRELAY | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1688 | Time Overcurrent Relay | SymbolPlacement:X2 | WCX2_OCRELAY | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1689 | Time Overcurrent Relay | SymbolPlacement:Y | WCY_OCRELAY | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1690 | Time Overcurrent Relay | SymbolPlacement:Y2 | WCY2_OCRELAY | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1691 | Time Overcurrent Relay | ThirdPartyOwned | THIRDPARTYOWNED_OCRELAY | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1692 | Time Overcurrent Relay | Types | TYPE_OCRELAY | Internals | Overccurent relay type. | String | #N/A | #N/A | DPF |  | 0 - Unknown 1 - Electromechanical 2 - Electronic | FALSE | #N/A | #N/A | #N/A | #N/A | RELAYTYPE | Yes | Yes | Yes | Yes
1693 | Transformer | Address | ADDRESS_TF | Internals | Transformer address. | String | #N/A | #N/A | OPS | “Not Provided” |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTR | Yes | Yes | Yes | Yes
1694 | Transformer | ASCCoilSize | ASCCOILSIZE_TF | Internals | Arc Suppression Coil size (kVA). | Float | kVA | kVA |  |  |  | FALSE | 10 | 100000 | 10 | 100000 | ASCCOILSIZE | Yes | Yes | No | No
1695 | Transformer | CnsType | CNSTTYPE_TF | Internals | Construction type (optional enumerated field). When the TFMOD_TF is not set, then this Construction Type field may be used. The construction type field is used by the Converter for creating the appropriate transformer models according to the base model information. In addition, it is an index into an optionally provided enumeration in the GLOBAL.CSV, which is used for providing display only information. | Integer | enumeration | enumeration | OPS, DPF, LVM, FISR, SCC |  |  | FALSE | 0 | 200 | 0 | 200 |  | Yes | Yes | Yes | Yes
1696 | Transformer | CompanyName | COMPANYNAME_TF | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1697 | Transformer | ConsecOperate | CONSECOPERATE_TF | Internals | Minimum time (in hours) between consecutive tap operations. This is a constraint used in the Load and Volt//VAR Management (LVM) application. | Float | hours | hours | OPS, LVM | 1 |  | No: Yes; No: Yes; No: Yes; No: Yes
1698 | Transformer | CoreLoss | #N/A | Internals | Core loss (MW). | Float | MW | MW | OPS, DPF |  |  | FALSE |  |  |  |  | MAGLOSS | Yes | Yes | Yes | Yes
1699 | Transformer | County | COUNTY_TF | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1700 | Transformer | Critical | CRITICAL_TF | Internals | Flag indicating there is a critical customer load connected to the transformer (True = critical). | Boolean | #N/A | #N/A | OPS, SLS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CRITICAL | Yes | Yes | Yes | Yes
1701 | Transformer | Customer | CUSTOMER_TF | Externals | Number of connected customers (customer count should now be set on the Load object). | Integer | count | count | OPS | 0 | No longer used. | FALSE | 0 | 5000 | 0 | 5000 | NOMCCUST | Yes | Yes | Yes | Yes
1702 | Transformer | DefaultASCRegulationOn | DEFAULTASCREGULATIONON_TF | Internals | Default value of the Arc Suppression Coil Regulation On status | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECDEFASCREGULATIONON | Yes | Yes | No | No
1703 | Transformer | DeltaSecGnd | DELTASECGND_TF | Internals | The phase that is grounded (center tap winding) for a delta connected secondary. Note this field should not be supplied for a transformer with a wye-connected secondary. | String | #N/A | #N/A | OPS, DPF |  | A, B, C. | FALSE | #N/A | #N/A | #N/A | #N/A | DELTASECPHASEGRND | Yes | Yes | Yes | Yes
1704 | Transformer | DisableAllFeederLVM | #N/A | Internals | Flag to indicate if the Load and Volt/VAR Management (LVM) application should be automatically disabled for all connected feeders if the transformer is not controllable (True = disable all feeders). | Boolean | #N/A | #N/A | DPF, LVM | TRUE |  | STATE: DISABLEALLFEEDERLVM; No: Yes; No: Yes; No: Yes; No: Yes
1705 | Transformer | DSOOverride | DSOOVER_TF | Internals | Eligibility override enumeration of the normal rules for the switching reconfiguration applications. | Integer | enumeration | enumeration | OPS, FISR, OMS |  | 0: Not Set 1: Allow 2: Disable | FALSE | 0 | 2 | 0 | 2 | DEVICEDSOOVER | Yes | Yes | Yes | Yes
1706 | Transformer | ExcitePercent | #N/A | Internals | Excitation current (percent). | Float | percent | percent | DPF |  |  | FALSE |  |  |  |  | EXCTEAMP | Yes | Yes | Yes | Yes
1707 | Transformer | ExternalId | EXTERNALID_TF | Internals | External Id of the transformer (optional). This information is stored in the DNOM model for all transformers except Distribution Transformer types (Regulators, Power Transformers and Auto Transformers etc.). It is provided to be used by any other external application that might uses the source data. | String | #N/A | #N/A | OPS |  |  | STATE: EXTERNALID.NOAPPSTR; No: Yes; No: Yes; No: Yes; No: Yes
1708 | Transformer | ExternalId | EXTERNALID_TF | Internals | Second transformer ID. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECONDID.NOAPPSTR | Yes | Yes | Yes | Yes
1709 | Transformer | FromNode | FRNODE_TF | Internals | From node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | FROMNODE | Yes | Yes | Yes | Yes
1710 | Transformer | Future | FUTURE_TF | Internals | Individual phases that are constructed but not energized. | String | #N/A | #N/A | OPS | “” | A, B, C, AB, BC, CA, ABC, or blank. | FALSE | #N/A | #N/A | #N/A | #N/A | FUTUREPHASES | Yes | Yes | Yes | Yes
1711 | Transformer | Ground | GROUND_TF | Internals | Enumerated type field that indicates which windings are grounded (if any). The following enumeration applies: 0 = No windings grounded, 1 = Primary, 2 = Secondary, 3 = Tertiary, 4 = Primary and secondary, 5 = Primary and tertiary, 6 = Secondary and Tertiary, and 7 = Primary, secondary, and tertiary. | Integer | enumeration | enumeration | DPF |  | 0: No grounds 1: Primary is grounded 2: Secondary is grounded 3: Tertiary is grounded 4: Primary and secondary are grounded 5: Primary and tertiary are grounded 6: Secondary and tettiary are grounded 7: Primary, secondar, and tertiary are grounded | FALSE | 0 | 7 | 0 | 7 | DSECGRND | Yes | Yes | Yes | Yes
1712 | Transformer | HasArcSuppressionCoil | HASARCSUPPRESSIONCOIL_TF | Internals | Power transformer has an Arc Suppression Coil connected to it | Boolean | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECHASARCSUPPRESSIONCOIL | Yes | Yes | No | No
1713 | Transformer | Id | ID_TF | Internals | Transformer unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1714 | Transformer | KVA |  | Internals | Apparent power | Float | KVA | KVA |  |  |  | TRUE: TRUE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1715 | Transformer | LabelPlacement:CharacterRotation | LABELCHRROTATION_TF | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1716 | Transformer | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_TF | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1717 | Transformer | LabelPlacement:FontSize | LABELSIZE_TF | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1718 | Transformer | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_TF | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1719 | Transformer | LabelPlacement:GeometryType | LABELGEOMTYPE_TF | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1720 | Transformer | LabelPlacement:Rotation | LABELROT_TF | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1721 | Transformer | LabelPlacement:Text | LABELTEXT_TF | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1722 | Transformer | LabelPlacement:X | LABELX_TF | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1723 | Transformer | LabelPlacement:Y | LABELY_TF | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1724 | Transformer | Limit1Name |  | Internals | Limit 1 name | String | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1725 | Transformer | Limit2Name |  | Internals | Limit 2 name | String | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1726 | Transformer | Limit3Name |  | Internals | Limit 3 name | String | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1727 | Transformer | LocationDescription | LOCATIONDESCRIPTION_TF | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1728 | Transformer | MaxASCGroundX | MAXASCGROUNDX_TF | Internals | Default value of the Arc Suppression Coil maximum ground impedance reactance (ohms). | Float | ohms | ohms |  |  |  | FALSE | 10 | 20000 | 10 | 20000 | MAXASCGROUNDX | Yes | Yes | No | No
1729 | Transformer | MaxOperations | MAXOPERATIONS_TF | Internals | Maximum number of daily operations. This is a constraint used in the Load and Volt//VAR Management (LVM) application. | Integer | #N/A | #N/A | DPF, LVM | 20 |  | FALSE | #N/A | #N/A | 1 | 100 | MAXOPERATIONS | Yes | Yes | Yes | Yes
1730 | Transformer | MaxVoltImbalance | MAXVOLTIMBALANCE_TF | Internals | Maximum voltage imbalance percentage for regulating transformers, typically a group of parallel single-phase regulators that regulate their individual phase voltage. | Float | #N/A | #N/A | DPF, LVM | 3 |  | FALSE | 0.1 | 10 | 0.1 | 10 | LVMMAXPHASEVOLTIMBALANCE | Yes | Yes | Yes | Yes
1731 | Transformer | MinASCGroundX | MINASCGROUNDX_TF | Internals | Default value of the Arc Suppression Coil minimum ground impedance reactance (ohms). | Float | ohms | ohms |  |  |  | FALSE | 10 | 20000 | 10 | 20000 | MINASCGROUNDX | Yes | Yes | No | No
1732 | Transformer | Municipality | MUNICIPALITY_TF | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1733 | Transformer | Name | NAME_TF | Internals | Transformer display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1734 | Transformer | NOMINAL_FEEDER_ID_TF | NOMINAL_FEEDER_ID_TF | Internals | Nominal feeder ID for the transformer. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for transformers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1735 | Transformer | NormallyDeenergized | NORMDEENERGIZED_TF | Internals | Flag indicating that the recloser is normally de-energized (True = de-energized). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYDEENERGIZED | Yes | Yes | Yes | Yes
1736 | Transformer | NormallyLooped | NORMLOOPED_TF | Internals | Flag indicating that the recloser is normally looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALLYLOOPED | Yes | Yes | Yes | Yes
1737 | Transformer | NormallyNetworkLooped | NORMNETWORKLOOPED_TF | Internals | Flag indicating that the device is normally network looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1738 | Transformer | NormallyParallelLooped | NORMPARALLELLOOPED_TF | Internals | Flag indicating that the device is normally parallel looped (True = looped). | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1739 | Transformer | NotLoaded | NOTLOADED_TF | Internals | A flag indicating the transformer has no secondary loads attached (True = no loads are connected). This is applicable for distribution (secondary or MV/LV) transformers. These transformers are skipped by BLA and Converter when allocating loads. | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1740 | Transformer | OperLimitEvent1 |  | Internals | Operation limit event 1 at primary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1741 | Transformer | OperLimitEvent1_Sec |  | Internals | Operation limit event 1 at secondary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1742 | Transformer | OperLimitEvent1_Ter |  | Internals | Operation limit event 1 at tertiary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1743 | Transformer | OperLimitEvent2 |  | Internals | Operation limit event 2 at primary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1744 | Transformer | OperLimitEvent2_Sec |  | Internals | Operation limit event 2 at secondary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1745 | Transformer | OperLimitEvent2_Ter |  | Internals | Operation limit event 2 at tertiary winding? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1746 | Transformer | Overhead | #N/A | Internals | Overhead flag (True = overhead, False=underground). | Boolean | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1747 | Transformer | PermitAreaId | PERMITAREAID_TF | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1748 | Transformer | Phase | PHASE_TF | Internals | Transformer phase connections field. This field is not used for transformer objects (use the PRIMPHASE_TF, SECPHASE_TF, and TERTPHASE_TF fields). | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | SHUNTPHASING | Yes | Yes | Yes | Yes
1749 | Transformer | PrBandwth | PRBANDWTH_TF | Internals | Primary winding tap changer two-sided bandwidth. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.001/0.12 | 0.1/24.0 | 0.001/0.12 | 0.1/24.0 | PRTAP.BANDWITH | Yes | Yes | Yes | Yes
1750 | Transformer | PrControlCapability | PRCONTROLCAPABILITY_TF | Internals | Primary winding tap changer control capability enumeration. This includes the ability to issue raise/lower tap steps and/or change a voltage setpoint. The enumeration includes the following values: 0 = No Control, 1 = Raise/Lower Only, 2 = Voltage Setpoint Only, 3 = Raise/Lower or Voltage Setpoint, and 4 = Voltage Reduction Only. | Integer | enumeration | enumeration | DPF, LVM |  | 0: No Control 1: Raise Lower Only 2: Voltage Setpoint Only 3: Raise Lower or Voltage Setpoint 4: Voltage Reduction Only | FALSE | 0 | 4 | 0 | 4 |  | Yes | Yes | Yes | Yes
1751 | Transformer | PrControllable | PRCONTROLABLE_TF | Internals | Prrimary winding tap changer controllability enumeration. The field has the following values: 0 = Fixed, 1 = Local control only, 2 = Remote control only, 3 = Remote with local control capability. | Integer | enumeration | enumeration | DPF, LVM |  | Required if transformer has tap changers on primary. The field has the following values: 0 = Fixed 1 = Local only 2 = Remote only 3 = Remote with local control | FALSE | 0 | 4 | 0 | 4 | PRTAP.TAPCNTRL | Yes | Yes | Yes | Yes
1752 | Transformer | PrCtRatio | PRCTRATIO_TF | Internals | Primary winding CT ratio. | Float | ratio | ratio | DPF |  | Required if transformer has tap changers on primary. | FALSE | 1 | 15000 | 1 | 15000 | PRTAP.CTRATIO | Yes | Yes | Yes | Yes
1753 | Transformer | PrCtSecamps | PRCTSECAMPS_TF | Internals | Primary winding CT full load secondary rating (Amps). | Float | Amps | Amps | DPF |  | User-configurable through Defaults File | FALSE | 0.1 | 20 | 0.1 | 20 | PRTAP.CTSECAMP | Yes | Yes | Yes | Yes
1754 | Transformer | PrCurrentControlMode | PRCURRENTCONTROLMODE_TF | Internals | The primary winding tap changer active control mode enumeration. This field is used in combination with the PRCONTROLCAPABILITY_TF field to determine the active control mode if the tap changer has multiple control mode capability. The enumeration includes the following values: 0 = None, 1 = Raise/Lower Tap, 2 = Voltage Setpoint, 3 = Voltage Reduction. This field is not applicable if the tap changer only supports a single control mode. | Integer | enumeration | enumeration | DPF, LVM |  | 0: None 1: Raise Lower Tap 2: Voltage Setpoint 3: Voltage Reduction | FALSE | 0 | 3 | 0 | 3 |  | Yes | Yes | Yes | Yes
1755 | Transformer | PrimaryRegNode | #N/A | Internals | Primary regulation node location (Primary, Secondary, or Tertiary connection node). | Integer | enumeration | enumeration | DPF |  | Field is redundant if the Pr/Sc/TeRegNodeId values are provided. | FALSE | 0 | 2 | 0 | 2 |  | Yes | Yes | Yes | Yes
1756 | Transformer | PrimMaxTap | #N/A | Internals | Primary maximum tap step. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if primary tap changer is not available. | FALSE |  |  |  |  | PRIMMAXTAPPOS | Yes | Yes | Yes | Yes
1757 | Transformer | PrimMinTap | #N/A | Internals | Primary minimum tap step. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if primary tap changer is not available. | FALSE |  |  |  |  | PRIMMINTAPPOS | Yes | Yes | Yes | Yes
1758 | Transformer | PrimNomTap | #N/A | Internals | Primary nominal tap step for fixed tap model. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if primary tap changer is not available. | FALSE |  |  |  |  | PRIMNOMTAPPOS | Yes | Yes | Yes | Yes
1759 | Transformer | PrimPhase | PRIMPHASE_TF | Internals | Primary winding transformer phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AN, BN, CN, ABC, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1760 | Transformer | PrimSecR1 | #N/A | Internals | For three-winding transformers, the leakage resistance (%) measured in the primary with the secondary short circuited and the tertiary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1761 | Transformer | PrimSecX1 | #N/A | Internals | For three-winding transformers, the leakage reactance (%) measured in the primary with the secondary short circuited and the tertiary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1762 | Transformer | PrimTapCost | #N/A | Internals | Primary tap movement cost. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Float | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | PRIMTAPCOST | Yes | Yes | Yes | Yes
1763 | Transformer | PrimTapStep | #N/A | Internals | Primary tap step increment(%). This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Float | percent | percent | DPF, LVM |  | Optional if primary tap changer is not available. | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1764 | Transformer | PrimTerR1 | #N/A | Internals | For three-winding transformers, the leakage resistance (%) measured in the primary with the tertiary short circuited and the secondary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1765 | Transformer | PrimTerX1 | #N/A | Internals | For three-winding transformers, the leakage reactance (%) measured in the primary with the tertiary short circuited and the secondary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1766 | Transformer | PrimVolt | PRIMVOLT_TF | Externals | Primary winding rated voltage (kV). The field is specified line to line in the station internals and line to ground in the station externals. | Float | kV | kV | DPF |  |  | TRUE | 0.1 | 300 | 0.1 | 300 | VOLTPR | Yes | Yes | Yes | Yes
1767 | Transformer | PrimVoltNominal | PRIMVOLTNOMINAL_TF | Externals | Primary winding nominal voltage (kV). This optional field can be used to define fixed tap distribution transformers. | Float | kV | kV | DPF |  |  | FALSE | 0.1 | 300 | 0.1 | 300 | VOLTLEVEL | Yes | Yes | Yes | Yes
1768 | Transformer | PrimVoltRated | N/A | Internals | Primary winding rated voltage (kV). This field is deprecated. | Float | kV | kV | DPF |  |  | FALSE | 0.1 | 300 | 0.1 | 300 |  | Yes | Yes | Yes | Yes
1769 | Transformer | PriTap | #N/A | Internals | Primary tap type enumeration. The field has the following values: None = 0, 1 = Fixed, 2 = Regulating | String | #N/A | #N/A | DPF, LVM |  | Required if transformer has tap changers on primary. | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.NAME | Yes | Yes | Yes | Yes
1770 | Transformer | PriWinding | #N/A | Internals | Primary winding type enumeration which is provided in the station internals transformer object if the associaated transformer model field TFMOD_TF is not provided. The enumeration has the following values: 0 = None, 1 = Delta 2 = Grounded_Wye, 3 = Wye, 4 = ZigZag. | String | #N/A | #N/A | DPF |  | 0: None 1: Delta 2: Grounded wye 3: Wye 4: Zigzag | FALSE | #N/A | #N/A | #N/A | #N/A | TFPRIMWINDTYPE | Yes | Yes | Yes | Yes
1771 | Transformer | PrLdcR | PRLDCR_TF | Internals | Primary winding line drop compensation resistance (Volts). | Float | Volts | Volts | DPF, LVM |  | Relaxed limits from 0:100 to -100:100 | FALSE | -100 | 100 | -100 | 100 | PRTAP.LDCCMPRV | Yes | Yes | Yes | Yes
1772 | Transformer | PrLdcX | PRLDCX_TF | Internals | Primary winding line drop compensation reactance (Volts). | Float | Volts | Volts | DPF, LVM |  |  | FALSE | -100 | 100 | -100 | 100 | PRTAP.LDCCMPXV | Yes | Yes | Yes | Yes
1773 | Transformer | PrNormTap | PRNORMTAP_TF | Internals | Primary winding normal tap position. | Integer | #N/A | #N/A | DPF | User-configurable through Defaults File | Optional if primary tap changer is not available. | FALSE | Minimum tap given on tap model. | Maximum tap given on tap model. | Minimum tap given on tap model. | Maximum tap given on tap model. | PRTAP.NORMTAP | Yes | Yes | Yes | Yes
1774 | Transformer | PrPhaseSense | PRPHASESENSE_TF | Internals | Non-neutral phases that are sensed (measured) for the primary winding tap. Valid entries include A, B, C, AB, BC, CA, or ABC. | String | #N/A | #N/A | DPF |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.PHSENSED | Yes | Yes | Yes | Yes
1775 | Transformer | PrPtRatio | PRPTRATIO_TF | Internals | Primary winding PT ratio (such as 63.5 or 60.0). | Float | ratio | ratio | DPF, LVM |  |  | FALSE | 1 | 2000 | 1 | 2000 | PRTAP.PTRATIO | Yes | Yes | Yes | Yes
1776 | Transformer | PrRegNodeId | PRREGNODEID_TF | Internals | Primary winding voltage regulation node ID. | String | #N/A | #N/A | DPF, LVM |  | A node ID must be given (if there is a regulating primary tap changer). | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.REGNODE.NAME | Yes | Yes | Yes | Yes
1777 | Transformer | PrReverseReg | PRREVERSEREG_TF | Internals | Flag indicating primary winding tap changer has reverse regulation capability (True = has reverse capability). | Boolean | #N/A | #N/A | DPF | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.REVREG | Yes | Yes | Yes | Yes
1778 | Transformer | PrRevRegNode | PRREVREGNODE_TF | Internals | Primary winding reverse voltage regulation node ID. This field only needs to be filled in if the PRREVERSEREG_TF field is set to True. | String | #N/A | #N/A | DPF | “” | A node ID must be given if the tap changer has reverse regulation capability. | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.REVREGND | Yes | Yes | Yes | Yes
1779 | Transformer | PrTapModel | PRTAPMODEL_TF | Internals | Primary associated tap changer model name. | String | #N/A | #N/A | DPF, LVM | “” | The tap model name must match a Tap Changer Model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | PRTAP.TAPMODEL.NAME | Yes | Yes | Yes | Yes
1780 | Transformer | PrVoltSetpointDeadBand | PRVOLTSETPOINTDEADBAND_TF | Internals | Primary winding tap changer voltage setpoint deadband (percent). The LVM generated setpoint control will be discarded during the LVM post processing if the tap changer voltage is within the original value plus/minus this deadband value. | Float | percent | percent | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | PRTAP.VSETPNTDEADBAND | Yes | Yes | Yes | Yes
1781 | Transformer | PrVoltSetpointRangeMax | PRVOLTSETPOINTRANGEMAX_TF | Internals | Primary winding tap changer voltage setpoint maximum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is larger than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | PRTAP.VSETPNTRANGEMAX | Yes | Yes | Yes | Yes
1782 | Transformer | PrVoltSetpointRangeMin | PRVOLTSETPOINTRANGEMIN_TF | Internals | Primary winding tap changer voltage setpoint minimum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is less than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | PRTAP.VSETPNTRANGEMIN | Yes | Yes | Yes | Yes
1783 | Transformer | PrVreduct | PRVREDUCT_TF | Internals | Primary winding tap changer voltage reduction setting. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF | User-configurable through Defaults File |  | FALSE | 0.0/0.0 | 0.10/12.0 | 0.0/0.0 | 0.10/12.0 | PRTAP.VREDPU | Yes | Yes | Yes | Yes
1784 | Transformer | PrVregLineLine | PRVREGLINELINE_TF | Internals | Flag that indicates whether the regulated (sensed) phases for the primary tap is measured line to line or line to ground (True = line to line). | Boolean | #N/A | #N/A | DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PRIMPTVMEASLL | Yes | Yes | Yes | Yes
1785 | Transformer | PrVtarget | PRVTARGET_TF | Internals | Primary winding tap changer voltage target. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.80/96.0 | 1.20/144.0 | 0.80/96.0 | 1.20/144.0 | PRTAP.VTARGET | Yes | Yes | Yes | Yes
1786 | Transformer | Rating1 | #N/A | Internals | Operational limit 1 for a two-winding transformer (MVA). | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALUE | Yes | Yes | Yes | Yes
1787 | Transformer | Rating1_Sec | #N/A | Internals | Secondary winding operational limit 1 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALS | Yes | Yes | Yes | Yes
1788 | Transformer | Rating1_Ter | #N/A | Internals | Tertiary winding operational limit 1 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALT | Yes | Yes | Yes | Yes
1789 | Transformer | Rating2 | #N/A | Internals | Operational limit 2 for a two-winding transformer (MVA). | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALUE | Yes | Yes | Yes | Yes
1790 | Transformer | Rating2_Sec | #N/A | Internals | Secondary winding operational limit 2 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALS | Yes | Yes | Yes | Yes
1791 | Transformer | Rating2_Ter | #N/A | Internals | Tertiary winding operational limit 2 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALT | Yes | Yes | Yes | Yes
1792 | Transformer | Rating3 | #N/A | Internals | Operational limit 3 for a two-winding transformer (MVA). | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALUE | Yes | Yes | Yes | Yes
1793 | Transformer | Rating3_Sec | #N/A | Internals | Secondary winding operational limit 3 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALS | Yes | Yes | Yes | Yes
1794 | Transformer | Rating3_Ter | #N/A | Internals | Tertiary winding operational limit 3 for a three-winding transformer. | Float | MVA | MVA | DPF |  |  | FALSE |  |  |  |  | LIMVALT | Yes | Yes | Yes | Yes
1795 | Transformer | RegLimit1 | #N/A | Internals | Dynamic regulation limit 1 (Amps). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | amps | amps | DPF |  | Required for regulators that have a dynamic limit. | FALSE | 0 | 4000 | 0 | 4000 | REGLIMIT | Yes | Yes | Yes | Yes
1796 | Transformer | RegLimit2 | #N/A | Internals | Dynamic regulation limit 2 (Amps). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | amps | amps | DPF |  | Required for regulators that have a dynamic limit. | FALSE | 0 | 4000 | 0 | 4000 | REGLIMIT | Yes | Yes | Yes | Yes
1797 | Transformer | RegLimit3 | #N/A | Internals | Dynamic regulation limit 3 (Amps). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | amps | amps | DPF |  | Required for regulators that have a dynamic limit. | FALSE | 0 | 4000 | 0 | 4000 | REGLIMIT | Yes | Yes | Yes | Yes
1798 | Transformer | RegLimit4 | #N/A | Internals | Dynamic regulation limit 4 (Amps). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | amps | amps | DPF |  | Required for regulators that have a dynamic limit. | FALSE | 0 | 4000 | 0 | 4000 | REGLIMIT | Yes | Yes | Yes | Yes
1799 | Transformer | RegLimit5 | #N/A | Internals | Dynamic regulation limit 5 (Amps). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | amps | amps | DPF |  | Required for regulators that have a dynamic limit. | FALSE | 0 | 4000 | 0 | 4000 | REGLIMIT | Yes | Yes | Yes | Yes
1800 | Transformer | RegLimitEvent1 |  | Internals | Regulation limit event 1? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1801 | Transformer | RegLimitEvent2 |  | Internals | Regulation limit event 2? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1802 | Transformer | RegLimitEvent3 |  | Internals | Regulation limit event 3? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1803 | Transformer | RegLimitEvent4 |  | Internals | Regulation limit event 4? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1804 | Transformer | RegLimitEvent5 |  | Internals | Regulation limit event 5? | Boolean | [5 empty] | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1805 | Transformer | RegStep1 | #N/A | Internals | Dynamic regulation limit step 1 (%). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | percent | percent | DPF |  | Required for regulators that have a dynamic limit. | FALSE |  |  |  |  | RGLIMSTP | Yes | Yes | Yes | Yes
1806 | Transformer | RegStep2 | #N/A | Internals | Dynamic regulation limit step 2 (%). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | percent | percent | DPF |  | Required for regulators that have a dynamic limit. | FALSE |  |  |  |  | RGLIMSTP | Yes | Yes | Yes | Yes
1807 | Transformer | RegStep3 | #N/A | Internals | Dynamic regulation limit step 3 (%). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | percent | percent | DPF |  | Required for regulators that have a dynamic limit. | FALSE |  |  |  |  | RGLIMSTP | Yes | Yes | Yes | Yes
1808 | Transformer | RegStep4 | #N/A | Internals | Dynamic regulation limit step 4 (%). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | percent | percent | DPF |  | Required for regulators that have a dynamic limit. | FALSE |  |  |  |  | RGLIMSTP | Yes | Yes | Yes | Yes
1809 | Transformer | RegStep5 | #N/A | Internals | Dynamic regulation limit step 5 (%). This field may be filled in for station internal regulators with a dynamic limit if the associaated transformer model field TFMOD_TF is not provided. | Float | percent | percent | DPF |  | Required for regulators that have a dynamic limit. | FALSE |  |  |  |  | RGLIMSTP | Yes | Yes | Yes | Yes
1810 | Transformer | RegulationMargin | REGULATIONMARGIN_TF | Internals | Regulator/LTC voltage regulation margin is expressed as a percent of the voltage base. The regulation margin is used in the LTC/Regulator Control Function in the Heuristic Load and Vvolt/VAR Management (LVM) application to provide a guard band to ensure that the voltage reduction will not result in low voltage violations. This individual regulator/LTC value has priority over the global value. | Float | percent | percent | DPF, LVM | 0.005 |  | FALSE | #N/A | #N/A | 0 | 0.1 | REGULATIONMARGIN | Yes | Yes | Yes | Yes
1811 | Transformer | RegUnits | #N/A | Internals | Regulating tap voltage settings enumeration. This field indicates the voltage representation of the voltage target, bandwidth, and voltage reduction fields (if any is supoported). This field is needed if the associated transformer model in field TFMOD_TF is not provided | String | #N/A | #N/A | OPS |  | Per_Unit or Volt_Actual_Base | FALSE | #N/A | #N/A | #N/A | #N/A | REGUNITS | Yes | Yes | Yes | Yes
1812 | Transformer | RGround | RGROUNDPRIME_TF | Internals | Primary grounding resistance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if primary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | PRIMGNDR | Yes | Yes | Yes | Yes
1813 | Transformer | RGroundsec | RGROUNDSEC_TF | Internals | Secondary grounding resistance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if secondary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | SEC1GNDR | Yes | Yes | Yes | Yes
1814 | Transformer | RGroundtert | RGROUNDTERT_TF | Internals | Tertiary grounding resistance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if tertiary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | SEC2GNDR | Yes | Yes | Yes | Yes
1815 | Transformer | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
1816 | Transformer | ScBandwth | SCBANDWTH_TF | Internals | Secondary winding tap changer two-sided bandwidth. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.001/0.12 | 0.1/24.0 | 0.001/0.12 | 0.1/24.0 | SECTAP.BANDWITH | Yes | Yes | Yes | Yes
1817 | Transformer | ScControlCapability | SCCONTROLCAPABILITY_TF | Internals | Secondary winding tap changer control capability enumeration. This includes the ability to issue raise/lower tap steps and/or change a voltage setpoint. The enumeration includes the following values: 0 = No Control, 1 = Raise/Lower Only, 2 = Voltage Setpoint Only, 3 = Raise/Lower or Voltage Setpoint, and 4 = Voltage Redcution Only. | Integer | enumeration | enumeration | DPF, LVM |  | 0: No Control 1: Raise Lower Only 2: Voltage Setpoint Only 3: Raise Lower or Voltage Setpoint 4: Voltage Reduction Only | FALSE | 0 | 4 | 0 | 4 |  | Yes | Yes | Yes | Yes
1818 | Transformer | ScControllable | SCCONTROLABLE_TF | Internals | Secondary winding tap changer controllability enumeration. The field has the following values: 0 = Fixed, 1 = Local control only, 2 = Remote control only, 3 = Remote with local control capability. | Integer | enumeration | enumeration | DPF, LVM |  | Required if transformer has tap changers on secondary. The field has the following values: 0 = Fixed 1 = Local only 2 = Remote only 3 = Remote with local control | FALSE | 0 | 4 | 0 | 4 | SECTAP.TAPCNTRL | Yes | Yes | Yes | Yes
1819 | Transformer | ScCtRatio | SCCTRATIO_TF | Internals | Secondary winding CT ratio. | Float | ratio | ratio | DPF |  | Required if transformer has tap changers on secondary. | FALSE | 1 | 15000 | 1 | 15000 | SECTAP.CTRATIO | Yes | Yes | Yes | Yes
1820 | Transformer | ScCtSecamps | SCCTSECAMPS_TF | Internals | Secondary winding CT full load secondary rating (Amps). | Float | Amps | Amps | DPF |  | User-configurable through Defaults File | FALSE | 0.1 | 20 | 0.1 | 20 | SECTAP.CTSECAMP | Yes | Yes | Yes | Yes
1821 | Transformer | ScCurrentControlMode | SCCURRENTCONTROLMODE_TF | Internals | The secondary winding tap changer active control mode enumeration. This field is used in combination with the SCCONTROLCAPABILITY_TF field to determine the active control mode if the tap changer has multiple control mode capability. The enumeration includes the following values: 0 = None, 1 = Raise/Lower Tap, 2 = Voltage Setpoint, 3 = Voltage Reduction. This field is not applicable if the tap changer only supports a single control mode. | Integer | enumeration | enumeration | DPF, LVM |  | 0: None 1: Raise Lower Tap 2: Voltage Setpoint 3: Voltage Reduction | FALSE | 0 | 3 | 0 | 3 |  | Yes | Yes | Yes | Yes
1822 | Transformer | ScLdcR | SCLDCR_TF | Internals | Secondary winding line drop compensation resistance (Volts). | Float | Volts | Volts | DPF, LVM |  |  | FALSE | -100 | 100 | -100 | 100 | SECTAP.LDCCMPRV | Yes | Yes | Yes | Yes
1823 | Transformer | ScLdcX | SCLDCX_TF | Internals | Secondary winding line drop compensation reactance (Volts). | Float | Volts | Volts | DPF, LVM |  |  | FALSE | -100 | 100 | -100 | 100 | SECTAP.LDCCMPXV | Yes | Yes | Yes | Yes
1824 | Transformer | ScNormTap | SCNORMTAP_TF | Internals | Secondary winding normal tap position. | Integer | #N/A | #N/A | DPF | User-configurable through Defaults File | Optional if secondary tap changer is not available. | FALSE | Minimum tap given on tap model. | Maximum tap given on tap model. | Minimum tap given on tap model. | Maximum tap given on tap model. | SECTAP.NORMTAP | Yes | Yes | Yes | Yes
1825 | Transformer | ScPhaseSense | SCPHASESENSE_TF | Internals | Non-neutral phases that are sensed (measured) for the secondary winding tap. Valid entries include A, B, C, AB, BC, CA, or ABC. | String | #N/A | #N/A | DPF |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.PHSENSED | Yes | Yes | Yes | Yes
1826 | Transformer | ScPtRatio | SCPTRATIO_TF | Internals | Secondary winding PT ratio (such as 63.5 or 60.0). | Float | ratio | ratio | DPF, LVM |  |  | FALSE | 1 | 400 | 1 | 400 | SECTAP.PTRATIO | Yes | Yes | Yes | Yes
1827 | Transformer | ScRegNodeId | SCREGNODEID_TF | Internals | Secondary winding voltage regulation node ID. | String | #N/A | #N/A | DPF, LVM |  | A node ID must be given (if there is a regulating secondary tap changer). | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.REGNODE.NAME | Yes | Yes | Yes | Yes
1828 | Transformer | ScReverseReg | SCREVERSEREG_TF | Internals | Flag indicating secondary winding tap changer has reverse regulation capability (True = has reverse capability). | Boolean | #N/A | #N/A | DPF | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.REVREG | Yes | Yes | Yes | Yes
1829 | Transformer | ScRevRegNode | SCREVREGNODE_TF | Internals | Secondary winding reverse voltage regulation node ID. This field only needs to be filled in if the SCREVERSEREG_TF field is set to True. | String | #N/A | #N/A | DPF | “” | A node ID must be given if the tap changer has reverse regulation capability. | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.REVREGND | Yes | Yes | Yes | Yes
1830 | Transformer | ScTapModel | SCTAPMODEL_TF | Internals | Secondary associated tap changer model name. | String | #N/A | #N/A | DPF, LVM | “” | The tap model name must match a Tap Changer Model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.TAPMODEL.NAME | Yes | Yes | Yes | Yes
1831 | Transformer | ScVoltSetpointDeadBand | SCVOLTSETPOINTDEADBAND_TF | Internals | Secondary winding tap changer voltage setpoint deadband (percent). The LVM generated setpoint control will be discarded during the LVM post processing if the tap changer voltage is within the original value plus/minus this deadband value. | Float | percent | percent | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | SECTAP.VSETPNTDEADBAND | Yes | Yes | Yes | Yes
1832 | Transformer | ScVoltSetpointRangeMax | SCVOLTSETPOINTRANGEMAX_TF | Internals | Secondary winding tap changer voltage setpoint maximum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is larger than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | SCTAP.VSETPNTRANGEMAX | Yes | Yes | Yes | Yes
1833 | Transformer | ScVoltSetpointRangeMin | SCVOLTSETPOINTRANGEMIN_TF | Internals | Secondary winding tap changer voltage setpoint minimum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is less than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | SCTAP.VSETPNTRANGEMIN | Yes | Yes | Yes | Yes
1834 | Transformer | ScVreduct | SCVREDUCT_TF | Internals | Secondary winding tap changer voltage reduction setting. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF | User-configurable through Defaults File |  | FALSE | 0.0/0.0 | 0.10/12.0 | 0.0/0.0 | 0.10/12.0 | SECTAP.VREDPU | Yes | Yes | Yes | Yes
1835 | Transformer | ScVregLineLine | SCVREGLINELINE_TF | Internals | Flag that indicates whether the regulated (sensed) phases for the secondary tap is measured line to line or line to ground (True = line to line). | Boolean | #N/A | #N/A | DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SECPTVMEASLL | Yes | Yes | Yes | Yes
1836 | Transformer | ScVtarget | SCVTARGET_TF | Internals | Secondary winding tap changer voltage target. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.80/96.0 | 1.20/144.0 | 0.80/96.0 | 1.20/144.0 | SECTAP.VTARGET | Yes | Yes | Yes | Yes
1837 | Transformer | SecLagsPrimDegree | #N/A | Internals | Phase angle shift (secondary winding lags primary winding in degrees). This field is required for station internal transformers when a transformer model is not provided. The Converter uses this field along with the winding types and phase fields to determine the value for the TFTYPE_TFMOD field in the global resources file. | Float | degrees | degrees | DPF, LVM, FISR, SCC | 0 |  | FALSE | 0 | 330 | 0 | 330 | SECLAGSPRIMPHAGEANGLE | Yes | Yes | Yes | Yes
1838 | Transformer | SecMaxTap | #N/A | Internals | Secondary maximum tap step. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field ScTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if secondary tap changer is not available. | FALSE |  |  |  |  | SECMAXTAPPOS | Yes | Yes | Yes | Yes
1839 | Transformer | SecMinTap | #N/A | Internals | Secondary minimum tap step. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field ScTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if secondary tap changer is not available. | FALSE |  |  |  |  | SECMINTAPPOS | Yes | Yes | Yes | Yes
1840 | Transformer | SecNomTap | #N/A | Internals | Secondary nominal tap step for fixed tap model. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field ScTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if secondary tap changer is not available. | FALSE |  |  |  |  | SECNOMTAPPOS | Yes | Yes | Yes | Yes
1841 | Transformer | SecondaryRegNode | #N/A | Internals | Secondary regulation node location (Primary, Secondary, or Tertiary connection node). | Integer | enumeration | enumeration | DPF |  |  | FALSE | 0 | 2 | 0 | 2 |  | Yes | Yes | Yes | Yes
1842 | Transformer | SecPhase | SECPHASE_TF | Internals | Secondary winding transformer phase connections. | String | #N/A | #N/A | OPS |  | A, B, C, AN, BN, CN, ABC, or ABCN. | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1843 | Transformer | SecTap | #N/A | Internals | Secondary tap type enumeration. The field has the following values: None = 0, 1 = Fixed, 2 = Regulating | String | #N/A | #N/A | DPF, LVM |  | Required if transformer has tap changers on secondary. | FALSE | #N/A | #N/A | #N/A | #N/A | SECTAP.NAME | Yes | Yes | Yes | Yes
1844 | Transformer | SecTapCost | #N/A | Internals | Secondary tap movement cost. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Float | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | SECTAPCOST | Yes | Yes | Yes | Yes
1845 | Transformer | SecTapCost | #N/A | Internals | Tertiary tap movement cost. This field may be filled in for station internal transformers and regulators if the associaated primary winding tap model field PrTapModel is not provided. | Float | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | TERTTAPCOST | Yes | Yes | Yes | Yes
1846 | Transformer | SecTapStep | #N/A | Internals | Secondary tap step increment(%). This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field ScTapModel is not provided. | Float | percent | percent | DPF, LVM |  | Optional if secondary tap changer is not available. | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1847 | Transformer | SecTerR1 | #N/A | Internals | For three-winding transformers, the leakage resistance (%) measured in the secondary with the tertiary short circuited and the primary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1848 | Transformer | SecTerX1 | #N/A | Internals | For three-winding transformers, the leakage reactance (%) measured in the secondary with the tertiary short circuited and the primary open. The impedance value is referred to the transformer power base, and it is used to determine the total winding impedance values. | Float | percent | percent | OPS, DPF, LVM, FISR, SCC |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1849 | Transformer | SecVolt | SECVOLT_TF | Externals | Secondary winding rated voltage (kV). For the transformer whose secondary is delta connected, if there exists a center tap ground on one leg of a three winding transformer or a single-phase transformer in a bank, this field is set to the line to ground voltage of that leg or transformer in the bank. Otherwise, the field is set to the normal line to ground voltage. | Float | kV | kV | DPF |  |  | TRUE | 0.11 | 100 | 0.11 | 100 | VOLTSC | Yes | Yes | Yes | Yes
1850 | Transformer | SecVoltNominal | SECVOLTNOMINAL_TF | Externals | Seconday winding nominal voltage (kV). | Float | kV | kV | DPF |  |  | FALSE | 0.11 | 100 | 0.11 | 100 | VOLTSECLEVEL | Yes | Yes | Yes | Yes
1851 | Transformer | SecVoltRated | N/A | Internals | Secondary winding rated voltage (kV). This field is deprecated. | Float | kV | kV | DPF |  |  | FALSE | 0.11 | 100 | 0.11 | 100 |  | Yes | Yes | Yes | Yes
1852 | Transformer | SecWinding | #N/A | Internals | Secondary winding type enumeration which is provided in the station internals transformer object if the associaated transformer model field TFMOD_TF is not provided. The enumeration has the following values: 0 = None, 1 = Delta 2 = Grounded_Wye, 3 = Wye, 4 = ZigZag. | String | #N/A | #N/A | DPF |  | 0: None 1: Delta 2: Grounded wye 3: Wye 4: Zigzag | FALSE | #N/A | #N/A | #N/A | #N/A | TFSECWINDTYPE | Yes | Yes | Yes | Yes
1853 | Transformer | SelfProtection | SELFPROTECTION_TF | Internals | This field contains comma-separated values (integers) of transformer self-protection types. The available transformer self-protection types values are as follows: None = 0 Differential - Transformer = 1 Differential - Bus = 2 Restricted Earth Fault (REF) = 3 Buchholz = 4 Distance = 5 Tank Earth = 6 Overfluxing = 7 Thermal = 8 Other = 9 | String | #N/A | #N/A | FISR, AFR, PLOS, PRV | None = 0 |  | FALSE | #N/A | #N/A | #N/A | #N/A | SELFPROTECTION | Yes | No | No | No
1854 | Transformer | ServiceCenter | SERVCNTR_TF | Internals | Associated service center. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | SERVCNTR.NAME | Yes | Yes | Yes | Yes
1855 | Transformer | SizeUnits | #N/A | Internals | Size units enumeration. This field has the following values: 1 = kVA, 2 = MVA , 3 = Regulated_kVA. This field is only applicable for transformers and regulators defined in the station internals file that do not specify an associated transformer model. Otherwise, the size unit enumeration is taken from the associated transformer model defined in the global resources file. | Integer | enumeration | enumeration | DPF |  | 1: kVA 2: MVA 3: Regulated kVA (for regulators) | FALSE | 1 | 3 | 1 | 3 | TFMODELUNITS | Yes | Yes | Yes | Yes
1856 | Transformer | SRatingTer | #N/A | Internals | Tertiary winding rating (kVA or MVA). This field is provided in the station internals transformer object if the associaated transformer model field TFMOD_TF is not provided. | Float | kVA or MVA | kVA or MVA | DPF |  |  | FALSE | 0 | #N/A | 0 | #N/A | SRATINGTER | Yes | Yes | Yes | Yes
1857 | Transformer | State | STATE_TF | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1858 | Transformer | StructureId | STRUCTURE_ID | Internals | ID of a structure (e.g., pole) that is associated with the device | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRUCTUREID | Yes | Yes | Yes | No
1859 | Transformer | SuppressFeeder |  | Internals | Flag indicating that the device name is suppressed. A topology object, a bus, or a fault indicator with the suppressed feeder flag set to true does not show the nominal feeder name in DMS displays. | Boolean | #N/A | #N/A | NTP | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1860 | Transformer | SymbolPlacement:GeometryLevel | GEOMLEVEL_TF | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1861 | Transformer | SymbolPlacement:GeometryType | GEOMTYPE_TF | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1862 | Transformer | SymbolPlacement:Rotation | ROTATION_TF | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1863 | Transformer | SymbolPlacement:Size | SIZE_TF | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1864 | Transformer | SymbolPlacement:X | WCX_TF | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1865 | Transformer | SymbolPlacement:X2 | WCX2_TF | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1866 | Transformer | SymbolPlacement:Y | WCY_TF | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1867 | Transformer | SymbolPlacement:Y2 | WCY2_TF | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1868 | Transformer | TapChanger | TAPCHANGER_TF | Internals | Enumerated value indicating whether there are taps on the transformer (on primary, secondary, or tertiary). The following enumeration applies: 0 = No windings have taps, 1 = Primary, 2 = Secondary, 3 = Tertiary, 4 = Primary and secondary, 5 = secondary and tertiary, 6 = primary and Tertiary, and 7 = Primary, secondary, and tertiary. | Integer | enumeration | enumeration | DPF, LVM | 0 | Required if transformer has tap changers. Values supported include the following: 0: No windings have taps 1: Primary winding has a tap 2: Secondary winding has a tap 3: Tertiary winding has a tap 4: Primary and secondary windings have a tap 5: Secondary and Tertiary windings have a tap 6: Primary and tertiary windings have a tap 7: Primary, secondary, and tertiary windings have a tap | FALSE | 0 | 7 | 0 | 7 |  | Yes | Yes | Yes | Yes
1869 | Transformer | TeBandwth | TEBANDWTH_TF | Internals | Tertiary winding tap changer two-sided bandwidth. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.001/0.12 | 0.1/24.0 | 0.001/0.12 | 0.1/24.0 | TETAP.BANDWITH | Yes | Yes | Yes | Yes
1870 | Transformer | TeControlCapability | TECONTROLCAPABILITY_TF | Internals | Tertiary winding tap changer control capability enumeration. This includes the ability to issue raise/lower tap steps and/or change a voltage setpoint. The enumeration includes the following values: 0 = No Control, 1 = Raise/Lower Only, 2 = Voltage Setpoint Only, 3 = Raise/Lower or Voltage Setpoint, and 4 = Voltage Redution Only. | Integer | enumeration | enumeration | DPF, LVM |  | 0: No Control 1: Raise Lower Only 2: Voltage Setpoint Only 3: Raise Lower or Voltage Setpoint 4: Voltage Reduction Only | FALSE | 0 | 4 | 0 | 4 |  | Yes | Yes | Yes | Yes
1871 | Transformer | TeControllable | TECONTROLABLE_TF | Internals | Tertiary winding tap changer controllability enumeration. The field has the following values: 0 = Fixed, 1 = Local control only, 2 = Remote control only, 3 = Remote with local control capability. | Integer | enumeration | enumeration | DPF, LVM |  | Required if transformer has tap changers on tertiary. The field has the following values: 0 = Fixed 1 = Local only 2 = Remote only 3 = Remote with local control | FALSE | 0 | 4 | 0 | 4 | TETAP.TAPCNTRL | Yes | Yes | Yes | Yes
1872 | Transformer | TeCtRatio | TECTRATIO_TF | Internals | Tertiary winding CT ratio. | Float | ratio | ratio | DPF |  | Required if transformer has tap changers on tertiary. | FALSE | 1 | 15000 | 1 | 15000 | TETAP.CTRATIO | Yes | Yes | Yes | Yes
1873 | Transformer | TeCtSecamps | TECTSECAMPS_TF | Internals | Tertiary winding CT full load secondary rating (Amps). | Float | Amps | Amps | DPF |  | User-configurable through Defaults File | FALSE | 0.1 | 20 | 0.1 | 20 | TETAP.CTSECAMP | Yes | Yes | Yes | Yes
1874 | Transformer | TeCurrentControlMode | TECURRENTCONTROLMODE_TF | Internals | The tertiary winding tap changer active control mode enumeration. This field is used in combination with the TECONTROLCAPABILITY_TF field to determine the active control mode if the tap changer has multiple control mode capability. The enumeration includes the following values: 0 = None, 1 = Raise/Lower Tap, 2 = Voltage Setpoint, 3 = Voltage Reduction. This field is not applicable if the tap changer only supports a single control mode. | Integer | enumeration | enumeration | DPF, LVM |  | 0: None 1: Raise Lower Tap 2: Voltage Setpoint 3: Voltage Reduction | FALSE | 0 | 3 | 0 | 3 |  | Yes | Yes | Yes | Yes
1875 | Transformer | TeLdcR | TELDCR_TF | Internals | Tertiary winding line drop compensation resistance (Volts). | Float | Volts | Volts | DPF, LVM |  |  | FALSE | -100 | 100 | -100 | 100 | TETAP.LDCCMPRV | Yes | Yes | Yes | Yes
1876 | Transformer | TeLdcX | TELDCX_TF | Internals | Tertiary winding line drop compensation reactance (Volts). | Float | Volts | Volts | DPF, LVM |  |  | FALSE | -100 | 100 | -100 | 100 | TETAP.LDCCMPXV | Yes | Yes | Yes | Yes
1877 | Transformer | Telemetered | TELEMETERED_TF | Internals | If not defined, the default value is False, meaning the device is not telemetered in SCADA. This information currently is not used by DMS application. It is provided to be used by any other application that might use the source data. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1878 | Transformer | TempSched1 |  | Internals | Temperature schedule 1 for primary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1879 | Transformer | TempSched1_Sec |  | Internals | Temperature schedule 1 for secondary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1880 | Transformer | TempSched1_Ter |  | Internals | Temperature schedule 1 for tertiary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1881 | Transformer | TempSched2 |  | Internals | Temperature schedule 2 for primary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1882 | Transformer | TempSched2_Sec |  | Internals | Temperature schedule 2 for secondary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1883 | Transformer | TempSched2_Ter |  | Internals | Temperature schedule 2 for tertiary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1884 | Transformer | TempSched3 |  | Internals | Temperature schedule 3 for primary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1885 | Transformer | TempSched3_Sec |  | Internals | Temperature schedule 3 for secondary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1886 | Transformer | TempSched3_Ter |  | Internals | Temperature schedule 3 for tertiary winding. | String | [5 empty] | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1887 | Transformer | TeNormTap | TENORMTAP_TF | Internals | Tertiary winding normal tap position. | Integer | #N/A | #N/A | DPF | User-configurable through Defaults File | Optional if tertiary tap changer is not available. | FALSE | Minimum tap given on tap model. | Maximum tap given on tap model. | Minimum tap given on tap model. | Maximum tap given on tap model. | TETAP.NORMTAP | Yes | Yes | Yes | Yes
1888 | Transformer | TePhaseSense | TEPHASESENSE_TF | Internals | Non-neutral phases that are sensed (measured) for the tertiary winding tap. Valid entries include A, B, C, AB, BC, CA, or ABC. | String | #N/A | #N/A | DPF |  | A, B, C, AB, BC, CA, or ABC. | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.PHSENSED | Yes | Yes | Yes | Yes
1889 | Transformer | TePtRatio | TEPTRATIO_TF | Internals | Tertiary winding PT ratio (such as 63.5 or 60.0). | Float | ratio | ratio | DPF, LVM |  |  | FALSE | 1 | 400 | 1 | 400 | TETAP.PTRATIO | Yes | Yes | Yes | Yes
1890 | Transformer | TeRegNodeId | TEREGNODEID_TF | Internals | Tertiary winding voltage regulation node ID. | String | #N/A | #N/A | DPF, LVM |  | A node ID must be given (if there is a regulating tertiary tap changer). | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.REGNODE.NAME | Yes | Yes | Yes | Yes
1891 | Transformer | TeReverseReg | TEREVERSEREG_TF | Internals | Flag indicating tertiary winding tap changer has reverse regulation capability (True = has reverse capability). | Boolean | #N/A | #N/A | DPF | User-configurable through Defaults File |  | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.REVREG | Yes | Yes | Yes | Yes
1892 | Transformer | TeRevRegNode | TEREVREGNODE_TF | Internals | Tertiary winding reverse voltage regulation node ID. This field only needs to be filled in if the TEREVERSEREG_TF field is set to True. | String | #N/A | #N/A | DPF | “” | A node ID must be given if the tap changer has reverse regulation capability. | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.REVREGND | Yes | Yes | Yes | Yes
1893 | Transformer | TerLagsPrimDegree | #N/A | Internals | Phase angle shift (teriary winding lags primary winding in degrees). This field is required for station internal three-winding transformers when a transformer model is not provided. The Converter uses this field along with the winding types and phase fields to determine the value for the TFTYPE_TFMOD field in the global resources file. | Float | degrees | degrees | DPF, LVM, FISR, SCC | 0 |  | FALSE | 0 | 330 | 0 | 330 | TERTLAGSPRIMPHAGEANGLE | Yes | Yes | Yes | Yes
1894 | Transformer | TerTap | #N/A | Internals | Tertiary tap type enumeration. The field has the following values: None = 0, 1 = Fixed, 2 = Regulating | String | #N/A | #N/A | DPF, LVM |  | Required if transformer has tap changers on tertiary. | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.NAME | Yes | Yes | Yes | Yes
1895 | Transformer | TertiaryNode | TENODE_TF | Internals | Tertiary node ID (only required for a three-winding transformer). | String | #N/A | #N/A | OPS |  | If the transformer has three windings, then a node ID must be given. | FALSE | #N/A | #N/A | #N/A | #N/A | TERNODE | Yes | Yes | Yes | Yes
1896 | Transformer | TertiaryRegNode | #N/A | Internals | Tertiary regulation node location (Primary, Secondary, or Tertiary connection node). | Integer | enumeration | enumeration | DPF |  |  | FALSE | 0 | 2 | 0 | 2 |  | Yes | Yes | Yes | Yes
1897 | Transformer | TertMaxTap | #N/A | Internals | Tertiary maximum tap step. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field TeTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | TERTMAXTAPPOS | Yes | Yes | Yes | Yes
1898 | Transformer | TertMinTap | #N/A | Internals | Tertiary minimum tap step. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field TeTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | TERTMINTAPPOS | Yes | Yes | Yes | Yes
1899 | Transformer | TertNomTap | #N/A | Internals | Tertiary nominal tap step for fixed tap model. This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field TeTapModel is not provided. | Integer | #N/A | #N/A | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE |  |  |  |  | TERTNOMTAPPOS | Yes | Yes | Yes | Yes
1900 | Transformer | TertPhase | TERTPHASE_TF | Internals | Tertiary winding transformer phase connections (three-winding transformer). | String | #N/A | #N/A | OPS |  | A, B, C, AN, BN, CN, ABC, or ABCN. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1901 | Transformer | TertTapCost |  | Internals | Tertoaru tap movement cost. This field may be filled in for station internal transformers and regulators if the associaated tertiary winding tap model field TeTapModel is not provided. | Float |  |  | LVM |  |  | FALSE: TRUE; No: Yes; No: Yes; No: Yes; No: Yes
1902 | Transformer | TertTapStep | #N/A | Internals | Tertiary tap step increment(%). This field is filled in for station internal transformers and regulators if the associaated primary winding tap model field TeTapModel is not provided. | Float | percent | percent | DPF, LVM |  | Optional if tertiary tap changer is not available. | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1903 | Transformer | TertVolt | TERTVOLT_TF | Externals | Tertiary winding rated voltage (kV). The field is specified line to line in the station internals and line to ground in the station externals. | Float | kV | kV | DPF, LVM, FISR, SCC |  |  | FALSE | 0.11 | 100 | 0.11 | 100 | VOLTTE | Yes | Yes | Yes | Yes
1904 | Transformer | TertVoltNominal | TERTVOLTNOMINAL_TF | Externals | Teriary winding nominal voltage (kV). | Float | kV | kV | DPF |  |  | FALSE | 0.11 | 100 | 0.11 | 100 | VOLTTERLEVEL | Yes | Yes | Yes | Yes
1905 | Transformer | TerVoltRated | N/A | Internals | Tertiary Voltage-rated. This field is deprecated. | Float | kV | kV | DPF |  |  | FALSE | 0.11 | 100 | 0.11 | 100 |  | Yes | Yes | Yes | Yes
1906 | Transformer | TerWinding | #N/A | Internals | Tertiary winding type enumeration which is provided in the station internals transformer object if the associaated transformer model field TFMOD_TF is not provided. The enumeration has the following values: 0 = None, 1 = Delta 2 = Grounded_Wye, 3 = Wye, 4 = ZigZag. | String | #N/A | #N/A | DPF |  | 0: None 1: Delta 2: Grounded wye 3: Wye 4: Zigzag | FALSE | #N/A | #N/A | #N/A | #N/A | TFTERTWINDTYPE | Yes | Yes | Yes | Yes
1907 | Transformer | TeTapModel | TETAPMODEL_TF | Internals | Tertiary associated tap changer model name. | String | #N/A | #N/A | DPF, LVM | “” | The tap model name must match a Tap Changer Model given in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | TETAP.TAPMODEL.NAME | Yes | Yes | Yes | Yes
1908 | Transformer | TeVoltSetpointDeadBand | TEVOLTSETPOINTDEADBAND_TF | Internals | Tertiary winding tap changer voltage setpoint deadband (percent). The LVM generated setpoint control will be discarded during the LVM post processing if the tap changer voltage is within the original value plus/minus this deadband value. | Float | percent | percent | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | TETAP.VSETPNTDEADBAND | Yes | Yes | Yes | Yes
1909 | Transformer | TeVoltSetpointRangeMax | TEVOLTSETPOINTRANGEMAX_TF | Internals | Tertiary winding tap changer voltage setpoint maximum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is larger than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | TETAP.VSETPNTRANGEMAX | Yes | Yes | Yes | Yes
1910 | Transformer | TeVoltSetpointRangeMin | TEVOLTSETPOINTRANGEMIN_TF | Internals | Tertiary winding tap changer voltage setpoint minimum value (per unit). The LVM generated setpoint control will be changed to this value if the recommend tap changer voltage is less than this value. | Float | per unit | per unit | DPF, LVM | 0 |  | FALSE | 0 |  | 0 |  | TETAP.VSETPNTRANGEMIN | Yes | Yes | Yes | Yes
1911 | Transformer | TeVreduct | TEVREDUCT_TF | Internals | Tertiary winding tap changer voltage reduction setting. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF | User-configurable through Defaults File |  | FALSE | 0.0/0.0 | 0.10/12.0 | 0.0/0.0 | 0.10/12.0 | TETAP.VREDPU | Yes | Yes | Yes | Yes
1912 | Transformer | TeVregLineLine | TEVREGLINELINE_TF | Internals | Flag that indicates whether the regulated (sensed) phases for the tertiary tap is measured line to line or line to ground (True = line to line). | Boolean | #N/A | #N/A | DPF, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TERTPTVMEASLL | Yes | Yes | Yes | Yes
1913 | Transformer | TeVtarget | TEVTARGET_TF | Internals | Tertiary winding tap changer voltage target. The units (either per unit or voltage) are determined based on a flag set in the transformer model if the associated transformer model field TFMOD_TF has been provided. Otherwise, the units are determined from the field defined in the RegUnits field. | Float | per unit or Volt | per unit or Volt | DPF, LVM |  |  | FALSE | 0.80/96.0 | 1.20/144.0 | 0.80/96.0 | 1.20/144.0 | TETAP.VTARGET | Yes | Yes | Yes | Yes
1914 | Transformer | TfHasTertiaryWinding |  | Internals | TF has tertiary winding? | Boolean | [5 empty] | FALSE: TRUE; No: Yes; No: Yes; No: Yes; No: Yes
1915 | Transformer | TfSize | SIZE_TF | Internals | Transformer or regulator size. This field is only applicable for transformers and regulators defined in the station internals file. Otherwise, the size value is taken from the associated transformer model defined in the global resources file. | Float | kVA or MVA | kVA or MVA | DPF |  |  | FALSE | 0 | #N/A | 0 | #N/A | TFSIZE | Yes | Yes | Yes | Yes
1916 | Transformer | ThirdPartyOwned | THIRDPARTYOWNED_TF | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1917 | Transformer | TimeDelaySchedule | TIMEDELAYSCHEDULE_TF | Internals | Time delay schedule name (optional). To prevent excessive tap movements, an additional time delay isprovided in the LTC/Regulator Control Function for Heuristic Load and Volt/VAR Management (LVM). In the time delay schedule, the minimum voltage difference value (in percent) is specified on the x-axis, and the time delay (in seconds) is specified on the y-axis. The minimum voltage difference value is the smallest voltage difference between a measured voltage and the minimum voltage limit (incorporating the regulation margin - see field below) for any telemetered voltage point downstream of the LTC or regulator. | String | #N/A | #N/A | DPF, LVM |  | The time delay shcedule name must match a schedule defined in the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A | TIMEDELAYSCHEDULE | Yes | Yes | Yes | Yes
1918 | Transformer | ToNode | TONODE_TF | Internals | To node ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | TONODE | Yes | Yes | Yes | Yes
1919 | Transformer | ToStation | TOSUB_TF | Internals | Associated external substation name. This field should only be set if the transformer connects two substations together. | String | #N/A | #N/A | OPS |  | The station name is checked against the stations list read from the global resources file. | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1920 | Transformer | TotalR | #N/A | Internals | Total resistance for two winding transformers, regulators, or zig-zag transformers (%). | Float | percent | percent | OPS |  |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1921 | Transformer | TotalX | #N/A | Internals | Total reactance for two winding transformers, regulators, or zig-zag transformers (%). | Float | percent | percent | OPS |  |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
1922 | Transformer | TransformerModel | TFMOD_TF | Internals | Transformer model name. If set to blank for substation internal equipment, the Converter will inspect and use the individual properties (e.g. size, impedance, losses, amapacity limits). Otherwise, the individual properties in the global resources file will be used. Note, this field property is labeled Associated Transformer Model in the Substation Editor. | String | #N/A | #N/A | DPF, LVM, FISR, SCC |  | The transformer model must be blank or match a transformer model given in the global resources file. | TRUE | #N/A | #N/A | #N/A | #N/A | MODEL.NAME | Yes | Yes | Yes | Yes
1923 | Transformer | TransType | #N/A | Internals | DMS transformer type enumeration which is provided in the station internals transformer object if the associaated transformer model field TFMOD_TF is not provided. The enumeration has the following values: 0 = None, 1 = Distribution, 2 = Regulator, 3 = Power,4 = Auto, 5 = StepUpStepDown, 6 = Zigag | String | #N/A | #N/A | OPS |  | 0: None 1: Distribution 2: Regulator 3: Power 4: Auto 5: Step up/Step down 6: Zigzag | FALSE | #N/A | #N/A | #N/A | #N/A | TFTYPE | Yes | Yes | Yes | Yes
1924 | Transformer | Type | #N/A | Internals | DMS transformer type enumeration that is only specified in the station internals file. | Integer | enumeration | enumeration | OPS |  | 0: Not specified 1: Distribution 2: Regulator 3: Power 4: Auto 5: Step Up/Step Down 6: Zigzag | FALSE | 1 | 6 | 1 | 6 | MODEL.DMSTYPE | Yes | Yes | Yes | Yes
1925 | Transformer | Units | UNITS_TF | Internals | Transformer size units for the station external file. This field is not used in the DMS (the size is taken from the associated transformer model defined in the global resources file). | Integer | enumeration | enumeration | OPS |  | 1: kVA 2: MVA 3: Regulated kVA (for regulators) | FALSE |  |  |  |  | TFMODELUNITS | Yes | Yes | Yes | Yes
1926 | Transformer | VoltRedBWCompensateFlag | VOLTREDBWCOMPENSATEFLAG | Internals | TF has voltage bandwidth reduction compensated? | Boolean | #N/A | #N/A | OPS, LVM |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | VOLTREDBWCOMPENSATEFLAG | Yes | Yes | Yes | No
1927 | Transformer | XGround | XGROUNDPRIME_TF | Internals | Primary grounding reactance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if primary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | PRIMGNDX | Yes | Yes | Yes | Yes
1928 | Transformer | XGroundsec | XGROUNDSEC_TF | Internals | Secondary grounding reactance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if secondary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | SEC1GNDX | Yes | Yes | Yes | Yes
1929 | Transformer | XGroundtert | XGROUNDTERT_TF | Internals | Tertiary grounding reactance (ohms). | Float | ohms | ohms | DPF | User-configurable through Defaults File | Required if tertiary winding is grounded. | FALSE | 0 | 100 | 0 | 100 | SEC2GNDX | Yes | Yes | Yes | Yes
1930 | Transformer | #N/A | NUMGEOM_TF | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1931 | Transformer | #N/A | NUMLABELGEOM_TF | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1932 | Transformer Bank | CompanyName | COMPANYNAME_TFBANK | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1933 | Transformer Bank | County | COUNTY_TFBANK | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1934 | Transformer Bank | CustomField:IsString | CUSTOMFIELDISSTRING_TFBANK |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1935 | Transformer Bank | CustomField:Name | CUSTOMFIELDNAME_TFBANK |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1936 | Transformer Bank | CustomField:Value | CUSTOMFIELDVALUE_TFBANK |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1937 | Transformer Bank | Id | ID_TFBANK | Internals | Transformer bank unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1938 | Transformer Bank | LabelPlacement:FontSize | LABELSIZE_TFBANK | Internals | Label font size . | Integer | count | count | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1939 | Transformer Bank | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_TFBANK | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1940 | Transformer Bank | LabelPlacement:GeometryType | LABELGEOMTYPE_TFBANK | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1941 | Transformer Bank | LabelPlacement:Rotation | LABELROT_TFBANK | Internals | Label rotation angle (degrees). | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1942 | Transformer Bank | LabelPlacement:Text | LABELTEXT_TFBANK | Internals | Label geometry text. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1943 | Transformer Bank | LabelPlacement:X | LABELX_TFBANK | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1944 | Transformer Bank | LabelPlacement:Y | LABELY_TFBANK | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1945 | Transformer Bank | LocationDescription | LOCATIONDESCRIPTION_TFBANK | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1946 | Transformer Bank | Municipality | MUNICIPALITY_TFBANK | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1947 | Transformer Bank | Name | NAME_TFBANK | Internals | Transformer bank display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1948 | Transformer Bank | NOMINAL_FEEDER_ID_TFBANK | NOMINAL_FEEDER_ID_TFBANK | Internals | Nominal feeder ID for the transformer bank. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for transformer banks marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
1949 | Transformer Bank | PermitAreaId | PERMITAREAID_TFBANK | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1950 | Transformer Bank | State | STATE_TFBANK | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1951 | Transformer Bank | SymbolPlacement:GeometryLevel | GEOMLEVEL_TFBANK | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1952 | Transformer Bank | SymbolPlacement:GeometryType | GEOMTYPE_TFBANK | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1953 | Transformer Bank | SymbolPlacement:Rotation | ROTATION_TFBANK | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1954 | Transformer Bank | SymbolPlacement:Size | SIZE_TFBANK | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1955 | Transformer Bank | SymbolPlacement:X | WCX_TFBANK | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X | Yes | Yes | Yes | Yes
1956 | Transformer Bank | SymbolPlacement:X2 | WCX2_TFBANK | Internals | X2 coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | X2 | Yes | No | Yes | No
1957 | Transformer Bank | SymbolPlacement:Y | WCY_TFBANK | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1958 | Transformer Bank | SymbolPlacement:Y2 | WCY2_TFBANK | Internals | Y2 coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | Y2 | Yes | No | Yes | No
1959 | Transformer Bank | TfIds | TFIDS_TFBANK | Internals | Collection of transformer IDs. | String | #N/A | #N/A | DPF |  | Each transformer must exist in the file. | TRUE | #N/A | #N/A | #N/A | #N/A | TFINBANK | Yes | Yes | Yes | Yes
1960 | Transformer Bank | ThirdPartyOwned | THIRDPARTYOWNED_TFBANK | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
1961 | Transformer Bank | #N/A | NUMBANK_TFBANK | Externals | The number of transformers in the bank. | Integer | count | count | DPF |  |  | FALSE | 2 | 9 | 2 | 9 | NUMTF | Yes | Yes | Yes | Yes
1962 | Transformer Bank | #N/A | NUMGEOM_TFBANK | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1963 | Transformer Bank | #N/A | NUMLABELGEOM_TFBANK | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
1964 | UI Container | CompanyName | COMPANYNAME_UICNTER | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
1965 | UI Container | County | COUNTY_UICNTER | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
1966 | UI Container | CustomField:IsString | CUSTOMFIELDISSTRING_UICNTER |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1967 | UI Container | CustomField:Name | CUSTOMFIELDNAME_UICNTER |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1968 | UI Container | CustomField:Value | CUSTOMFIELDVALUE_UICNTER |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1969 | UI Container | Id | ID_UICNTER | Internals | UI Container unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
1970 | UI Container | LabelPlacement:CharacterRotation | LABELCHRROTATION__UICNTER | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
1971 | UI Container | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_UICNTER | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
1972 | UI Container | LabelPlacement:FontSize | LABELSIZE_UICNTER | Internals | Label font size. | Integer | count | count | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
1973 | UI Container | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_UICNTER | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1974 | UI Container | LabelPlacement:GeometryType | LABELGEOMTYPE_UICNTER | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
1975 | UI Container | LabelPlacement:Rotation | LABELROT_UICNTER | Internals | Label rotation angle (degrees). | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
1976 | UI Container | LabelPlacement:Text | LABELTEXT_UICNTER | Internals | Label geometry text. The label geometry text will override the text provided in the Name field when labels are turned on it the graphical user interface. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
1977 | UI Container | LabelPlacement:X | LABELX_UICNTER | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
1978 | UI Container | LabelPlacement:Y | LABELY_UICNTER | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
1979 | UI Container | LocationDescription | LOCATIONDESCRIPTION_UICNTER | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
1980 | UI Container | Municipality | MUNICIPALITY_UICNTER | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
1981 | UI Container | Name | NAME_UICNTER | Internals | UI Container display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
1982 | UI Container | Objects:ID | OBJECTn_UICNTER | Internals | Collection of objects IDs in the UI Container. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | VLTOBJ.ID | Yes | Yes | Yes | Yes
1983 | UI Container | Objects:Ivalue | FUNCTIONTYPEn_UICNTER | Internals | Collection of object functions (enumeration) in the UI Container (deprecated). | Integer | enumeration | enumeration | OPS |  | UI_Recloser = 1, UI_BypSwitch = 2, UI_AutoSwitch = 3, UI_IsolSwitch = 4, UI_Transformer 5, UI_VacIntSwitch 6, UI_Switch = 7, UI_Fuse = 8, UI_Bus = 9, UI_VacSwitch = 10, UI_Fault_Ind = 11, UI_Sect = 12, UI_Jumper = 13, UI_Throwover = 14, UI_Multi_Sw = 15 | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
1984 | UI Container | Objects:Type | OBJECTTYPEn_UICNTER | Internals | The type of objects in the UI Container (such as SWITCH, FUSE, BREAKER, or others). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | VLTOBJ.TYPE | Yes | Yes | Yes | Yes
1985 | UI Container | PermitAreaId | PERMITAREAID_UICNTER | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
1986 | UI Container | State | STATE_UICNTER | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
1987 | UI Container | SymbolPlacement:GeometryLevel | GEOMLEVEL_UICNTER | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1988 | UI Container | SymbolPlacement:GeometryType | GEOMTYPE_UICNTER | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PLACEMNT.GEOMETRY | Yes | Yes | Yes | Yes
1989 | UI Container | SymbolPlacement:IsPoint | ISPOINT_UICNTER | Internals | Flag indicating it is a point placement. | Boolean | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
1990 | UI Container | SymbolPlacement:Rotation | ROTATION_UICNTER | Internals | Rotation Angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.ROTATION | Yes | Yes | Yes | Yes
1991 | UI Container | SymbolPlacement:Size | SIZE_UICNTER | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.SIZE | Yes | Yes | Yes | Yes
1992 | UI Container | SymbolPlacement:Vertex:X | WCXn_UICNTER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX | Yes | Yes | Yes | Yes
1993 | UI Container | SymbolPlacement:Vertex:X2 | WCX2n_UICNTER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX2 | Yes | No | Yes | No
1994 | UI Container | SymbolPlacement:Vertex:Y | WCYn_UICNTER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY | Yes | Yes | Yes | Yes
1995 | UI Container | SymbolPlacement:Vertex:Y2 | WCY2n_UICNTER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY2 | Yes | No | Yes | No
1996 | UI Container | SymbolPlacement:X | WCX_UICNTER | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X | Yes | Yes | Yes | Yes
1997 | UI Container | SymbolPlacement:X2 | WCX2_UICNTER | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X2 | Yes | No | Yes | No
1998 | UI Container | SymbolPlacement:Y | WCY_UICNTER | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y | Yes | Yes | Yes | Yes
1999 | UI Container | SymbolPlacement:Y2 | WCY2_UICNTER | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y2 | Yes | No | Yes | No
2000 | UI Container | ThirdPartyOwned | THIRDPARTYOWNED_UICNTER | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
2001 | UI Container | Type | TYPE_UICNTER | Internals | UI Container type enumeration (0 - UI_No_Uincnter, 1 - UI_OCR_Bypass, 2 - UI_OH_Auto, 3 - UI_Reg_Bypass, 4 - UI_VacInt_Bypass, 5 - UI_SwCab_Sw, 6 - UI_CompSw_Throwover, 7 - UI_Elbow_Group, 8 - UI_Fuse_Group, 9 - UI_Recloser_Group, 10 - UI_Sect_Group, 11 - UI_Jumper_Group, 12 - UI_Tf_Group, 13 - UI_Comp_Sw) | Integer | #N/A | #N/A | OPS |  | Recloser with Bypass = 1, Automated Switch = 2, Regulator with Bypass = 3, Vacuum Interrupter with Bypass = 4, Switch Cabinet = 5, Composite Switch - Throwover = 6, Elbow Switch Group = 7, Fuse Group = 8, Recloser Group = 9, Sectionalizer Group = 10, Permanent Jumper Group = 11, Transformer Group = 12, Composite Switch = 13 | FALSE | #N/A | #N/A | #N/A | #N/A | ENUMTYPE | Yes | Yes | Yes | Yes
2002 | UI Container | #N/A | NUMOBJECT_UICNTER | Externals | The number of objects in the UI Container. | Integer | count | count | OPS |  |  | FALSE | 1 | 100 | 1 | 100 | NUMOBJ | Yes | Yes | Yes | Yes
2003 | UI Container | #N/A | NUMGEOM_UICNTER | Externals | Number of geometries. | Integer | count | count | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
2004 | UI Container | #N/A | NUMVERT_UICNTER | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | PLACEMNT.NUMVERT | Yes | Yes | Yes | Yes
2005 | UI Container | #N/A | NUMLABELGEOM_UICNTER | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
2006 | Value Placement | AnchorPoint |  | Internals | Enumeration of the value placement anchor point: 0 = TopLeft 1 = TopRight 2 = BottomLeft 3 = BottomRight 4 = CenterTop 5 = CenterBottom 6 = CenterLeft 7 = CenterRight | Enumeration | [5 empty] | FALSE |  |  |  |  | ANCHORPOINT | Yes | Yes | Yes | Yes
2007 | Value Placement | ArrowRotation | ARROWROTATION_VLEPLE | Internals | Arrow rotation angle. | Integer | #N/A | #N/A |  |  | In degrees. Counterclockwise from x-axis. | FALSE | #N/A | #N/A | #N/A | #N/A | ARROWROTATION | Yes | Yes | Yes | Yes
2008 | Value Placement | ArrowRotationCalculated | ARROWLABELCALCULATED_VLEPLE | Internals | Indicates whether the initial arrow angle is calculated by the Converter (True = calculated by Converter). | Boolean | #N/A | #N/A |  |  | True of False | FALSE | #N/A | #N/A | #N/A | #N/A | ARROWLABELCALCULATED | Yes | Yes | Yes | Yes
2009 | Value Placement | ColorIndex1 | COLORIDX1_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX1 | Yes | Yes | Yes | Yes
2010 | Value Placement | ColorIndex2 | COLORIDX2_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX2 | Yes | Yes | Yes | Yes
2011 | Value Placement | ColorIndex3 | COLORIDX3_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX3 | Yes | Yes | Yes | Yes
2012 | Value Placement | ColorIndex4 | COLORIDX4_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX4 | Yes | Yes | Yes | Yes
2013 | Value Placement | ColorIndex5 | COLORIDX5_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX5 | Yes | Yes | Yes | Yes
2014 | Value Placement | ColorIndex6 | COLORIDX6_VLEPLE | Internals | Indicates the color for the label and arrow. | Integer | #N/A | #N/A |  |  | Feeder color index as listed on the Lines tab in the Viewer Configuration Editor | FALSE | 1 | 24 | 1 | 24 | COLORIDX6 | Yes | Yes | Yes | Yes
2015 | Value Placement | ComponentType | CMPONENTTYPE_VLEPLE | Internals | The type of the linked DNOM object for the value placement. | String | #N/A | #N/A |  |  | For non-SCADA devices (e.g., switches, lines, and transformers). For SCADA devices use “NotUsed” | TRUE | #N/A | #N/A | #N/A | #N/A | CMPONENTTYPE | Yes | Yes | Yes | Yes
2016 | Value Placement | ConnectionPointX | CONNPOINTX_VLEPLE | Internals | Value placement connection point X coordinate. | Float | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNPOINTX | Yes | Yes | Yes | Yes
2017 | Value Placement | ConnectionPointY | CONNPOINTY_VLEPLE | Internals | Value placement connection point Y coordinate. | Float | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNPOINTY | Yes | Yes | Yes | Yes
2018 | Value Placement | CustomField:IsString | CUSTOMFIELDISSTRING_VLEPLE |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2019 | Value Placement | CustomField:Name | CUSTOMFIELDNAME_VLEPLE |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2020 | Value Placement | CustomField:Value | CUSTOMFIELDVALUE_VLEPLE |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2021 | Value Placement | DnomID | DNOMID_VLEPLE | Internals | The ID of the linked DNOM object for the value placement. | String | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | DNOMID | Yes | Yes | Yes | Yes
2022 | Value Placement | GeometryLevel |  | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2023 | Value Placement | GeometryType | GEOMETRYTYPE_VLEPLE | Internals | Geographic geometry name. | String | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
2024 | Value Placement | Id | ID_VLEPLE | Internals | Value placement uique ID. | String | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
2025 | Value Placement | MeasLabel1 | MEASLABEL1_VLEPLE | Internals | The label/text to show next to the measurement value 1. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL1 | Yes | Yes | Yes | Yes
2026 | Value Placement | MeasLabel2 | MEASLABEL2_VLEPLE | Internals | The label/text to show next to the measurement value 2. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL2 | Yes | Yes | Yes | Yes
2027 | Value Placement | MeasLabel3 | MEASLABEL3_VLEPLE | Internals | The label/text to show next to the measurement value 3. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL3 | Yes | Yes | Yes | Yes
2028 | Value Placement | MeasLabel4 | MEASLABEL4_VLEPLE | Internals | The label/text to show next to the measurement value 4. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL4 | Yes | Yes | Yes | Yes
2029 | Value Placement | MeasLabel5 | MEASLABEL5_VLEPLE | Internals | The label/text to show next to the measurement value 5. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL5 | Yes | Yes | Yes | Yes
2030 | Value Placement | MeasLabel6 | MEASLABEL6_VLEPLE | Internals | The label/text to show next to the measurement value 6. | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MEASLABEL6 | Yes | Yes | Yes | Yes
2031 | Value Placement | MeasType1 | MEASTYPE1_VLEPLE | Internals | Measurement type 1 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE1 | Yes | Yes | Yes | Yes
2032 | Value Placement | MeasType2 | MEASTYPE2_VLEPLE | Internals | Measurement type 2 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE2 | Yes | Yes | Yes | Yes
2033 | Value Placement | MeasType3 | MEASTYPE3_VLEPLE | Internals | Measurement type 4 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE3 | Yes | Yes | Yes | Yes
2034 | Value Placement | MeasType4 | MEASTYPE4_VLEPLE | Internals | Measurement type 4 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE4 | Yes | Yes | Yes | Yes
2035 | Value Placement | MeasType5 | MEASTYPE5_VLEPLE | Internals | Measurement type 5 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE5 | Yes | Yes | Yes | Yes
2036 | Value Placement | MeasType6 | MEASTYPE6_VLEPLE | Internals | Measurement type 5 associated with the value placement. | String | #N/A | #N/A |  |  | kVLL, kVLG, kW, kVAR, kVA, AmpA, AmpB, AmpC, Amp3, MW, MVAR, Val_MVA , V, Tap_Pos, VA, VB, or VC | FALSE | #N/A | #N/A | #N/A | #N/A | MEASTYPE6 | Yes | Yes | Yes | Yes
2037 | Value Placement | Name | NAME_VLEPLE | Internals | Value placement display name. | String | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | Name | Yes | Yes | Yes | Yes
2038 | Value Placement | PermitAreaId | PERMITAREAID_VLEPLE | Internals | Permission area ID (8-character maximum). | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PAREANME | Yes | Yes | Yes | Yes
2039 | Value Placement | ShowArrow1 | MEASSHOWARROW1_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True or False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW1 | Yes | Yes | Yes | Yes
2040 | Value Placement | ShowArrow2 | MEASSHOWARROW2_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True or False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW2 | Yes | Yes | Yes | Yes
2041 | Value Placement | ShowArrow3 | MEASSHOWARROW3_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True of False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW3 | Yes | Yes | Yes | Yes
2042 | Value Placement | ShowArrow4 | MEASSHOWARROW4_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True of False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW4 | Yes | Yes | Yes | Yes
2043 | Value Placement | ShowArrow5 | MEASSHOWARROW5_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True of False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW5 | Yes | Yes | Yes | Yes
2044 | Value Placement | ShowArrow6 | MEASSHOWARROW6_VLEPLE | Internals | Indicates whether to show the arrow or not (True = show arrow). | Boolean | #N/A | #N/A |  |  | True or False | FALSE | #N/A | #N/A | #N/A | #N/A | MEASSHOWARROW6 | Yes | Yes | Yes | Yes
2045 | Value Placement | TextRotation | LABELROTATION_VLEPLE | Internals | Text angle (degrees). | Integer | #N/A | #N/A |  |  | In degrees. Counterclockwise from x-axis. | TRUE | #N/A | #N/A | #N/A | #N/A | LABELROTATION | Yes | Yes | Yes | Yes
2046 | Value Placement | TextRotationCalculated | LABELROTCALCULATED_VLEPLE | Internals | Indicates whether the initial text angle is calculated by the Converter (True = calculated by Converter). | Boolean | #N/A | #N/A |  |  | True of False | TRUE | #N/A | #N/A | #N/A | #N/A | LABELROTCALCULATED | Yes | Yes | Yes | Yes
2047 | Value Placement | ValuePlacementType |  | Internals | Value placement type | String | [5 empty] | TRUE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
2048 | Value Placement | X | X_VLEPLE | Internals | Value placement X coordinate. | Float | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | XVLPLACE | Yes | Yes | Yes | Yes
2049 | Value Placement | Y | Y_VLEPLE | Internals | Value placement Y coordinate. | Float | #N/A | #N/A |  |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | YVLPLACE | Yes | Yes | Yes | Yes
2050 | Vault | Address | ADDRESS_VAULT | Internals | Non-electrical device address. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ADDRESS.NOAPPSTRING | Yes | Yes | Yes | Yes
2051 | Vault | AlternateName | ALTNAME_VAULT | Internals | Alternate name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ALTERNATENAME | Yes | Yes | Yes | Yes
2052 | Vault | CompanyName | COMPANYNAME_VAULT | Internals | Name of the company that is associated with the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | EXTCOMPANY, COMPANYNAME | Yes | No | No | No
2053 | Vault | County | COUNTY_VAULT | Internals | The name of the associated county | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | COUNTY | No | No | No | No
2054 | Vault | CustomField:IsString | CUSTOMFIELDISSTRING_VAULT |  | Determines if CustomField is String or not | Boolean | #N/A | #N/A |  | TRUE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2055 | Vault | CustomField:Name | CUSTOMFIELDNAME_VAULT |  | Custom Field Name | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2056 | Vault | CustomField:Value | CUSTOMFIELDVALUE_VAULT |  | Custom Field Value | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2057 | Vault | ExternalId | EXTERNALID_VAULT | Internals | External Id of VAULT.This information currently is not used by DMS Application. It is provided to be used by any other application that might uses the source data. | String | #N/A | #N/A | OPS |  |  | Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
2058 | Vault | Id | ID_VAULT | Internals | Vault unique ID. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID | Yes | Yes | Yes | Yes
2059 | Vault | LabelPlacement:CharacterRotation | LABELCHRROTATION_VAULT | Internals | Label geometry text character rotation. The label geometry text rotation of each character within the string. | Integer | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CHRROTATION | Yes | Yes | Yes | Yes
2060 | Vault | LabelPlacement:ConnectionPoint | LABELCONNECTIONPOINT_VAULT | Internals | Connection Point enumeration, allowed values: Default,NW,N,NE,W,CENTER,E,SW,S and SE | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONNECTIONPOINT | Yes | Yes | Yes | Yes
2061 | Vault | LabelPlacement:FontSize | LABELSIZE_VAULT | Internals | Label font size. | Integer | points | points | OPS |  |  | FALSE |  |  |  |  | SIZE | Yes | Yes | Yes | Yes
2062 | Vault | LabelPlacement:GeometryLevel | LABELGEOMLEVEL_VAULT | Internals | Label geometry level. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2063 | Vault | LabelPlacement:GeometryType | LABELGEOMTYPE_VAULT | Internals | Label geometry type. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | GEOMETRY | Yes | Yes | Yes | Yes
2064 | Vault | LabelPlacement:Rotation | LABELROT_VAULT | Internals | Label rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | FALSE |  |  |  |  | ROTATION | Yes | Yes | Yes | Yes
2065 | Vault | LabelPlacement:Text | LABELTEXT_VAULT | Internals | Label geometry text. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEXT | Yes | Yes | Yes | Yes
2066 | Vault | LabelPlacement:X | LABELX_VAULT | Internals | Label X coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | X | Yes | Yes | Yes | Yes
2067 | Vault | LabelPlacement:Y | LABELY_VAULT | Internals | Label Y coordinate. | Float | #N/A | #N/A | OPS |  |  | FALSE |  |  |  |  | Y | Yes | Yes | Yes | Yes
2068 | Vault | LocationDescription | LOCATIONDESCRIPTION_VAULT | Internals | Information about the device location (for example, pole number or street number) | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOCATIONDESCRIPTION | No | No | No | No
2069 | Vault | Municipality | MUNICIPALITY_VAULT | Internals | The name of the associated municipality | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | MUNICIPALITY | No | No | No | No
2070 | Vault | Name | NAME_VAULT | Internals | Vault display name. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME | Yes | Yes | Yes | Yes
2071 | Vault | NOMINAL_FEEDER_ID_VAULT | NOMINAL_FEEDER_ID_VAULT | Internals | Nominal feeder ID for the vault. This field is usually an information only field that is used for Converter logging purposes, but it is optionally applied by the Converter for setting the nominal feeder for breakers marked as future construction. | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | FEEDERID | Yes | Yes | Yes | Yes
2072 | Vault | Objects:ID | OBJECTn_VAULT | Internals | Collection of object IDs in the vault. | String | #N/A | #N/A | OPS |  | Each object must be found in the file. Required if objects are defined. | FALSE | #N/A | #N/A | #N/A | #N/A | VLTOBJ.ID | Yes | Yes | Yes | Yes
2073 | Vault | Objects:Ivalue | #N/A | Internals | Collection of object functions (enumeration) in the Vault. | Integer | enumeration | enumeration | OPS |  |  | FALSE: FALSE; Yes: Yes; Yes: Yes; Yes: Yes; Yes: Yes
2074 | Vault | Objects:Type | OBJECTTYPEn_VAULT | Internals | The type of objects in the vault (such as SWITCH, FUSE, BREAKER, or others). | String | #N/A | #N/A | OPS |  | The object type must be defined in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | VLTOBJ.TYPE | Yes | Yes | Yes | Yes
2075 | Vault | PermitAreaId | PERMITAREAID_VAULT | Internals | Permission area ID (8-character maximum) | String | #N/A | #N/A | OPS |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | PERMITAREAID | Yes | Yes | Yes | Yes
2076 | Vault | Refdwg | REFDWG_VAULT | Internals | Associated reference drawing. | String | #N/A | #N/A | OPS | “” |  | FALSE | #N/A | #N/A | #N/A | #N/A | REFDRAW | Yes | Yes | Yes | Yes
2077 | Vault | ScadaCompositeID |  | Internals | Composite Id of device in SCADA. Used to auto-match SCADA mapping | String | #N/A | #N/A |  | FALSE |  | FALSE | #N/A | #N/A | #N/A | #N/A |  | Yes | No | No | No
2078 | Vault | State | STATE_VAULT | Internals | The name of the associated state | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | STATE | No | No | No | No
2079 | Vault | SymbolPlacement:GeometryLevel | GEOMLEVEL_VAULT | Internals | Geometry level. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2080 | Vault | SymbolPlacement:GeometryType | GEOMTYPE_VAULT | Internals | Geometry type. | String | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PLACEMNT.GEOMETRY | Yes | Yes | Yes | Yes
2081 | Vault | SymbolPlacement:IsPoint | ISPOINT_VAULT | Internals | Flag indicating it is a point placement (True = point). | Boolean | #N/A | #N/A | OPS |  |  | TRUE | #N/A | #N/A | #N/A | #N/A |  | Yes | Yes | Yes | Yes
2082 | Vault | SymbolPlacement:Rotation | ROTATION_VAULT | Internals | Rotation angle (degrees). | Integer | degrees | degrees | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.ROTATION | Yes | Yes | Yes | Yes
2083 | Vault | SymbolPlacement:Size | SIZE_VAULT | Internals | Size. | Integer | points | points | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.SIZE | Yes | Yes | Yes | Yes
2084 | Vault | SymbolPlacement:Vertex:X | WCXn_VAULT | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX | Yes | Yes | Yes | Yes
2085 | Vault | SymbolPlacement:Vertex:X2 | WCX2n_VAULT | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AX2 | Yes | No | Yes | No
2086 | Vault | SymbolPlacement:Vertex:Y | WCYn_VAULT | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY | Yes | Yes | Yes | Yes
2087 | Vault | SymbolPlacement:Vertex:Y2 | WCY2n_VAULT | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.AY2 | Yes | No | Yes | No
2088 | Vault | SymbolPlacement:X | WCX_VAULT | Internals | X coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X | Yes | Yes | Yes | Yes
2089 | Vault | SymbolPlacement:X2 | WCX2_VAULT | Internals | X2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.X2 | Yes | No | Yes | No
2090 | Vault | SymbolPlacement:Y | WCY_VAULT | Internals | Y coordinate. | Float | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y | Yes | Yes | Yes | Yes
2091 | Vault | SymbolPlacement:Y2 | WCY2_VAULT | Internals | Y2 coordinate. | Double | #N/A | #N/A | OPS |  |  | TRUE |  |  |  |  | PLACEMNT.Y2 | Yes | No | Yes | No
2092 | Vault | Telemetered | TELEMETERED_VAULT | Internals | If not defined, the default value is false, meaning the device is not telemetered in SCADA. This information currently is not used by DMS application. It is provided to be used by any other application that might uses the source data. | Boolean | #N/A | #N/A | OPS | FALSE |  | FALSE: FALSE; No: Yes; No: Yes; No: Yes; No: Yes
2093 | Vault | ThirdPartyOwned | THIRDPARTYOWNED_VAULT | Internals | Specifies whether a third-party company owns the component | String | #N/A | #N/A |  |  |  | FALSE | #N/A | #N/A | #N/A | #N/A | ISTHIRDPARTY | Yes | No | No | No
2094 | Vault | Type | TYPE_VAULT | Internals | User defined vault type enumeration defined in the global reosurces file. | String | #N/A | #N/A | OPS |  | Please refer to global.csv file | FALSE | #N/A | #N/A | #N/A | #N/A | VAULTTYPE | Yes | Yes | Yes | Yes
2095 | Vault | #N/A | NUMOBJECT_VAULT | Externals | The number of objects in the vault. | Integer | count | count | OPS |  |  | FALSE | 1 | 100 | 1 | 100 | NUMOBJ | Yes | Yes | Yes | Yes
2096 | Vault | #N/A | NUMGEOM_VAULT | Externals | Number of geometries. | Integer | #N/A | #N/A | OPS |  |  | TRUE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
2097 | Vault | #N/A | NUMVERT_VAULT | Externals | Number of vertices. | Integer | count | count | OPS |  |  | TRUE | 0 | 100 | 0 | 100 | PLACEMNT.NUMVERT | Yes | Yes | Yes | Yes
2098 | Vault | #N/A | NUMLABELGEOM_VAULT | Externals | Number of label geometries. | Integer | count | count | OPS |  |  | FALSE | 0 | 50 | 0 | 50 |  | Yes | Yes | Yes | Yes
Note on M35: Paul Kuntz: Is this field required if the ground trip capability flag is set to false?
Note on M37: Paul Kuntz: This field is very tricky since different fields are required depending on the Converter validation scope. For example, the Breaker Maximum Interruption rating is not required for the Operations Scope but it is required for the DPF Scope. There are also several sets of fields where one field in the "group" must be set but the others are then not filled in.
Note on F58: Paul Kuntz: What about a parallel vs. a loop? The same for the other NormalyLooped parameters.
Note on J58: Paul Kuntz: We only support OPS (operations including NTP/tracing) and DPF (network applications).
Note on M91: Paul Kuntz: Technically, no placement information is required but these are needed for graphically displaying the devices.
Note on C409: Paul Kuntz: Where did this field come from?
Note on F873: Paul Kuntz: Is this functionality supported?
Note on F927: Paul Kuntz: This is not very clear.
Note on F1150: Paul Kuntz: IS this field going to be retained?
Note on F1393: Paul Kuntz: Same as above comment.
Note on F1394: Paul Kuntz: Time cannot be entered in this field (single on/off)?
Note on F1397: Paul Kuntz Confirm the last sentence. What is the difference between the two values?
Note on F1430: Paul Kuntz: Confirm with SBP.
Note on F1431: Paul Kuntz: We already have a VregLineLine field so what do theses two fields do?
Note on F1539: Paul Kuntz: What if SSE is not used for the modeling of the station internals)?
Note on L1693: Paul Kuntz: This shpould be converted to a user definable enumeration (enums table in global.csv file).
Note on F1769: Paul Kuntz: It appears that this field is no longer used (nominal and rated voltage code has been cleaned up in the newer SSE code).
Note on F1852: Paul Kuntz: It appears that this field is no longer used (nominal and rated voltage code has been cleaned up in the newer SSE code).
Note on F1906: Paul Kuntz: It appears that this field is no longer used (nominal and rated voltage code has been cleaned up in the newer SSE code).
Note on B2032: Paul Kuntz: Why wasn't this implemented using repeating fields?

## Measurement Types
Measurement Type | Valid Measurement Group | Enumeration GE use only values may change | Source | Comment if Deprecated | Detailed Device Type(s) | Associated Node(s) | SWO Function | DNAF Application | DNAF Group Type | DMS Usage | Valid Phases | SDIS=0 meaning | SDIS=1 meaning
AbnormalEnergized | Status | 202 | DMS |  | Line, Jumper | At any node | Not supported | -- | -- | The NTP application determines abnormal energization for branch (two terminal) devices. This flag is sent from the DMS to SCADA for determining if the abnormal energization halo is drawn in the SCADA one-line display. | A, B, C, N,ABC | Open | Closed
ActiveSettingGroup | Analog | 198 | SCADA |  | Recloser |  | Not supported | Reconfig | Protection Group | Active settings group
ActiveSettingsGroupTemplate | Analog | 197 | SCADA |  | Recloser |  | Not supported | Reconfig | Protection Group | Active settings group template
AmpAOutput |  | 214 | Deprecated | Obsolete |  |  |  | -- | --
AmpBOutput |  | 215 | Deprecated | Obsolete |  |  |  | -- | --
AmpCOutput |  | 216 | Deprecated | Obsolete |  |  |  | -- | --
AmpMeasurementType |  | 1 | Deprecated | Obsolete |  |  |  | -- | --
AmpNOutput |  | 217 | Deprecated | Obsolete |  |  |  | -- | --
AmpsOutput | Analog | 213 | DMS |  | Feeder, power transformer, station | At the device object. | Not supported | -- | -- | The DPF application calculates the current flows (in Amps) on feeder, power transformer (high side), and substation. This analog is sent from the DMS to SCADA to display the value in a SCADA one-line diagram. | ABC
AnalogActiveInverterFixedPowerFactorcurve | Analog | 106 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active fixed power factor curve.
AnalogActiveInverterFrequencyWattCurve | Analog | 151 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | This measurement indicates the active Frequency-Watt curve when the Frequency-Watt mode is active (determined by measurement type StatusInverterActiveModeFrequencyWatt). The SCADA analog value for each Frequency-Watt curve is defined in the static model.
AnalogActiveInverterHFRTcurve | Analog | 195 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active HFRT curve
AnalogActiveInverterHVRTcurve | Analog | 191 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active HVRT curve
AnalogActiveInverterLFRTcurve | Analog | 193 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active LFRT curve
AnalogActiveInverterLVRTcurve | Analog | 186 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active LVRT curve.
AnalogActiveInverterMaxPowerLimitingcurve | Analog | 115 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active max power limiting curve.
AnalogActiveInverterVVcurve | Analog | 180 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active Volt-VAR curve
AnalogActiveInverterVWcurve | Analog | 184 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active Volt-Watt curve.
AnalogActiveInverterWPFcurve | Analog | 182 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Index of active Watt-PF curve.
AnalogActiveRegulationMode | Analog | 164 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | The active regulation mode for telemetered regulators which has advanced regulation ability. The SCADA value must match the index value given in the Regulation Mode record in the REgulationControl.csv file. | A,B,C,ABC
AnalogDeltaVoltage | Analog | 149 | SCADA | Future | Capacitor | At single node | Not supported | LVM | Capacitor | The delta voltage value is the change in the measured voltage when a capacitor is opened or closed. This value is calculated by the capacitor field controller over several open or close operations. This value is compared to the Heuristic LVM calculated delta voltage value. Large discrepancies between the measured and calculated values are logged and also displayed in the System Activity Log. | A,B,C,N, ABC
AnalogLowerVoltageLimit | Analog | 173 | DMS |  | Capacitor |  | Not supported | DPF | Capacitor | Lower voltage limit | A,B,C,ABC
AnalogReverseFlowMVA | Analog | 147 | SCADA |  | Line, Transformer, Series_Reactor, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This analog is for VA flow in the reverse (off-nominal direction. | A,B,C,N,ABC
AnalogReverseFlowMVAR | Analog | 146 | SCADA |  | Line, Transformer, Series_Reactor, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This analog is for VAR flow in the reverse (off-nominal) direction. | A,B,C,N,ABC
AnalogReverseFlowMW | Analog | 145 | SCADA |  | Line, Transformer, Series_Reactor, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This analog is for Watt flow in the reverse (off-nominal direction. | A,B,C,N,ABC
AnalogUpperVoltageLimit | Analog | 172 | DMS |  | Capacitor |  | Not supported | DPF | Capacitor | Upper voltage limit | A,B,C,ABC
AnalogVoltReductionValue | Analog | 168 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | Indicates the percentage voltage reduction for the tap changer controller. This is the percent voltage that the voltage setpoint will be set to. | A,B,C,ABC
AreaWattLoad | Analog | 66 | SCADA | Future | Substations in the same Division | n/a | Not supported | -- | -- | The LVM application uses this measurement to indicate the area (division) real power (MW) load. Based on the current MW load, a pre-defined schedule Not yet supported. | ABC
ArmDisarmComplete | Status | 104 | SCADA |  | Breaker | At any node |  | Reconfig | Eligibility | Status indicate device arm/disarm action is complete. |  | Incomplete | Complete
AutoRecloseEnabled |  | 111 | Deprecated | Obsolete. Use DeviceReclosingEnabled instead |  |  |  | -- | --
AVRStatus |  | 30 | Deprecated | Not used |  |  |  | -- | --
CalcAvgVoltOutput | Analog | 268 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Calculated average voltage of the regulated bus. | ABC
CalcSecVarOutput | Analog | 277 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Calculated three-phase aggregated reactive power at the secondary side of station transformers | ABC
CalcSecWOutput | Analog | 279 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Calculated three-phase aggregated real power at the secondary side of station transformers | ABC
CapControlFailed | Status | 107 | SCADA |  | Capacitor | At single node | Not supported | LVM | Eligibility | LVM application removes this capacitor from further analysis (if FAILED or PENDING), until reset by the SCADA operator | A,B,C,N,ABC matching CapStatus | MeasDnomMultiState = true SDIS = 0 - NOT FAILED SDIS = 1 - FAILED XDIS = 0 - NOT PENDING XDIS = 1 - PENDING
CapEnableAndAuto |  | 106 | Deprecated | Obsolete |  |  |  | -- | --
CapMeasurementType | Analog | 7 | SCADA |  | Capacitor |  | Not supported | DPF | Capacitor | This measurement returns the current capacitor step for multiple-state capacitors.
CapOpenAndAvailable | Status | 105 | SCADA | Use CapStatus and DeviceSupervisoryCutout instead | Capacitor |  | Not supported | LVM | Eligibility | Capacitor Open and Available status. |  | MeasDnomMultiState = true SDIS = 0 - OPEN SDIS = 1 - CLOSED XDIS = 0 - AVAILABLE XDIS = 1 - UNAVAILABLE
CapStatus | Status | 14 | SCADA |  | Capacitor | At single node | Status | DPF | Capacitor | Used by RT, ST, and SIM: This measurement stores the network-connectivity status of the capacitor. It may be used for single-phase switches or a three-phase switch, regardless of whether the switch(es) are separate from or integral to the capacitor. | A,B,C,N,ABC | Off Open | On Closed
ConnectedPhase | Analog | 189 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Connected phase
ConnectionStatus | Status | 13 | SCADA |  | Generator, Energy Resource |  | Not supported | DPF | Generator | Generator/energy resource connection status (connected or disconnected from the network).
ControlAvailable | Status | 100 | SCADA |  | Capacitor, Switch, Tap Changing Transformer |  | Not supported | LVM, Reconfig | Eligibility | Control Available status. |  | Not Available | Available
CtlActiveInverterVVcurveOutput | Ctrl | 206 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter Volt-VAR curve output
CtlSetPctVarMaxOutput | Ctrl | 205 | DMS |  | Inverter |  | Not supported | LVM | Inverter | VAR setpoint maximum output
CtrlActiveInverterHFRTcurveOutput | Ctrl | 224 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter HFRT curve output
CtrlActiveInverterHVRTcurveOutput | Ctrl | 220 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter HVRT curve output
CtrlActiveInverterLFRTcurveOutput | Ctrl | 222 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter LFRT curve output
CtrlActiveInverterLVRTcurveOutput | Ctrl | 215 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter LVRT curve output
CtrlActiveInverterVWcurveOutput | Ctrl | 210 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter Volt-Watt curve output
CtrlActiveInverterWPFcurveOutput | Ctrl | 208 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Active inverter Watt-PF curve output
CtrlAutoRecloseEnabled |  | 127 | Deprecated | Obsolete. Use DeviceReclosingEnabled instead |  |  |  | -- | --
CtrlCapStatusCheckOutput |  | 237 | Deprecated | Obsolete |  |  |  | -- | --
CtrlCapStatusOffOutput | Ctrl | 236 | DMS |  | Capacitor | At single node | Not supported | LVM | Capacitor | Control issued by LVM application to turn off a Remotely controlled capacitor | A,B,C,ABC
CtrlCapStatusOnOutput | Ctrl | 235 | DMS |  | Capacitor | At single node | Not supported | LVM | Capacitor | Control issued by LVM application to turn on a Remotely controlled capacitor | A,B,C,ABC
CtrlConnectedPhaseOutput | Ctrl | 218 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Connected phase
CtrlDADisabled | Ctrl | 253 | DMS |  | Switch |  | Not supported | Reconfig | Eligibility | Optimization control disanabled status. This measurement is used for switching devices in FISR/AFR.
CtrlDAEnabled | Ctrl | 252 | DMS |  | Switch |  | Not supported | Reconfig | Eligibility | Optimization control enabled status. This measurement is used for switching devices in FISR/AFR.
CtrlDerStatusConnectOutput | Status | 227 | DMS |  | Energy Resource |  | Not supported | LVM | Generator | Control issued from DMS to change an energy resource connection status to Connected.
CtrlDerStatusDisconnectOutput | Status | 228 | DMS |  | Energy Resource |  | Not supported | LVM | Generator | Control issued from DMS to change an energy resource connection status to Disconnected.
CtrlDeviceReclosingDisableOutput | Ctrl | 293 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Sets the DeviceReclosingEnabled status to Disabled
CtrlDeviceReclosingEnableOutput | Ctrl | 284 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Changes the DeviceReclosingEnabled status to Enabled
CtrlDisableAltSetting | Ctrl | 303 | DMS |  | Reclosers, Breakers | At any node | Not supported | DPF, PRV, Reconfig | Protection Group | This control set "Primary Setting Group" as active setting group.
CtrlEnableAltSetting | Ctrl | 302 | DMS |  | Reclosers, Breakers | At any node | Not supported | DPF, PRV, Reconfig | Protection Group | This control set "Alternate Setting Group" as active setting group.
CtrlEnableSettingGroup1 | Ctrl | 244 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 1 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup2 | Ctrl | 245 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 2 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup3 | Ctrl | 246 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 3 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup4 | Ctrl | 247 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 4 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup5 | Ctrl | 248 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 5 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup6 | Ctrl | 249 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 6 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup7 | Ctrl | 250 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 7 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableSettingGroup8 | Ctrl | 251 | DMS |  | Reclosers, Breakers | At any node | Not supported | Reconfig | Protection Group | Sets Setting Group 8 as active protection group (Note that SetPntProtectionSettingsGroup can be used instead) |  | Disabled | Enabled
CtrlEnableVoltReductionMode1 | Ctrl | 261 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Sets voltage reduction step 1 as the selected step. Causes step 2 and step 3 to be unselected | ABC
CtrlEnableVoltReductionMode2 | Ctrl | 262 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Sets voltage reduction step 2 as the selected step. Causes step 1 and step 3 to be unselected | ABC
CtrlEnableVoltReductionMode3 | Ctrl | 263 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Sets voltage reduction step 3 as the selected step. Causes step 1 and step 2 to be unselected | ABC
CtrlGroundTripDisableOutput | Ctrl | 294 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Sets the GroundTripEnabled status to Disabled
CtrlGroundTripEnableOutput | Ctrl | 285 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Changes the GroundTripEnabled status to Enabled
CtrlInverterActiveModeHFRT | Ctrl | 225 | DMS |  | Inverter |  | Not supported | LVM | Inverter | HFRT mode active
CtrlInverterActiveModeHVRT | Ctrl | 221 | DMS |  | Inverter |  | Not supported | LVM | Inverter | HVRT mode active
CtrlInverterActiveModeLFRT | Ctrl | 223 | DMS |  | Inverter |  | Not supported | LVM | Inverter | LFRT mode active
CtrlInverterActiveModeLVRT | Ctrl | 216 | DMS |  | Inverter |  | Not supported | LVM | Inverter | LVRT mode active
CtrlInverterActiveModeVoltVar | Ctrl | 207 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Volt-VAR control active
CtrlInverterActiveModeVoltWatt | Ctrl | 214 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Volt-Watt control active
CtrlInverterActiveModeWattPf | Ctrl | 209 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Watt-PF mode active
CtrlKVARSetpointOutput | Ctrl | 281 | DMS |  | DER, DG | At any node | Not supported | LVM | Generator | KVAR setpoint output
CtrlkWSetpointOutput | Ctrl | 204 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Watt setpoint output
CtrlLowerTapOutput | Ctrl | 232 | DMS |  | Transformer | At any node | Not supported | LVM | Transformer | Control issued by LVM application to lower the tap position | A,B,C,ABC | -- | --
CtrlMaxRampRateOutput | Ctrl | 219 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Setpoint for maximum ramp rate
CtrlMultiStateStatusControl | Ctrl | 301 | DMS |  | Composite Switch | At any node | Not supported | Reconfig | Switch | The CtrlMultiStateStatusControl is a four state ADMS to SCADA control output measurement used for issuing a composite (multi-state) switch control to SCADA from the ADMS Plan Manager subsystem. The SDIS and XDIS bits for this multi-state status control are set based on the mapping table defined in the composite switch model in the global.csv file, specifically the SCADAVALUEn_COMPSWMOD field (or the ScadaValue field in the globalinternals.xml file). The composite switch states’ SCADA value is configured in the model which maps each valid state to a SCADA value. For example, the mapping table for the RAG type composite switch is as follows: Open: SDIS = 0, XDIS = 0 (SCADA Value 0) Tie: SDIS = 0, XDIS = 1 (SCADA Value 1) Closed: SDIS = 1, XDIS = 0 (SCADA Value 2) Not Used (not supported): SDIS = 1, XDIS = 1 (SCADA Value 3)
CtrlPFSetpointOutput | Ctrl | 282 | DMS |  | DER, DG | At any node | Not supported | LVM | Generator | PF setpoint output
CtrlProhibitRestorationDisableOutput | Ctrl | 295 | DMS |  | Breaker | At any node | Not supported | -- | Output | Sets the ProhibitRestoration status to Disabled
CtrlProhibitRestorationEnableOutput | Ctrl | 286 | DMS |  | Breaker | At any node | Not supported | -- | Output | Changes the ProhibitRestoration status to Enabled
CtrlRaiseTapOutput | Ctrl | 231 | DMS |  | Transformer | At any node | Not supported | LVM | Transformer | Control issued by LVM application to raise the tap position | A,B,C,ABC | -- | --
CtrlRampRateOutput | Ctrl | 217 | DMS |  | Inverter |  | Not supported | LVM | Inverter | Default ramp rate
CtrlReverseVoltSetPointOutput | Ctrl | 267 | DMS |  | Capacitor |  | Not supported | LVM | Transformer | Sets the reverse regulation voltage setpoint | ABC
CtrlSchemeAutoEnabled |  | 129 | Deprecated | Obsolete. Use SchemeAutoEnabled instead |  |  |  | -- | --
CtrlSettingGroupPrimAlt | Ctrl | 256 | DMS | Obsolete. Use CtrlEnableAltSetting and CtrlDisableAltSetting instead.
CtrlSwitch3STSCloseOutput | Ctrl | 298 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Sets the switch status to Close.
CtrlSwitch3STSOpenOutput | Ctrl | 297 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Sets the switch status to Open.
CtrlSwitchAHLInOutput | Ctrl | 299 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Sets the switch status to In.
CtrlSwitchAHLOutOutput | Ctrl | 300 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Sets the switch status to Out.
CtrlSwitchLocallRemote |  | 118 | Deprecated | Obsolete. Use DeviceLocalRemote instead. |  |  |  | -- | --
CtrlSwitchPreventClose |  | 119 | Deprecated | Obsolete. Use SwitchCloseBlocked instead |  |  |  | -- | --
CtrlSwitchPreventNormalClose | Ctrl | 296 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Sets the SwitchPreventNormalClose status.
CtrlSwitchStatusCloseOutput | Ctrl | 239 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Control issued by FISR/AFR application to close a Remotely controlled Switching device | A,B,C,ABC
CtrlSwitchStatusOpenOutput | Ctrl | 238 | DMS |  | Breaker, Recloser, Switch | At any node | Not supported | Reconfig | Switch | Control issued by FISR/AFR application to open a Remotely controlled Switching device | A,B,C,ABC
CtrlSwitchSuperviosryCutout |  | 116 | Deprecated | Obsolete. Use DeviceSupervisoryCutout instead. |  |  |  | -- | --
CtrlVoltReductionOffOutput | Ctrl | 265 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Turns off voltage reduction. Sets MeasVReductRegTap to disabled. | ABC
CtrlVoltReductionOnOutput | Ctrl | 264 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Turns on voltage reduction. Sets MeasVReductRegTap to enabled. | ABC
CtrlVVCReadyOffOutput | Status | 230 | DMS |  |  |  | Not supported | LVM | Eligibility | LVM ready off output status.
CtrlVVCReadyOnOutput | Status | 229 | DMS |  |  |  | Not supported | LVM | Eligibility | LVM ready on output status.
CurrentFeederCustomerCount | Analog | 259 | DMS |  | Feeder head breaker or feeder head object |  | Not supported | -- | -- | The dynamic customer count for the feeder based on the current NTP calculated value. | ABC
DAProhibit | Status | 102 | SCADA |  | Breaker | At any node |  | Reconfig | Team/Scheme | Status point modeled for feeder breaker if the feeder have Teams and Schemes. Depending on the configuration, when DAProhibit (DAP) point is set to Enabled, and the feeder breaker is open, then ADMS should issue control to disable all Team and Scheme devices. When DAP point is set to Disabled, and the feeder breaker is closed, then ADMS should issue control to enable all Team and Scheme devices. If the RECLOSING_DISABLED_POINT_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if DAProhibit is set to "Enabled" on a feeder head breaker and the feeder breaker is open, all automated switching scheme devices on a feeder are disarmed. Disarming includes the following operations: • DeviceReclosingEnabled is changed from 1 to 0 (reclosing is disabled) • ProhibitRestoration is changed from 0 to 1 (no restoration allowed) • GroundTripEnabled is changed from 1 to 0 (ground trip protection turned off) If the ARM_DEACTIVATED_DEVICE_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if StatusDAEnabled = 1, DAProhibit = 0, and DeviceReclosingEnabled = 1 on a feeder head breaker and the breaker is closed, all automated switching scheme devices on a feeder are rearmed. Arming (rearming) includes the following operations: • DeviceReclosingEnabled is changed from 0 to 1 (reclosing is enabled) • ProhibitRestoration is changed from 1 to 0 (restoration is allowed) • GroundTripEnabled is changed from 0 to 1 (ground trip protection turned on) | ABC | Disabled | Enabled
DERProductionPOutput | Analog | 272 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for DER real power production to this measurement. | ABC
DERProductionQOutput | Analog | 273 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for DER reactive power production to this measurement. | ABC
DeviceAutoManual | Status | 110 | SCADA |  | Capacitor, [Regulator] Transformer with TransType=Regulator, Switch, Power Transformer (which has TransType = Power) | At any node | AutoManual | LVM, Reconfig | Eligibility | DNAF applications don't issue controls on devices that are in Manual Mode. If the device is in Auto mode, the DeviceSupervisoryControl status will be used to issue controls NOTE: DOTS -Change between Auto and Manual is blocked when Local/Remote mode is Local | A,B,C,ABC | Manual | Auto
DeviceLocalRemote | Status | 118 | SCADA |  | Breaker, Recloser, Switch | At any node |  | Reconfig | Eligibility | DNAF applications don't issue controls on devices that are in Local Mode. | A,B,C,ABC | Local | Remote
DeviceReclosingEnabled | Status | 111 | SCADA |  | Recloser, Breaker | At any node | ReclosingEnabled | Reconfig | Miscellaneous | Specifies whether the device reclosing is enabled. Also used by DOTS: governs attempt to reclose while simulating a fault. If the RECLOSING_DISABLED_POINT_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if DeviceReclosingEnabled is disabled on a feeder head breaker, all automated switching scheme devices on a feeder are disarmed. Disarming includes the following operations: • DeviceReclosingEnabled is changed from 1 to 0 (reclosing is disabled) • ProhibitRestoration is changed from 0 to 1 (no restoration allowed) • GroundTripEnabled is changed from 1 to 0 (ground trip protection turned off) If the ARM_DEACTIVATED_DEVICE_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if StatusDAEnabled = 1, DAProhibit = 0, and DeviceReclosingEnabled = 1 on a feeder head breaker and the breaker is closed, all automated switching scheme devices on a feeder are rearmed. Arming (rearming) includes the following operations: • DeviceReclosingEnabled is changed from 0 to 1 (reclosing is enabled) • ProhibitRestoration is changed from 1 to 0 (restoration is allowed) • GroundTripEnabled is changed from 0 to 1 (ground trip protection turned on) |  | Disabled | Enabled
DeviceSupervisoryCutout | Ctrl | 117 | SCADA |  | Breaker, Recloser, Switch, Capacitor, Recloser, Transformer | At any node | SupervisoryCutout | LVM, Reconfig | Eligibility | The DeviceSupervisoryCutout measurement stores the state of the device's ability to accept controls. | A,B,C,N,ABC | Open control commands are rejected | Closed control commands are accepted
EGLPOutput |  | 226 | Deprecated | Not used |  |  |  | -- | --
Energized |  | 207 | Deprecated | Obsolete. Use EnergizedStatus instead. |  |  |  | -- | --
EnergizedA |  | 208 | Deprecated | Obsolete. Use EnergizedStatus instead. |  |  |  | -- | --
EnergizedB |  | 209 | Deprecated | Obsolete. Use EnergizedStatus instead. |  |  |  | -- | --
EnergizedC |  | 210 | Deprecated | Obsolete. Use EnergizedStatus instead. |  |  |  | -- | --
EnergizedStatus | Status | 243 | DMS |  | Transformer | At any node | Not supported | -- | -- | Adjusted by DMS to reflect changes in network topology. | A, B, C, AN, BN, CN, ABC, ABCN | De-energized | Energized
FaultStatus | Status | 15 | SCADA |  | Fault Detector | At any node | Not supported | FL, FISR | Fault | Indication from SCADA that a particular node saw a fault current. DMS application like Fault Location ,FISR gets triggered when it gets SET. | A,B,C,N,ABC | Unset | Set
FaultStatus1 |  | 153 | Deprecated | Obsolete |  |  |  | -- | --
FaultStatus2 |  | 154 | Deprecated | Obsolete |  |  |  | -- | --
FaultStatusA |  | 16 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
FaultStatusB |  | 17 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
FaultStatusC |  | 18 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
FaultStatusMultiState | Status | 153 | SCADA |  | Fault Detector | At any node | Not supported | FL, FISR | Fault | Indication from SCADA that a node saw a fault occurs at downstream/upstream if it is three phase fault, or a fault occurs at bus side/line side if it is single phase fault. This status measurement is 4-state measurement.
FaultStatusN |  | 19 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
FeederAutoReconfigAbn |  | 115 | Deprecated | Obsolete |  |  |  | -- | --
FeederColor | Analog | 201 | DMS |  | Line, Jumper | At any node | Not supported | -- | -- | The dynamic feeder is determined by NTP for all feeder (and lateral) devices. The feeder color (the numeric index of the color from the Viewer Configuration) is sent from the DMS to SCADA to set the feeder color for devices in a SCADA one-line diagram. See Section "Feeder Colors" in the ADMS Modeling Reference Guide.
FeederFltDetected |  | 114 | Deprecated | Obsolete |  |  |  | -- | --
Frequency | Analog | 16 | SCADA |  | Substation | n/a | Not supported | DPF | Miscellaneous | Frequency measurement value from SCADA.
GenerationCapacityPOutput | Analog | 274 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for real power generation capacity to this measurement. | ABC
GenerationCapacityQOutput | Analog | 275 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for reactive power generation capacity to this measurement. | ABC
GenericAnalog | Analog | 123 | SCADA |  | none |  | Not supported | -- | -- | Measurements which do not affect the topology or other electrical view of the distribution system (e.g. door alarm) may be modeled as GenericAnalog. In DOTS, values can be set with an event script and forwarded to SCADA.
GenericStatus | Status | 124 | SCADA |  | none | optional | Not supported | -- | -- | Measurements which do not affect the topology or other electrical view of the distribution system (e.g. door alarm) may be modeled as GenericStatus. In DOTS, values can be set with an event script and forwarded to SCADA. |  | Off | On
GenMeasurementType |  | 13 | Deprecated | Obsolete |  |  |  | -- | --
GroundTripEnabled | Status | 112 | SCADA |  | Breaker, Recloser | At any node | GroundTripEnabled | Reconfig, PRV | Miscellaneous | This measurement status value indicates wherher the recloser or breaker has ground trip protection. This is mainly used for PRV application and for automated local peer-to-peer switching schemes. If the RECLOSING_DISABLED_POINT_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if GroundTripEnabled is set to "Disabled" on a feeder head breaker, all automated switching scheme devices on a feeder will have GroundTripEnabled set to "Disabled". If the ARM_DEACTIVATED_DEVICE_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if GroundTripEnabled is set to "Enabled" on a feeder head breaker, all automated switching scheme devices on a feeder will have GroundTripEnabled set to "Enabled" |  | Disabled | Enabled
HaloColor | Analog | 241 | DMS |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | -- | -- | Abnormal connectivity including looped, partially energized, or de-energized status is determined by NTP for all DNOM topology objects including conductors. The halo color is sent from the DMS to SCADA to set the halo color for devices in a SCADA one-line diagram. | ABC
KVAROutput | Analog | 212 | DMS |  | Feeder, power transforme, and station | on the device | Not supported | -- | -- | The three phase aggregated reactive power value on each level. This analog is sent from the DMS to SCADA to display the value in a SCADA one-line diagram. | ABC
KVARSetpoint | Analog | 176 | SCADA |  | DER, DG |  | Not supported | DPF | Generator | kVAR Setpoint
KWOutput | Analog | 211 | DMS |  | Feeder, power transforme, and station | on the device | Not supported | -- | -- | The three phase aggregated active power values on each level. This analog is sent from the DMS to SCADA to display the value in a SCADA one-line diagram. | ABC
kWSetpoint | Analog | 178 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Watt setpoint. Sets power output to the specified level.
Looped | Status | 203 | DMS |  | 2-winding Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | -- | -- | Set by the Network Topology Processor and used by NetClient to affect the display of the device (see Viewer Configuration Editor). Available to SCADA for display or any other purpose it pleases. | A,B,C,ABC | Not Looped | Looped
LoopedA |  | 204 | Deprecated | Obsolete. Use Looped instead. |  |  |  | -- | --
LoopedB |  | 205 | Deprecated | Obsolete. Use Looped instead. |  |  |  | -- | --
LoopedC |  | 206 | Deprecated | Obsolete. Use Looped instead. |  |  |  | -- | --
LtcCapBlockMeasurementType | Status | 11 | SCADA |  | Regulating Transformer |  | TapBlocked | DPF | Eligibility | This measurement is used for the blocking of regulating transformers.
LtcCapFixMeasurementType |  | 9 | Deprecated | Obsolete |  |  |  | -- | --
LtcCapRemoteMeasurementType | Status | 10 | SCADA |  | Capacitor, Tap Changing Transformer |  | RemoteLocal | DPF | Eligibility | This measurement is used for the tap changing transformer and capacitor Remote/Local status.
ManOperDisabled | Status | 113 | SCADA | Use DeviceSupervisoryCutout instead. | Capacitor |  | Not supported | DPF | Eligibility | The capacitor Local/Remote status.
MeasActivePickup | Analog | 134 | SCADA |  | Breaker, Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Analog value for the phase trip current setting in the protective device's settings group. This measurement value has high priority that the phase trip current setting from the protection settings file ProtectionSettings.csv.
MeasAmpA |  | 41 | Deprecated | Obsolete. Use MeasAmps instead. |  |  |  | -- | --
MeasAmpB |  | 42 | Deprecated | Obsolete. Use MeasAmps instead. |  |  |  | -- | --
MeasAmpC |  | 43 | Deprecated | Obsolete. Use MeasAmps instead. |  |  |  | -- | --
MeasAmpN |  | 44 | Deprecated | Obsolete. Use MeasAmps instead. |  |  |  | -- | --
MeasAmps | Analog | 40 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. The Amp flows when multiplied by the telemetered or DPF estimated voltage provide the VA value which is used in the load allocation process. | A,B,C,N,ABC
MeasAutoOpIntell |  | 38 | Deprecated | Obsolete. Use SchemeAutoEnabled instead. |  |  |  | -- | --
MeasAvgVoltOutput | Analog | 269 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Measured average voltage of the regulated bus. | ABC
MeasCommEstablished | Status | 39 | SCADA |  | Capacitor, Switch |  | Not supported | LVM, Reconfig | Eligibility | Measurement communication established status. |  | Not Established | Established
MeasEnergized | Status | 32 | DMS |  |  |  | Not supported | -- | -- | Passes the energization status from DMS to SCADA. If the device is closed, the node energization status is used to set the measurement status. | A,B,C,ABC
MeasFaultCurrent | Analog | 108 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | FL, FISR | Fault | The Fault Location application utilizes fault current measurements and fault indication measurements (measurement type FaultStatus) from the feeder breaker to find feeder fault locations. These fault locations are shown on the DMS geographic UI and also in a tabular format. | A,B,C,N,ABC
MeasFaultExistsA |  | 33 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
MeasFaultExistsB |  | 34 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
MeasFaultExistsC |  | 35 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
MeasFaultExistsG |  | 36 | Deprecated | Obsolete. Use FaultStatus instead. |  |  |  | -- | --
MeasNSFaultStatus | Status | 96 | SCADA |  | Transformer (Power or ZigZag) | At any node | Not supported | FSD | Fault | The status will tell the FSD application if a fault exists. It is a SCADA calculated status point which is based on the analog measurement type MeasNSVoltage. See the SCADA calculation details in for MeasNSVoltage. |  | Unset | Set
MeasNSVoltage | Analog | 97 | SCADA |  | Transformer (Power or ZigZag) | At any node | Not supported | FSD | Fault | The value is very small (close to zero) when there is no fault (Network balanced and neutral close to earth). Based on MV voltage level (22kV or 33kV) the expected value is in the range of 20V to 200V in case of single line to ground fault. A SCADA calculation is used to calculate MeasNSFaultStatus. If the value is less than threshold , then it is considered no fault (MeasNSFaultStatus is False); If the value is values is greater than threshold, then it is considered as faulted (MeasNSFaultStatus is True). The threshold is a fixed value and defined in SCADA. The typical value for threshold is 10V or 20V. For Fantasy Island simulation environment, 0.0 is given when there is no fault and 200.0 is given when there is ASC fault.
MeasPFA |  | 91 | Deprecated | Obsolete. Use PfMeasurementType instead. |  |  |  | -- | --
MeasPFB |  | 92 | Deprecated | Obsolete. Use PfMeasurementType instead. |  |  |  | -- | --
MeasPFC |  | 93 | Deprecated | Obsolete. Use PfMeasurementType instead. |  |  |  | -- | --
MeasPFN |  | 94 | Deprecated | Obsolete. Use PfMeasurementType instead. |  |  |  | -- | --
MeasPFT |  | 90 | Deprecated | Obsolete. Use PfMeasurementType instead. |  |  |  | -- | --
MeasPhaseAngle | Analog | 95 | SCADA |  | MeasurementPoint at the RefBusInterface | At single node | Not supported | DPF | BLA | The voltage magnitude and voltage angle are commonly transferred from the EMS State Estimator to SCADA analogs. The relative voltage phase angle difference is critical for DMS in determining valid switching plans generated by the switching reconfiguration applications including FISR, AFR, PLOS, and FISRCA. | ABC
MeasProtectionSettingGroup | Analog | 133 | SCADA |  | Breaker, Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | DMS uses this message to confirm which protection settings group is now applied. To convert the received float value to an integer that is associated with a protection settings group number, the system uses a tolerance that is specified by the MEAS_PROT_SETTINGS_TOLERANCE parameter in NetServerMainConfig_localhost.txt.
MeasReadyIntell |  | 37 | Deprecated | Obsolete |  |  |  | -- | --
MeasSchemeEnabled | Status | 129 | SCADA |  | Feeder Head |  | Not supported | Reconfig | Team/Scheme | Specifies whether the scheme is enabled (for the team and scheme functionality)
MeasSecVarOutput | Analog | 278 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Measured three-phase aggregated reactive power at the secondary side of station transformers | ABC
MeasSecWOutput | Analog | 280 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Measured three-phase aggregated real power at the secondary side of station transformers | ABC
MeasSiteModeStatus |  | 109 | Deprecated | Obsolete |  |  |  | -- | --
MeasStateOfCharge | Analog | 18 | SCADA |  | Energy Resource |  | Not supported | -- | -- | Energy resource state of charge (SoC), which is the level of charge of the DER storage device relative to device's capacity (in kWh). SoC is specified as a fraction (For example, 0.0 = empty or 0%; 1.0 = full or 100%).
MeasSwitchReady | Status | 127 | Deprecated | Not used. Use SchemeAutoEnabled |  |  |  | -- | --
MeasTeam1Ready | Status | 87 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 1 readiness status, Team1 Ready. A switch can participate in up to 8 teams. Applies to the team and scheme functionality. Not currently used in DNAF code.
MeasTeam2Ready | Status | 88 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 2 readiness status, Team2 Ready. Not currently used in DNAF code.
MeasTeam3Ready | Status | 89 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 3 readiness status, Team3 Ready. Not currently used in DNAF code.
MeasTeam4Ready | Status | 90 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 4 readiness status, Team4 Ready. Not currently used in DNAF code.
MeasTeam5Ready | Status | 91 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 5 readiness status, Team5 Ready. Not currently used in DNAF code.
MeasTeam6Ready | Status | 92 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 6 readiness status, Team6 Ready. Not currently used in DNAF code.
MeasTeam7Ready | Status | 93 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 7 readiness status, Team7 Ready. Not currently used in DNAF code.
MeasTeam8Ready | Status | 94 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | The team 8 readiness status, Team8 Ready. Not currently used in DNAF code.
MeasTransferinProgress | Status | 128 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | Reconfig | Team/Scheme | Specifies whether the switch is being transferred in scope of the team and scheme functionality
MeasVARA |  | 71 | Deprecated | Obsolete. Use MeasVARs instead, |  |  |  | -- | --
MeasVARB |  | 72 | Deprecated | Obsolete. Use MeasVARs instead, |  |  |  | -- | --
MeasVARC |  | 73 | Deprecated | Obsolete. Use MeasVARs instead, |  |  |  | -- | --
MeasVARN |  | 74 | Deprecated | Obsolete. Use MeasVARs instead, |  |  |  | -- | --
MeasVARs | Analog | 70 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This measurement type is for VAR flow. | A,B,C,ABC
MeasVARsQ1 | Status | 71 | DMS |  | Inverter |  | Not supported | BLA/DPF | BLA | Measured VARs Q1 |  | Disabled | Enabled
MeasVARsQ4 | Status | 72 | DMS |  | Inverter |  | Not supported | BLA/DPF | BLA | Measured VARs Q4 |  | Disabled | Enabled
MeasVltAmps | Analog | 80 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer |  | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This measurement type is for VA flow. | A,B,C,ABC
MeasVoltA |  | 51 | Deprecated | Obsolete. Use MeasVolts instead. |  |  |  | -- | --
MeasVoltB |  | 52 | Deprecated | Obsolete. Use MeasVolts instead. |  |  |  | -- | --
MeasVoltC |  | 53 | Deprecated | Obsolete. Use MeasVolts instead. |  |  |  | -- | --
MeasVoltN |  | 54 | Deprecated | Obsolete. Use MeasVolts instead. |  |  |  | -- | --
MeasVolts | Analog | 50 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. The voltage when multiplied by telemetered Amp floew measurements provide a VA value which is used in the load allocation process. Voltage measurements are also used in the LVM application to provide a better voltage "operating envelope" which is very important in preventing low or high load voltages. | A,B,C,ABC
MeasVReductRegTap | Status | 31 | SCADA |  | [Regulator] Transformer with TransType=Regulator; [LTC Transformer] Transformer with TransType=Power and (PriTap or SecTap)=Regulating; | At any node | Not supported | DPF | Transformer | If a regulating transformer is voltage reduction capable then this status point indicates the status. i.e. the controller's target voltage setting to a lower value (the voltage reduction percentage is set in the static model defnition for the regulator or LTC).
MeasWattA |  | 61 | Deprecated | Obsolete. Use MeasWatts instead. |  |  |  | -- | --
MeasWattB |  | 62 | Deprecated | Obsolete. Use MeasWatts instead. |  |  |  | -- | --
MeasWattC |  | 63 | Deprecated | Obsolete. Use MeasWatts instead. |  |  |  | -- | --
MeasWattN |  | 64 | Deprecated | Obsolete. Use MeasWatts instead. |  |  |  | -- | --
MeasWatts | Analog | 60 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | The DPF application, along with BLA, allocates valid flow measurements (Watt/VAR or VA) to non-telemetered loads. All DNAF utilize the results from the load allocation. This measurement type is for Watt flow. | A,B,C,ABC
MeasWeightedVoltOutput | Analog | 276 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | Measured weighted average voltage of the regulated bus. | ABC
NominalFeederCustomerCount | Analog | 260 | DMS |  | Feeder head breaker or feeder head object |  | Not supported | -- | -- | The nominal customer count for the feeder. | ABC
NominalSettingGroup | Analog | 199 | SCADA |  | Recloser |  | Not supported | Reconfig | Protection Group | Nominal settings group for a device at the current feeder. Used by DPF to correct settings group if not correct. (via the Settings Group Correction option on the DPF page in the DNAF Configuration Editor. Used when there is no overcurrent section (lookup) in the protection settings file ProtectionSettings.csv.
NoneMeasurementType | N/A | 0 | N/A | Should never appear in a model file. | N/A | N/A | N/A | -- | -- | This measurement type is occasionally exposed to the modeler, but it should not be selected. It is used by DMS code as a delimiter of the valid measurement types. | N/A | N/A | N/A
PfMeasurementType | Analog | 6 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer | At any node | Not supported | BLA/DPF | BLA | A power factor measurement along with Amps and Volts allows Watt and VAR values to be calculated. The Watt and VAR values are used in the DPF application, along with BLA, to allocate valid flow measurements (Watt/VAR or VA) to non-telemetered loads. | A,B,C,ABC
PFSetpoint | Analog | 177 | SCADA |  | DER, DG |  | Not supported | DPF | Generator | PF Setpoint
PhaseTripSettingGroup1 | Analog | 154 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Normal Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup2 | Analog | 155 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 1 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup3 | Analog | 156 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 2 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup4 | Analog | 157 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 3 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup5 | Analog | 158 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 4 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup6 | Analog | 159 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 5 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup7 | Analog | 160 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 6 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PhaseTripSettingGroup8 | Analog | 161 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Alternate 7 Trip Setting used by PRV and FISR PRV. | A,B,C,ABC
PredictedStatus | Status | 242 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | -- | Provides OMS predicted status to SCADA. | A,B,C,ABC | MeasDnomMultiState = true SDIS XDIS MEANING 0 0 NOT PREDICTED 0 1 CONFIRMED CLOSED 1 0 PREDICTED OPEN 1 1 NOT VALID
ProhibitRestoration | Status | 103 | SCADA |  | Breaker | At any node |  | Reconfig | Eligibility | Status point modeled for feeder breaker. If Enabled, the load that is shed by the load shedding function will not be restored automatically. |  | Disable | Enable
RecloserOpMode | Status | 130 | SCADA | Future (not used) | Recloser |  | Not supported | Reconfig | Switch | Recloser operating mode. Used to specify or override the optionally modelled nominal operating mode for reclosers.
RemoteLocalDriver | Status | 254 | DMS |  | Capacitor, LTC Transformer |  |  | LVM | Miscellaneous | Remote/Local driver status. |  | Local | Remote
ReverseFaultStatus | Status | 175 | SCADA |  | Fault Detector | At any node | Not supported | FL, FISR | Fault | Indication from SCADA that a particular type 2 fault indicator saw a reverse fault current. DMS application like FISR gets triggered when it gets SET. If it is the single measurement indicating the reveser direction and the actual phase is defined by the FaultStatus measurement, then the phase of this reverse flag measurement must be ABC. | A,B,C,N,ABC | Unset | Set
ReverseVoltSetpoint | Analog | 169 | DMS |  | Capacitor |  | Not supported | DPF | Transformer | Voltage setpoint for the reverse regulation direction. If available, this measurement value is used as a voltage target instead of the value in the regulationcotrol.csv file. | A,B,C,ABC
SchemeAutoEnabled | Status | 121 | SCADA |  | Switch, Fuse, Breaker, Recloser, Sectionalizer |  | TransferSchemeEnabled | Reconfig | Team/Scheme | This status indicates that a local control scheme is enabled. The real time FISR and AFR applications consider any switching device that is active in a scheme as an ineligible control device (FISR and AFR plans do not recommend switching these devices). |  | Disabled | Enabled
SetActiveAnalogRegulationMode | Ctrl | 234 | DMS |  | Transformer, Regulator |  | Not supported | LVM | Transformer | Sets active regulation mode for telemetered regulators which has advanced regulation ability. The SCADA value must match the index value given in the Regulation Mode record in the RegulationControl.csv file.
SetAutoDeterminationMode | Ctrl | 292 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Auto-Determination. Applies to cogen voltage regulators.
SetBidirectionalMode | Ctrl | 291 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Bi-Directional. Applies to cogen voltage regulators.
SetCapStepPositionOutput | Status | 240 | DMS |  | Capacitor |  | Not supported | LVM | Capacitor | Capacitor step output. Used in the LVM capacitor step control (for multi-step capacitors). | A,B,C,ABC
SetCogenMode | Ctrl | 290 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Cogeneration. Applies to cogen voltage regulators.
SetDefInverterMaxRampRate | Analog | 190 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Setpoint for maximum ramp rate
SetDefInverterRampRate | Analog | 188 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Default ramp rate
SetIdleMode | Ctrl | 289 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Idle. Applies to cogen voltage regulators.
SetLoadShedEnabled | Status | 257 | DMS |  | Breaker, Recloser |  | Not supported | Load Shed | Miscellaneous | Indicates if the device is available for the load shed. | ABC
SetLoadShedSortOrder | Analog | 258 | DMS |  | Breaker, Recloser |  | Not supported | Load Shed | Miscellaneous | The load shed sorting setting. The sorting is used to determine which device is shed first.
SetLockedForwardMode | Ctrl | 287 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Locked-Forward. Applies to cogen voltage regulators.
SetLockedReverseMode | Ctrl | 288 | DMS |  | Regulator |  | Not supported | DPF | Transformer | Sets regulation mode to Locked-Reverse. Applies to cogen voltage regulators.
SetPntProtectionSettingsGroup | Ctrl | 283 | DMS |  | Breaker, Recloser | At any node | Not supported | Reconfig | Protection Group | DMS uses this control to send a new protection settings group value to be applied
SetTapPositionOutput | Status | 233 | DMS |  | Transformer |  | Not supported | LVM | Transformer | Tap position output. Used in the existing LVM setpoint control logic.
SetVoltReductionValue | Analog | 266 | DMS |  | Transformer, Regulator | At any node | Not supported | LVM | Transformer | Sets the analog voltage reduction percent in AnalogVoltReductionValue | ABC
SetVoltSetPointOutput | Ctrl | 255 | DMS |  | Power Transformer, Regulator | At any node | Not supported | LVM | Transformer | Control issued by LVM application to adjust value of transformer or regulator voltage set point | A,B,C,ABC
SimulateSwitchStatus | Status | 132 | SCADA |  | n/a | n/a | Not supported | -- | -- | Enables a SCADAMOM MANUAL or CALC POINT to display as tagged in DMS. This measurement supports hardware-implemented group controls which can be inhibited in SCADA by tagging the "parent" group control point. | n/a | Open | Closed
StActCap | Analog | 73 | DMS |  | Inverter |  | Not supported | BLA/DPF | Capacitor | StActCap. FixedW=0, FixedVAR=1, FixedPF=2
StatusAutoDeterminationMode | Status | 86 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Auto Determination regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusBidirectionalMode | Status | 85 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Bi-Directional regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusCogenMode | Status | 84 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Cogeneration regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusDAEnabled | Status | 144 | SCADA |  | Recloser, Breaker, controllable Switch,Feeder,Substation |  | Not supported | Reconfig | Eligibility | The Distribution Automation (advanced DNAF applications) eligibility status of a device. If the RECLOSING_DISABLED_POINT_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if StatusDAEnabled is set to "Disabled" on a feeder head breaker, all automated switching scheme devices on a feeder are disarmed. Disarming includes the following operations: • DeviceReclosingEnabled is changed from 1 to 0 (reclosing is disabled) • ProhibitRestoration is changed from 0 to 1 (no restoration allowed) • GroundTripEnabled is changed from 1 to 0 (ground trip protection turned off) If the ARM_DEACTIVATED_DEVICE_ENABLED parameter in NetServerDnafConfig.txt is enabled (=1), if StatusDAEnabled = 1, DAProhibit = 0, and DeviceReclosingEnabled = 1 on a feeder head breaker and the breaker is closed, all automated switching scheme devices on a feeder are rearmed. Arming (rearming) includes the following operations: • DeviceReclosingEnabled is changed from 0 to 1 (reclosing is enabled) • ProhibitRestoration is changed from 1 to 0 (restoration is allowed) • GroundTripEnabled is changed from 0 to 1 (ground trip protection turned on) |  | Disabled | Enabled
StatusDAEnabledOutput |  | 254 | Deprecated | Obsolete |  |  |  | -- | --
StatusDeviceAlarm | Status | 135 | SCADA |  | Transformer, Series_Reactor, Line, Switch, Jumper, Fuse, Breaker, Recloser, Sectionalizer, Capacitor, Generator, SVC | At any node | Not supported | LVM, Reconfig | Eligibility | Used by DNAF to disable Distribution Automation on the device, if the device is in Alarm. Can be used to indicate the device has failed. |  | Normal | Alarm
StatusFlowDirection | Status | 170 | SCADA |  | Regulator |  | Not supported | BLA/DPF | BLA | Power flow forward/reverse sensed direction | A,B,C,ABC | Forward | Reverse
StatusIdleMode | Status | 83 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Idle regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusInverterActiveModeFixedPowerFactor | Status | 109 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | This measurement indicates if the fixed power factor control mode is active. |  | Disabled | Enabled
StatusInverterActiveModeFrequencyWatt | Status | 152 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | This measurement indicates if the Frequency-Watt control mode is active. |  | Disabled | Enabled
StatusInverterActiveModeHFRT | Status | 196 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | HFRT control mode active |  | Disabled | Enabled
StatusInverterActiveModeHVRT | Status | 192 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | HVRT control mode active |  | Disabled | Enabled
StatusInverterActiveModeLFRT | Status | 194 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | LFRT control mode active |  | Disabled | Enabled
StatusInverterActiveModeLVRT | Status | 187 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | LVRT control mode active.
StatusInverterActiveModeMaxPowerLimiting | Status | 116 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | This measurement indicates if the max power limiting control mode is active. |  | Disabled | Enabled
StatusInverterActiveModeVoltVar | Status | 181 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Volt-VAR control mode active. |  | Disabled | Enabled
StatusInverterActiveModeVoltWatt | Status | 185 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Volt-Watt control mode active. |  | Disabled | Enabled
StatusInverterActiveModeWattPf | Status | 183 | SCADA |  | Inverter |  | Not supported | DPF | Inverter | Watt-PF control mode active
StatusLockedForwardMode | Status | 81 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Locked-Forward regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusLockedReverseMode | Status | 82 | SCADA |  | Regulator |  | Not supported | DPF | Transformer | The Locked-Reverse regulation mode status. Applies to cogen voltage regulators. |  | Disabled | Enabled
StatusLossVoltageTarget |  | 134 | Deprecated | Obsolete |  |  |  | -- | --
StatusNeutralImbalance | Status | 150 | SCADA |  | Capacitor | At single node | Not supported | LVM | Capacitor | This status indicates that a flow imbalance has been detected at the neutral connection of a capacitor. This commonly indicates a blown fuse in a three-phase capacitor installation. | N | Normal | Imbalance Detected
StatusSCADAControl |  | 148 | Deprecated | Obsolete |  |  |  | -- | --
StatusSettingGroupApplied1 | Status | 136 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 1 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 1 not active | Setting Group 1 is active
StatusSettingGroupApplied2 | Status | 137 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 2 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 2 not active | Setting Group 2 is active
StatusSettingGroupApplied3 | Status | 138 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 3 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 3 not active | Setting Group 3 is active
StatusSettingGroupApplied4 | Status | 139 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 4 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 4 not active | Setting Group 4 is active
StatusSettingGroupApplied5 | Status | 140 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 5 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 5 not active | Setting Group 5 is active
StatusSettingGroupApplied6 | Status | 141 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 6 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 6 not active | Setting Group 6 is active
StatusSettingGroupApplied7 | Status | 142 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 7 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 7 not active | Setting Group 7 is active
StatusSettingGroupApplied8 | Status | 143 | SCADA |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Indicates if Settings Group 8 has been enabled for overcurrent protection. (Either StatusSettingGroupApplied1-8, or StatusSettingGroupPrimAlt, or MeasProtectionSettingGroup can be used) |  | Setting Group 8 not active | Setting Group 8 is active
StatusSettingGroupPrimAlt | Status | 163 | DMS |  | Breaker,Recloser | At any node | Not supported | Reconfig, PRV | Protection Group | Whether the Primary or Alternate setting group is active (Note that either this measurement or StatusSettingGroupApplied1-8 can be used to the specify current setting group). |  | Primary (1) Setting Group is active | Alternate (2) Setting Group is active
StatusVoltageRailsEnabled | Status | 174 | SCADA |  | Capacitor |  | Not supported | DPF | Capacitor | Voltage rails status for a capacitor |  | Disabled | Enabled
StatusVoltReductionMode1 | Status | 165 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | Status indicate the voltage reduction setting. Used in conjuction of StatusVoltReductionMode2 (166) and StatusVoltReductionMode3 (167) to determine which voltage reduction parameter should be used in regulation. | A,B,C,ABC | Voltage reduction mode 1 is NOT active. One of VR modes 2 or 3 should be set. | Voltage reduction mode 1 is selected. If MeasVReductRegTap is Enabled, then this VR step will be used.
StatusVoltReductionMode2 | Status | 166 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | Status indicate the voltage reduction setting. Used in conjuction of StatusVoltReductionMode1 (165) and StatusVoltReductionMode3 (167) to determine which voltage reduction parameter should be used in regulation. | A,B,C,ABC | Voltage reduction mode 2 is NOT active. One of VR modes 1 or 3 should be set. | Voltage reduction mode 2 is selected. If MeasVReductRegTap is Enabled, then this VR step will be used.
StatusVoltReductionMode3 | Status | 167 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | Status indicates the voltage reduction setting. Used in conjuction of StatusVoltReductionMode1 (165) and StatusVoltReductionMode2 (166) to determine which voltage reduction parameter should be used in regulation. | A,B,C,ABC | Voltage reduction mode 3 is NOT active. One of VR modes 1 or 2 should be set. | Voltage reduction mode 1 is selected. If MeasVReductRegTap is Enabled, then this VR step will be used.
StatVVCReady | Status | 101 | SCADA |  | Breaker at Feeder Head | At any node | Not supported | LVM | Eligibility | LVM ignores devices on feeder for which this is "LVM Disabled". This is the value needed per feeder. | ABC | LVM Disabled | LVM Enabled
Switch3STSMeasurementType | Status | 17 | SCADA |  | Breaker, Recloser, Switch |  | Not supported | -- | -- | Three-state switch state (Open, Closed, Transition). | A,B,C,ABC | SDIS = 0: Open SDIS = 1: Close XDIS = 1: Transition
SwitchAHLMeasurementType | Status | 18 | SCADA |  | Breaker, Recloser, Switch |  | Not supported | -- | -- | The device auto reclose and hot line tag states (Auto Reclose Enabled/Disabled and Hot Line Tag Placed /Hot Line Tag Not Placed). | A,B,C,ABC | SDIS = 0: Disabled SDIS = 1: Enabled XDIS = 1: Placed
SwitchCloseBlocked | Status | 120 | SCADA |  | Recloser, Breaker, controllable Switch | At any node | BlockClose | Reconfig | Eligibility | This measurement is an equivalent of the Hot Line Tag/Hold Line Hold function. When Applied, a switching device is not eligible for operation by DNAF applications. | A,B,C,ABC | Not Applied | Applied
SwitchFailure | Status | 122 | SCADA |  | Recloser, Breaker, controllable Switch | At any node | Not supported | Reconfig | Eligibility | Failure Status of the switching device coming from the SCADA. | A,B,C,ABC | Off | On
SwitchLockout | Status | 125 | SCADA |  |  |  | Not supported | FISR | Eligibility | Distribution Automation treats this as the equivalent of a Lockout tag.The Lockout status is also set to On when a recloser or breaker is tripped by an operator in DMS. |  | Off | On
SwitchPreventNormalClose | Status | 119 | SCADA |  | Breaker, Recloser, Switch | At any node |  | Reconfig | Miscellaneous | The switch Prevent Normal-Close status. Used to prevent FISR to close a large DER site back in on a circuit that cannot handle its load. | A,B,C,ABC | Not Applied | Applied
SwitchStatusMeasurementType | Status | 12 | SCADA |  |  |  | Status | DPF | Switch | The switching device status is used by the Network Topology Processor (NTP) to determine network connctivity including energization, abnormal energization, and loops. | A,B,C,ABC | Open | Closed
SwitchStatusOutput |  | 225 | Deprecated | Obsolete |  |  |  | -- | --
TapPositionOutput |  | 221 | Deprecated | Obsolete. Use SetTapPositionOutput instead. |  |  |  | -- | --
TargetVHigh |  | 21 | Deprecated | Obsolete |  |  |  | -- | --
TargetVLow |  | 20 | Deprecated | Obsolete |  |  |  | -- | --
Temperature | Analog | 131 | SCADA |  | Substation | n/a | Not supported | BLA/DPF | Miscellaneous | A substation temperature reading can optionally be used in the DPF (specifically for load allocation) and also for evaluating dynamic ampacity limits for conductors.
TrueLoadPOutput | Analog | 270 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for true real power load to this measurement. | ABC
TrueLoadQOutput | Analog | 271 | DMS |  | DER, DG, Power Transformer, Feeder, Substation | At any node | Not supported | -- | Output | DNAF writes aggregated DPF results for true reactive power load to this measurement. | ABC
VaMeasurementType |  | 4 | Deprecated | Obsolete. Use MeasVltAmps instead. |  |  |  | -- | --
VarMaxPctSetPoint | Analog | 179 | DMS |  | Inverter |  | Not supported | DPF | Inverter | VarMaxPct setPoint. Reactive power, % of I_VArMax.
VarMeasurementType |  | 3 | Deprecated | Obsolete. Use MeasVARs instead. |  |  |  | -- | --
VoltageKVLGInput |  | 24 | Deprecated | Obsolete |  |  |  | -- | --
VoltageKVLGOutput |  | 219 | Deprecated | Obsolete |  |  |  | -- | --
VoltageKVLLInput |  | 23 | Deprecated | Obsolete |  |  |  | -- | --
VoltageKVLLOutput |  | 218 | Deprecated | Obsolete |  |  |  | -- | --
VoltageKVSecondaryInput |  | 25 | Deprecated | Obsolete |  |  |  | -- | --
VoltageKVSecondaryOutput |  | 220 | Deprecated | Obsolete |  |  |  | -- | --
VoltMeasurementType |  | 5 | Deprecated | Obsolete. Use MeasVolts instead. |  |  |  | -- | --
VoltSetpoint | Analog | 162 | SCADA |  | Power Transformer, Regulator | At any node | Not supported | DPF | Transformer | The voltage magnitude of voltage setpoint feedback point. The value is used to monitor the success or failure of voltage setpoint control. | A,B,C,ABC
WattMeasurementType |  | 2 | Deprecated | Obsolete. Use MeasWatts instead. |  |  |  | -- | --
XftapMeasurementType | Analog | 8 | SCADA |  | [Regulator] Transformer with TransType=Regulator; [LTC Transformer] Transformer with TransType=Power and (PriTap or SecTap)=Regulating. | At any node | Not supported | DPF | Transformer | The DNAF needs to have knowledge of the tap position of regulators and LTCs. If the tap position is not provied using this measurement type, the DPF emulates the behavior of the local field controller using control settings entered during model construction (voltage target, voltage bandwidth, and line drop compensation R/X parameters).
DeviceFastTripEnabled | Status | 114 | SCADA |  | Breaker, Recloser | At any node | Not supported | -- | Miscellaneous | This measurement status value indicates whether the recloser or breaker has fast trip protection. |  | Disabled | Enabled
CtrlDeviceFastTripEnableOutput | Ctrl | 304 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Sets the DeviceFastTripEnabled status to Disabled
CtrlDeviceFastTripDisableOutput | Ctrl | 305 | DMS |  | Breaker, Recloser | At any node | Not supported | -- | Output | Changes the DeviceFastTripEnabled status to Enabled

## Globals Input
Sort | Model | Substation Editor Column Name | Global Internals XML Field Name | Corresponding Global CSV Field Name | Attribute Type | Imperial Units | Metric Units | Description | Scope | Possible Values or Reference | Required? | Low Value Imperial Units | High Value Imperial Units | Low Value Metric Units | High Value Metric Units | Queryable Field Name
1 | Area Division | Name | Name | NAME_AREADIV | String | #N/A | #N/A | Operating area/division name. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
2 | Area Division | #N/A | Division | DIVISION_AREADIV | String | #N/A | #N/A | Alternate operating area/division name. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
3 | Area Power Factor | Name | Name | NAME_AREAPF | String | #N/A | #N/A | Unique operational area name. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME
4 | Area Power Factor | #N/A | TargetPFSched | TARGETPFSCHED_AREAPF | String | #N/A | #N/A | Associated target power factor schedule. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | PFSCHED.NAME
5 | Automation Scheme | #N/A | Id | ID_SCHEME | String |  |  | ID of the automation scheme.
6 | Automation Scheme | #N/A | Description | DESCRIPTION_SCHEME | String |  |  | Description of the automation scheme.
7 | Automation Team | #N/A | Id | ID_TEAM | String |  |  | ID of the automation scheme team.
8 | Automation Team | #N/A | Scheme | SCHEME_TEAM | String |  |  | Name of the associated automation scheme.
9 | Automation Team | #N/A | Description | DESCRIPTION_TEAM | String |  |  | Description of the automation scheme team.
10 | Automation Team Switch | #N/A | Id | ID_TEAMSW | String |  |  | ID of the switching device.
11 | Automation Team Switch | #N/A | Team | TEAM_TEAMSW | String |  |  | Name of the associated automation scheme team
12 | Automation Team Switch | #N/A | SecondId | SECONDID_TEAMSW | String |  |  | ID of the automation scheme team.
13 | Automation Team Switch | #N/A | Station1 | STATION1_TEAMSW | String |  |  | The first station that is associated with the switching device.
14 | Automation Team Switch | #N/A | Station2 | STATION2_TEAMSW | String |  |  | The second station that is associated with the switching device. (For boundary switches.)
15 | Automation Team Switch | #N/A | SwitchRole | ROLE_TEAMSW | String |  |  | Switching device role (primary or secondary).
16 | Composite Switch Model | Name | Name | NAME_COMPSWMOD | String | #N/A | #N/A | Composite switch model name. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME
17 | Composite Switch Model | Composite Switch - SwitchType | SwitchType | SWITCHTYPE_COMPSWMOD | Integer | enumeration | enumeration | Enumerated composite switch model type. The enumeration has the following values: 1 = Throwover, 2 = ESCO Throwover, 3 = RAL, 4 = GRAL, 5 = Regulator Bypass, 6 = UG Multi Switch, 7 = Grounding_Switch , 8 = Rag, 9 = Rac. | OPS |  | TRUE | 1 | 9 | 1 | 9 | SWTYPE
18 | Composite Switch Model | Composite Switch - NumLink | NumLink | NUMLINK_COMPSWMOD | Integer | count | count | The number of two node switch links (typically a switch or fuse) that are contained in the composite switch model. | OPS |  | TRUE | 2 | 4 | 2 | 4 | NUMLINK
19 | Composite Switch Model | #N/A | BitmapScheme | BITMAPSCHEME_COMPSWMOD | String | #N/A | #N/A | Name of the bitmap scheme (default is blank). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
20 | Composite Switch Model | Composite Switch - InitialMode | InitialMode | INITIALMODE_COMPSWMOD | Integer | #N/A | #N/A | Initial operating mode (1 = automatic, 0 = manual). | OPS |  | FALSE | 0 | 1 | 0 | 1 | INITMODE
21 | Composite Switch Model | Composite Switch - Is Reconfigurable? | Reconfigurable | RECONFIGURE_COMPSWMOD | Boolean | #N/A | #N/A | Reconfigurable flag for geoschematics (true = reconfigurable). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | RECONFIG
22 | Composite Switch Model | Composite Switch - Number of States | States | NUMSTATE_COMPSWMOD | Integer | count | count | The number of valid switching states. | OPS |  | TRUE | 2 | 4 | 2 | 4 | NUMSTATE
23 | Composite Switch Model | Composite Switch - States Name | StateName | STATENAMEn_COMPSWMOD | String | #N/A | #N/A | The name of the state (as given on the UI includidng the pop-ups and toolbar). | OPS |  | TRUE | #N/A | #N/A | #N/A | #N/A | STNAME
24 | Composite Switch Model | Composite Switch - States State | State | STATEn_COMPSWMOD | Integer | enumeration | enumeration | Integer value representing the on/off status of the individual switch links. For a throwover switch in the preferred state, the value of the switch links are as follows: closed on the preferred link (1) and open on the alternate link (0). This gives a binary state value of 10, which is equal to 2 (base 10). | OPS |  | TRUE | 0 | 15 | 0 | 15 | STVALUE
25 | Composite Switch Model | Composite Switch - States ScadaValue | ScadaValue | SCADAVALUEn_COMPSWMOD | Integer | count | count | Integer value from SCADA for determining the device state. A SCADA value of -1 means the composite switch is in manual state (for example, ground), any SCADA commands will have no effect on composite switch state. If the SCADA value is not -1, then the composite switch is SCADA-telemetered, and the measurement change in SCADA system will update the composite switch state in DMS. | OPS |  | FALSE | -1 | 3 | 0 | 3 | STSCADAVAL
26 | Conductor Model | Name | Name | NAME_CONDMOD | String | #N/A | #N/A | Unique conductor model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
27 | Conductor Model | Conductor – Is Dist Cond? | DistCond | DISTCOND_CONDMOD | Boolean | #N/A | #N/A | Flag indicating model represents a distribution conductor (True = distribution, False = transmission). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | DISTMOD
28 | Conductor Model | Conductor - Rphase | Rphase | RPHASE_CONDMOD | Float | ohms/kft | ohms/km | Phase conductor resistance for a construction model. Not used for sequence impedance model. | DPF |  | TRUE | 0.001 | 10 | 0.0032808 | 32.8084 | RPHASE
29 | Conductor Model | Conductor - Gshunt | Gshunt | GSHUNT_CONDMOD | Float | microSiemens/kft | microSiemens/km | Shunt conductance for a construction model. Not used for sequence impedance model. | DPF | 0 | FALSE | 0.01 | 100 | 0.3937 | 3937 | GSHUNT
30 | Conductor Model | Conductor - Bshunt | Bshunt | BSHUNT_CONDMOD | Float | microSiemens/kft | microSiemens/km | Shunt susceptance for a construction model. Not used for sequence impedance model. | DPF | 0 | FALSE | 0.01 | 100 | 0.3937 | 3937 | BSHUNT
31 | Conductor Model | Conductor - Xphase | Xphase | XPHASE_CONDMOD | Float | ohms/kft | ohms/km | Phase conductor reactance for a construction model. Not used for sequence impedance model. | DPF | 0 | FALSE | 0.001 | 10 | 0.03937 | 393.7 | XPHASE
32 | Conductor Model | Conductor - Diameter | Diameter | DIAMETER_CONDMOD | Float | inches | millimeters | Diameter of the conductor for a construction model. Not used for sequence impedance model. | DPF |  | TRUE | 0.01 | 10 | 0.254 | 254 | DIAMETER
33 | Conductor Model | Conductor - GmRphase | GmRphase | GMRPHASE_CONDMOD | Float | feet | millimeters | Phase conductor geometric mean radius. Needed for both construction and sequence impedance models. | DPF |  | TRUE | 0.001 | 10 | 0.3048 | 3048 | GMRPHASE
34 | Conductor Model | Conductor - PhDist | PhDist | PHDIST_CONDMOD | Float | inches | millimeters | Phase conductor spacing for a three conductor cable for a construction model. Not used for sequence impedance model. | DPF | Required for cables. | FALSE | 0.001 | 10 | 0.0254 | 254 | PHDIST
35 | Conductor Model | Conductor - Insulation | Insulation | INSULATION_CONDMOD | Integer | enumeration | enumeration | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). Not used for a sequence impedance model. | DPF |  | FALSE | 1 | 8 | 1 | 8 | INSULTYP
36 | Conductor Model | Conductor - ShieldThick | ShieldThick | SHIELDTHICK_CONDMOD | Float | inches | millimeters | Shield thickness for a non-concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for tape shielded cables. | FALSE | 0.001 | 1 | 0.0254 | 25.4 | SHDTHICK
37 | Conductor Model | Conductor - Diam. Shield | DIAMShield | DIAMSHIELD_CONDMOD | Float | inches | millimeters | Outside diameter over the shield for a non-concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for tape shielded cables. | FALSE | 0.1 | 10 | 2.54 | 254 | OUTDIAM
38 | Conductor Model | Conductor - Rneutral | Rneutral | RNEUTRAL_CONDMOD | Float | ohms/kft | ohms/km | Neutral conductor resistance for a concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for cable. | FALSE | 0.001 | 100 | 0.0032808 | 328.084 | RNEUTRAL
39 | Conductor Model | Conductor - GmRneutral | GmRneutral | GMRNEUT_CONDMOD | Float | feet | millimeters | Neutral conductor bundle self geometric mean radius for a concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for cable. | FALSE | 0.001 | 1 | 0.3048 | 304.8 | GMRNEUT
40 | Conductor Model | Conductor - NeutDist | NeutDist | NEUTDIST_CONDMOD | Float | inches | milimeters | Center to neutral conductor spacing for a concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for cable. | FALSE | 0.01 | 10 | 0.254 | 254 | NEUTDIST
41 | Conductor Model | Conductor - Number of Strands | NumStrands | NUMSTRANDS_CONDMOD | Integer | count | count | The number of concentric neutral strands for a concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for cable. | FALSE | 1 | 100 | 1 | 100 | STRNDCNT
42 | Conductor Model | Conductor - Diam. Neutral | Diamneutral | DIAMNEUTRAL_CONDMOD | Float | inches | milimeter | Diameter of a concentric neutral strand for a concentric neutral cable for a construction model. Not used for sequence impedance model. | DPF | Required for cable. | FALSE | 0.01 | 1 | 0.254 | 25.4 | STRNDIAM
43 | Conductor Model | Conductor - Cable Type | CableType | CABLETYPE_CONDMOD | Integer | enumeration | enumeration | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three-conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three-conductor concentric neutral cable, 5 = Secondary cable. Used for a construction model. Not used for sequence impedance model. | DPF |  | FALSE | 0 | 5 | 0 | 5 | CONDTYPE
44 | Conductor Model | Conductor - SustfRate | SustfRate | SUSTFRATE_CONDMOD | Float | failures/kft-year | failures/km-year | Default sustained failure rate. | DPF |  | FALSE | 0 | 100 | 0 | 100 | PRMFRATE
45 | Conductor Model | Conductor - MomfRate | MomfRate | MOMFRATE_CONDMOD | Float | failures/kft-year | failures/km-year | Default momentary failure rate. | DPF |  | FALSE | 0 | 100 | 0 | 100 | TMPFRATE
46 | Conductor Model | Conductor - MTTR | MTTR | MTTR_CONDMOD | Float | hours | hours | Default mean time to repair. | DPF |  | FALSE | 0 | 500 | 0 | 500 | REPTIME
47 | Conductor Model | Conductor - SmallDisp? | SmallDisp | SMALLDISP_CONDMOD | Boolean | #N/A | #N/A | Flag indicating that a small conductor type has been found – used for displaying lines (true = small conductor). This field is no longer supported. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | SMALDISP
48 | Conductor Model | Conductor - AmpDerateSched | AmpDerateSched | AMPDERATESCHED_CONDMOD | String | #N/A | #N/A | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is optional. | DPF | The schedule name must match a schedule listed in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | AMPSCHED
49 | Conductor Model | Conductor - TypeDesc | TypeDesc | TYPEDESC_CONDMOD | String | #N/A | #N/A | Conductor type (copper, aluminum. other). This is a display only field. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | STRCTYPE
50 | Conductor Model | Conductor - SizeDesc | SizeDesc | SIZEDESC_CONDMOD | String | #N/A | #N/A | Conductor size (568, 1.0, other). This is a display only field. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | CONDSIZE
51 | Conductor Model | Conductor - CnstType | CnstType | CNSTTYPE_CONDMOD | Integer | enumeration | enumeration | Construction type enumeration. This enumeration has the following vales: 0 = Overhead, 1 = Direct Buried; 2 = In Conduit. Used for a construction model. Not used for sequence impedance model. | DPF |  | FALSE | 0 | 2 | 0 | 2 | CONDCNST
52 | Conductor Model | #N/A | R1 | R1_CONDMOD | Float | ohms/kft | ohms/km | Positive sequence resistance. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 10 | 0 | 32.8084
53 | Conductor Model | #N/A | X1 | X1_CONDMOD | Float | ohms/kft | ohms/km | Positive sequence reactance based on a 1 foot conductor spacing. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 10 | 0 | 32.8084
54 | Conductor Model | #N/A | R0 | R0_CONDMOD | Float | ohms/kft | ohms/km | Zero sequence resistance. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 30 | 0 | 98.4252
55 | Conductor Model | #N/A | X0 | X0_CONDMOD | Float | ohms/kft | ohms/km | Zero sequence reactance based on a 1 foot conductor spacing. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 30 | 0 | 98.4252
56 | Conductor Model | #N/A | B1 | B1_CONDMOD | Float | microSiemens/kft | microSiemens/km | Positive sequence shunt admittance. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 100 | 0 | 328.084
57 | Conductor Model | #N/A | B0 | B0_CONDMOD | Float | microSiemens/kft | microSiemens/km | Zero sequence shunt admittance. Used for sequence impedance model. Not used for a construction model (the preferred approach). | DPF |  | FALSE | 0 | 100 | 0 | 328.084
58 | Conductor Model | #N/A | #N/A | NUMOPLIMIT_CONDMOD | Integer | count | count | The number of operational limits. | DPF | Required for limit monitoring. | FALSE | 0 | 20 | 0 | 20 | NUMLIMIT
59 | Conductor Model | Conductor - Oplimits Name | Name | OPLIMITNAMEn_CONDMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). | DPF | Required for limit monitoring. | FALSE | #N/A | #N/A | #N/A | #N/A | LIMNAME
60 | Conductor Model | Conductor - Oplimits Unit | Unit | OPLIMITUNITn_CONDMOD | Integer | enumeration | enumeration | Enumerated limit units. The enumeration has the following values: 1 = amps, 2 = kVA. | DPF | Required for limit monitoring. | FALSE | 1 | 2 | 1 | 2 | LIMUNIT
61 | Conductor Model | Conductor - Oplimits Limit | Limit | OPLIMITn_CONDMOD | Float | amps or kVA | amps or kVA | The value of the limit. | DPF | Required for limit monitoring. | FALSE | 1.00/0.01 | 7600.0/200,000.0 | 1.00/0.01 | 7600.0/200,000.0 | LIMVALUE
62 | Conductor Model | Conductor - Oplimits Season | Season | OPLIMITSEASONn_CONDMOD | String | #N/A | #N/A | The name of an associated season when the limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. Required for limit monitoring. | FALSE | #N/A | #N/A | #N/A | #N/A | LIMSEAS
63 | Conductor Model | Conductor - Oplimits TempSched | TempSched | OPLIMITSCHEDn_CONDMOD | String | #N/A | #N/A | The name of an associated temperature based ampacity schedule (optional). | DPF | The name of the season must match a season given in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | TEMPSCHED
64 | Conductor Model | Limit Event | LimitEvent | OPLIMITEVENTn_CONDMOD | Boolean | #N/A | #N/A | Flag indicating a SCADA alarm is issued by the Dsitribution Power Flow when there is a violation of this limit (True = issue alarm). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENT
65 | Construction Model | Name | Name | NAME_CNSTMOD | String | #N/A | #N/A | Unique construction model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
66 | Construction Model | Construction – Voltage | Voltage | VOLTAGE_CNSTMOD | Integer | kV | kV | Voltage class (15 kV, 25 kV, other). | DPF |  | TRUE | 1 | 500 | 1 | 500 | rVoltage
67 | Construction Model | Ground Spacing | GRNDSPACING | GRNDSPACING_CNSTMOD | Float | feet | meter | Maximum ground pole spacing. This field is used in determining the neutral conductor current flow. | DPF | Field is optional. | FALSE | 0 | 1000 | 0 | 304.8 | rGrndSpacing
68 | Construction Model | Ground Resistance | GRNDRESISTANCE | GRNDRESISTANCE_CNSTMOD | Float | ohms | ohms | Grounding resistance. This field is used in determining the neutral conductor current flow. | DPF | Field is optional. | FALSE | 0 | 200 | 0 | 200 | rGrndResistance
69 | Construction Model | Construction - OHUG Flag | OHUGFlag | OHUGFLAG_CNSTMOD | Boolean | #N/A | #N/A | Flag indicating overhead vs. underground construction (True = overhead). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | bOverhead
70 | Construction Model | Construction - Xa Coordinate | XaCoord | XACOORD_CNSTMOD | Float | feet | meter | X coordinate for conductor in position 1 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this X coordinate is for Phase C. | DPF | Required for proper DPF solution. | FALSE | -50 | 50 | -15.24 | 15.24 | rXPhaseA
71 | Construction Model | Construction - Ya Coordinate | YaCoord | YACOORD_CNSTMOD | Float | feet | meter | Y coordinate for conductor in position1 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this Y coordinate is for Phase C. | DPF | Required for proper DPF solution. | FALSE | -20 | 100 | -6.096 | 30.48 | rYPhaseA
72 | Construction Model | Construction - Xb Coordinate | XbCoord | XBCOORD_CNSTMOD | Float | feet | meter | X coordinate for conductor in position 2 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this X coordinate is for Phase A. | DPF | Required for proper DPF solution. | FALSE | -50 | 50 | -15.24 | 15.24 | rXPhaseB
73 | Construction Model | Construction - Yb Coordinate | YbCoord | YBCOORD_CNSTMOD | Float | feet | meter | Y coordinate for conductor in position 2 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this Y coordinate is for Phase A. | DPF | Required for proper DPF solution. | FALSE | -20 | 100 | -6.096 | 30.48 | rYPhaseB
74 | Construction Model | Construction - Xc Coordinate | XcCoord | XCCOORD_CNSTMOD | Float | feet | meter | X coordinate for conductor in position 3 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this X coordinate is for Phase B. | DPF | Required for proper DPF solution. | FALSE | -50 | 50 | -15.24 | 15.24 | rXPhaseC
75 | Construction Model | Construction - Yc Coordinate | YcCoord | YCCOORD_CNSTMOD | Float | feet | meter | Y coordinate for conductor in position 3 (vertical coordinate). The phase value string given for the Line object in the station external file is an ordered set of phases. For example, if the Line object Phase (or PHASE_LINE) value is CABN, then this Y coordinate is for Phase B. | DPF | Required for proper DPF solution. | FALSE | -20 | 100 | -6.096 | 30.48 | rYPhaseC
76 | Construction Model | Construction - Xn Coordinate | XnCoord | XNCOORD_CNSTMOD | Float | feet | meter | X coordinate for the neutral conductor (vertical coordinate). | DPF | Required for proper DPF solution. | FALSE | -50 | 50 | -15.24 | 15.24 | rXPhaseN
77 | Construction Model | Construction - Yn Coordinate | YnCoord | YNCOORD_CNSTMOD | Float | feet | meter | Y coordinate for the neutral conductor (vertical coordinate). | DPF | Required for proper DPF solution. | FALSE | -20 | 100 | -6.096 | 30.48 | rYPhaseN
78 | Day Type | Name | Name | NAME_DAYTYPE | String | #N/A | #N/A | Unique day type name (Weekday, Weekend, Holiday 1, …). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
79 | Day Type | Description | Desc | DESC_DAYTYPE | String | #N/A | #N/A | Description of the day type. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | DESC
80 | Day Type | Day of Week | DayofWeek | NUMDAYOFWEEK_DAYTYPE | Integer | count | count | The number of days of the week. | DPF |  | FALSE | 0 | 7 | 0 | 7 | NAME
81 | Day Type | #N/A | Day | DAYOFWEEK_DAYTYPE | Integer | count | count | The days of the week represented as an integer: (0 = Sunday, 1 = Monday, 2 = Tuesday, 3 = Wednesday, 4 = Thursday, 5 = Friday, and 6 = Saturday). | DPF |  | FALSE | 0 | 6 | 0 | 6 | DAYOFWEEK
82 | Day Type | Calendar Day | CalendarDay | NUMCALENDARDAY_DAYTYPE | Integer | count | count | The number of calendar days (such as for specific holidays or other special days). | DPF |  | FALSE | 0 | 20 | 0 | 20 | NUMCALENDARDAY
83 | Day Type | #N/A | Cday | CALENDARDAY_DAYTYPE | string | #N/A | #N/A | Calendar day (format is month/day/year format). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | Cday
84 | Energy Resource Model | Name | Name | NAME_ENERGYRESMOD | String | #N/A | #N/A | Unique energy resource model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
85 | Energy Resource Model | Voltage units. 1 = Per unit voltage, 2 = Actual voltage | VoltUnits | VOLTUNITS_ENERGYRESMOD | Integer | enumeration | enumeration | Enumerated flag indicating the voltage units that should be used. The following values are supported: 1 = Per unit voltage, 2 = Actual voltage (on a user-configured voltage base specified in VoltageBase field). | DPF |  | TRUE | 1 | 2 | 1 | 2 | VOLTUNIT
86 | Energy Resource Model | Voltage Base Value | VoltageBase | VOLTAGEBASE_ENERGYRESMOD | Float | V | V | Voltage base value. | DPF |  | TRUE | 10 | 45000 | 10 | 45000 | VOLTAGEBASE
87 | Energy Resource Model | Energy Resource Rating (kVA) | KVA | KVA_ENERGYRESMOD | Float | kVA | kVA | Energy resource rating. | DPF |  | TRUE | 1 | 50000 | 1 | 50000 | KVA
88 | Energy Resource Model | Rated power factor | RatedPF | RATEDPF_ENERGYRESMOD | Float | units | units | Rated power factor. | DPF |  | FALSE | -1 | 1 | -1 | 1 | RATEDPF
89 | Energy Resource Model | Maximum real power output (kW) | PgenMax | PGENMAX_ENERGYRESMOD | Float | kW | kW | Maximum real power output. | DPF |  | TRUE | 1 | 50000 | 1 | 50000 | PGENMAX
90 | Energy Resource Model | Minimum real power output (kW) | PgenMin | PGENMIN_ENERGYRESMOD | Float | kW | kW | Minimum real power output. | DPF |  | TRUE | -50000 | 50000 | -50000 | 50000 | PGENMIN
91 | Energy Resource Model | The maximum reactive power output (kVAR) | QgenMax | QGENMAX_ENERGYRESMOD | Float | kVAR | kVAR | The maximum reactive power output. | DPF |  | TRUE | -50000 | 50000 | -50000 | 50000 | QGENMAX
92 | Energy Resource Model | The minimum reactive power output (kVAR) | QgenMin | QGENMIN_ENERGYRESMOD | Float | kVAR | kVAR | The minimum reactive power output. | DPF |  | TRUE | -50000 | 50000 | -50000 | 50000 | QGENMIN
93 | Energy Resource Model | Output capability curve schedule | PoutCapCurve | PCAPSCHED_ENERGYRESMOD | String | #N/A | #N/A | Energy resource piecewise linear capability curve (modeled using a schedule with real power value on the horizontal axis, and the reactive power values on the vertical axis.). | DPF | The name must match a schedule given in the file. Optional. | TRUE | #N/A | #N/A | #N/A | #N/A | CAPCURVESCHED.NAME
94 | Energy Resource Model | The operational cost of switching on/off a generator | SwitchCost | SWITCOST_ENERGYRESMOD | Float | units | units | The operational cost of switching on/off a generator. | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | SWCOST
95 | Energy Resource Model | Allow low voltage ride-through | AllowLVRT | ALLOWLVRT_ENERGYRESMOD | Boolean | #N/A | #N/A | Flag indicating device has low voltage ride-through capability (True = device has ride through capability). DEPRECATED | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A
96 | Energy Resource Model | Allow Contributes To Fault Current | AllowContributeToFault | ALLOWCONTRIBUTETOFAULT_ENERGYRESMOD | Boolean | #N/A | #N/A | Flag indicating device will contribute to fault current during SSC or PRV | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | CONFAULTCURR
97 | Energy Resource Model |  |  | RATEDPF_ENERGYRESMOD | Float | #N/A | #N/A | DPF rate | DPF |  |  | #N/A | #N/A | #N/A | #N/A
98 | Energy Resource Model | LVRT upper voltage limit | VHighLimit | VHIGHLIMIT_ENERGYRESMOD | Float | per unit | per unit | LVRT upper voltage limit. | DPF |  | TRUE | 1.1 | 1.5 | 1.1 | 1.5 | VHIGHLIMIT
99 | Energy Resource Model | LVRT low voltage limit | VLowLimit | VLOWLIMIT_ENERGYRESMOD | Float | per unit | per unit | LVRT low voltage limit. | DPF |  | TRUE | 0.1 | 0.9 | 0.1 | 0.9 | VLOWLIMIT
100 | Energy Resource Model | Short circuit resistance (per unit) | RSC | RSC_ENERGYRESMOD | Float | per unit | per unit | Short circuit resistance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | RSC
101 | Energy Resource Model | Short circuit reactance (per unit) | XSC | XSC_ENERGYRESMOD | Float | per unit | per unit | Short circuit reactance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | XSC
102 | Energy Resource Model | Zero sequence resistance (per unit) | R0 | R0_ENERGYRESMOD | Float | per unit | per unit | Zero sequence resistance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | RZERO
103 | Energy Resource Model | Zero sequence reactance (per unit) | X0 | X0_ENERGYRESMOD | Float | per unit | per unit | Zero seqeunce reactance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | XZERO
104 | Energy Resource Model | Negative sequence resistance (per unit) | R2 | R2_ENERGYRESMOD | Float | per unit | per unit | Negative sequence resistance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | RNEG
105 | Energy Resource Model | Negative sequence reactance (per unit) | X2 | X2_ENERGYRESMOD | Float | per unit | per unit | Negative seqeunce reactance. | DPF |  | TRUE | 0.001 | 5 | 0.001 | 5 | XNEG
106 | Energy Resource Model |  | NumSched | NUMOPSCHED_ENERGYRESMOD | Integer | units | units | The number of statically defined operating schedules (P, Q, V). The dynamic schedule function, the ability to read schedules in from an external source, is also supported in the DMS. DEPRECATED | DPF |  | FALSE | 0 | 100 | 0 | 100 | NUMOPSCHEDS
107 | Energy Resource Model |  | OpScheduleName | OPSCHEDn_ENERGYRESMOD | String | #N/A | #N/A | The name of statically defined operating schedules (P, Q, V).
108 | Energy Resource Model |  | Schedule | SCHEDn_ENERGYRESMOD | String | #N/A | #N/A | The name of an operating schedule.DEPRECATED | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | TBD
109 | Energy Resource Model |  | PlannedRestorationTime | PLANNEDRESTORATIONTIME_ENERGYRESMOD | Integer | second | second | Planned restoration time after re-energization of the feeder. | DPF |  | FALSE |  |  |  |  | PLANNEDRESTORATIONTIME
110 | Energy Resource Model |  | NumSCVoltageRanges | NUMSCVOLTAGERANGES_ENERGYRESMOD | short |  |  | The number of voltage ranges and their associated fault current level | DPF |  | TRUE |  |  |  |  | NUMSCVOLTAGERANGES
111 | Energy Resource Model |  | HIGHVOLTRANGE | HIGHVOLTRANGEn_ENERGYRESMOD | Integer | per unit | per unit | High voltage value (per unit V) | DPF |  | TRUE |  |  |  |  | HIGHVOLTRANGES
112 | Energy Resource Model |  | LOWVOLTRANGE | LOWVOLTRANGEn_ENERGYRESMOD | Integer | per unit | per unit | Low voltage value (per unit V) | DPF |  | TRUE |  |  |  |  | LOWVOLTRANGES
113 | Energy Resource Model |  | SCCURRENTLEVEL | SCCURRENTLEVELn_ENERGYRESMOD | Integer |  |  | Fault current as a rated multiplier of the rated output | DPF |  | TRUE |  |  |  |  | SCCURRENTLEVELS
114 | Energy Resource Program Definition |  | Name | NAME_ENERGYRESPROGRAMDEF | String | #N/A | #N/A | Unique program enrollment name. |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
115 | Energy Resource Program Definition |  | ProgramName | PROGRAMNAME_ENERGYRESPROGRAMDEF | String | #N/A | #N/A | Specific program name. |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PROGRAMNAME
116 | Energy Resource Program Definition |  | Enrollment | ENROLLMENT_ENERGYRESPROGRAMDEF | Integer | #N/A | #N/A | Integer representing a program number which is used to link an Energy Resource object to one or more Energy Resource Programs. |  |  | TRUE | 1 | 63 | 1 | 63 | ENROLLMENT
117 | Energy Resource Program Definition |  | ProgramType | PROGRAMTYPE_ENERGYRESPROGRAMDEF | String | #N/A | #N/A | Program type description. |  |  | TRUE | #N/A | #N/A | #N/A | #N/A | PROGRAMTYPE
118 | Enumeration Table Model | Enum Device Type | EnumDevice | DEVICE_ENUM | String | #N/A | #N/A | The device enumeration type. The following values are supported: SWTYPE - set in SWTYPE_SWMOD field in the Switch Model CABINETTYPE - set in TYPE_SWCAB field in the Switch Cabinet object (external file) VAULTYPE - set in TYPE_VAULT field in the Vault object (external file) RELAYTYPE - set in field TYPE_OCRELAY in the Time Overcurrent Rrelay object (internal or external file) GENERATIONTYPE - set in the GENTYPE_LOAD field in the Load object (external file) LOADTYPE - set in the TYPE_LOAD field in the Load object (external file) CNSTTYPE_CONDMOD - set in field CNSTTYPE_CONDMOD in the Conductor model object. TFCONSTTYPE - set in field CNSTTYPE_TF in the Transformer object (internal or external file) | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | DEVICE
119 | Enumeration Table Model | Value of Enums Type | TypeValue | TYPEVALUE_ENUM | Integer | enumeration | enumeration | The integer value for a specific device type. | OPS |  | FALSE |  |  |  |  | TYPEVALUE
120 | Enumeration Table Model | #N/A | Description | DESCRIPTION_ENUM | String | #N/A | #N/A | The text description of the specific device type. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | DESCRIPTION
121 | Generator Model |  | PlannedRestorationTime | PLANNEDRESTORATIONTIME_GENMOD | Integer | second | second | Planned restoration time after re-energization of the feeder. | DPF |  | FALSE |  |  |  |  | PLANNEDRESTORATIONTIME
122 | Generator Model | Name | Name | NAME_GENMOD | String | #N/A | #N/A | Unique generator model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
123 | Generator Model | Direct axis synchronous resistance (per unit) | RD | RD_GENMOD | Float | per unit | per unit | Direct axis synchronous resistance. | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | RDSYNC
124 | Generator Model | Direct axis synchronous reactance (per unit). | XD | XD_GENMOD | Float | per unit | per unit | Direct axis synchronous reactance. | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | XDSYNC
125 | Generator Model | Quadrature axis synchronous resistance (per unit). | RQ | RQ_GENMOD | Float | per unit | per unit | Quadrature axis synchronous resistance. | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | RQSYNC
126 | Generator Model | Quadrature axis synchronous reactance (per unit). | XQ | XQ_GENMOD | Float | per unit | per unit | Quadrature axis synchronous reactance. | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | XQSYNC
127 | Generator Model | Direct axis transient resistance (per unit) | RDPrime | RDPRIME_GENMOD | Float | per unit | per unit | Direct axis transient resistance (per unit). | DPF |  | TRUE | 0.001 | 5 | 0.1 | 5 | RDPRIM
128 | Generator Model | Direct axis transient reactance (per unit) | XDPrime | XDPRIME_GENMOD | Float | per unit | per unit | Direct axis transient reactance (per unit). | DPF |  | TRUE | 0.001 | 5 | 0.1 | 5 | XDPRIM
129 | Generator Model | Quadrature axis transient resistance (per unit) | RQPrime | RQPRIME_GENMOD | Float | per unit | per unit | Quadrature axis transient resistance (per unit). | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | RQPRIM
130 | Generator Model | Quadrature axis transient reactance (per unit) | XQPrime | XQPRIME_GENMOD | Float | per unit | per unit | Quadrature axis transient reactance (per unit). | DPF |  | TRUE | 0.1 | 5 | 0.1 | 5 | XQPRIM
131 | Generator Model | Direct axis subtransient resistance (per unit). | RDDPrime | RDDPRIME_GENMOD | Float | per unit | per unit | Direct axis subtransient resistance. | DPF |  | TRUE | 0.001 | 2 | 0.01 | 2 | RDSUB
132 | Generator Model | Direct axis subtransient reactance (per unit). | XDDPrime | XDDPRIME_GENMOD | Float | per unit | per unit | Direct axis subtransient reactance. | DPF |  | TRUE | 0.001 | 2 | 0.01 | 2 | XDSUB
133 | Generator Model | Quadrature axis subtransient resistance (per unit). | RQDPrime | RQDPRIME_GENMOD | Float | per unit | per unit | Quadrature axis subtransient resistance. | DPF |  | TRUE | 0.01 | 2 | 0.01 | 2 | RQSUB
134 | Generator Model | Quadrature axis subtransient reactance (per unit). | XQDPrime | XQDPRIME_GENMOD | Float | per unit | per unit | Quadrature axis subtransient reactance. | DPF |  | TRUE | 0.01 | 2 | 0.01 | 2 | XQSUB
135 | Generator Model | Negative sequence resistance (per unit) | R2 | R2_GENMOD | Float | per unit | per unit | Negative sequence resistance (per unit). | DPF |  | TRUE | 0.001 | 2 | 0.01 | 2 | R2
136 | Generator Model | Negative sequence reactance (per unit) | X2 | X2_GENMOD | Float | power factor | power factor | Negative sequence reactance (per unit). | DPF |  | TRUE | 0.01 | 2 | 0.01 | 2 | X2
137 | Generator Model | Zero sequence resistance (per unit). | R0 | R0_GENMOD | Float | per unit | per unit | Zero sequence resistance. | DPF |  | TRUE | 0.0001 | 2 | 0.01 | 2 | RZERO
138 | Generator Model | Zero sequence reactance (per unit). | X0 | X0_GENMOD | Float | per unit | per unit | Zero sequence reactance. | DPF |  | TRUE | 0.001 | 2 | 0.01 | 2 | XZERO
139 | Generator Model | Generator rating (kVA). | KVA | KVA_GENMOD | Float | kVA | kVA | Generator rating. | DPF |  | TRUE | 1 | 50000 | 1 | 50000 | KVA
140 | Generator Model | Maximum real power output (kW). | PgenMax | PGENMAX_GENMOD | Float | kW | kW | The maximum real power output. | DPF |  | TRUE | 1 | 50000 | 1 | 50000 | PGENMAX
141 | Generator Model | Minimum real power output (kW). | PgenMin | PGENMIN_GENMOD | Float | kW | kW | The minimum real power output. | DPF |  | TRUE | 1 | 5000 | 1 | 5000 | PGENMIN
142 | Generator Model | The maximum reactive power output (kVAR). | QgenMax | QGENMAX_GENMOD | Float | kVAR | kVAR | The maximum reactive power output. | DPF |  | TRUE | -50000 | 50000 | -50000 | 50000 | QGENMAX
143 | Generator Model | The minimum reactive power output (kVAR). | QgenMin | QGENMIN_GENMOD | Float | kVAR | kVAR | The minimum reactive power output. | DPF |  | TRUE | -50000 | 50000 | -50000 | 50000 | QGENMIN
144 | Generator Model | Generator capability curve schedule | GenCapCurve | CAPSCHED_GENMOD | String | #N/A | #N/A | Generator piecewise linear capability curve (modeled using a schedule with real power value on the horizontal axis, and the reactive power values on the vertical axis.). | DPF | The name must match a schedule given in the file. Optional. | TRUE | #N/A | #N/A | #N/A | #N/A | CAPCURVESCHED.NAME
145 | Generator Model | The operational cost of switching on/off a generator. | SwitchCost | SWITCOST_GENMOD | Float | units | units | The operational cost of switching the device on or off. This relative cost is used in the Load and Vvolt/VAR Management (LVM) application. | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | SWCOST
146 | Generator Model | Voltage units. 1 = Per unit voltage, 2 = Actual voltage | VoltUnits | VOLTUNITS_GENMOD | Integer | enumeration | enumeration | Enumerated flag indicating the voltage units that are used. The following values are supported: 1 = Per unit voltage, 2 = Actual voltage (on a user-configured voltage base specified in VoltageBase field). | DPF |  | FALSE | 1 | 2 | 1 | 2 | VOLTUNIT
147 | Generator Model | Voltage Base Value | VoltageBase | VOLTAGEBASE_GENMOD | Float | V | V | Voltage base value. | DPF |  | FALSE | 10 | 45000 | 10 | 45000 | VOLTAGEBASE
148 | Generator Model |  | NumSched | NUMOPSCHED_GENMOD | String | #N/A | #N/A | The number of statically defined operating schedules (P, Q, V). The "dynamic schedule" function is also supported in the DMS (the ability to read schedules in from an external source). DEPRECATED | DPF | Optional. Multiple schedule definition is optional therefore the default value is 0 (no schedules). In this case the Schedule (OpScheduleName) field is not filled in. | TRUE | 0 | 100 | 0 | 100 | NUMOPSCHEDS
149 | Generator Model |  | OpScheduleName | OPSCHEDn_GENMODEL | String | #N/A | #N/A | The name of an operating schedule. DEPRECATED | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A
150 | Generator Model | Rated power factor | RatedPF | RATEDPF_GENMOD | Float | units | units | Rated power factor. | DPF |  | FALSE | -1 | 1 | -1 | 1 | RATEDPF
151 | Generator Model | Rated stator Amps | RatedAmps | RATEDAMPS_GENMOD | Float | Amps | Amps | Rated stator current. | DPF |  | FALSE | 1 | 1000 | 1 | 1000 | RATEDAMPS
152 | Inverter Model |  | AMPRATING | AMPRATING_INVERTERMOD | Float | RMS Amps | RMS Amps | The maximum nameplate AC current level of the DER (RMS Amps). | DPF |  | TRUE | 0 | 500 | 0 | 500 | AMPRATING
153 | Inverter Model | Decs | DESCRIPTION | DESC_INVERTERMOD | String |  |  | Description of the inverter model | DPF |  | FALSE |  |  |  |  | DESCRIPTION
154 | Inverter Model |  | DISCONNECTCAPABILITY | DISCONNECTCAPABILITY_INVERTERMOD | Integer | enumeration | enumeration | The inverter disconnect capability enumeration. The following values are supported: 1 = Physical - isolation between the inverter and the grid 2 = Virtual - real and reactive power output are set to 0 3 = Physical and Virtual 4 = None | DPF |  | FALSE |  |  |  |  | DISCONNECTCAPABILITY
155 | Inverter Model |  | DISCREVERSIONTIMEOUT | DISCREVERSIONTIMEOUT_INVERTERMOD | Integer | second | second | ime after which a command to disconnect expires and the device is able to reconnect (sec). A value of 0 means there is no timeout. | DPF |  | TRUE | 0 | 60 | 0 | 60 | DISCREVERSIONTIMEOUT
156 | Inverter Model |  | LIMITTIMEWINDOW | LIMITTIMEWINDOW_INVERTERMOD | Integer | second | second | A time over which a new setting is taking place (sec). For example, if the time window is set to 60 seconds, then the DER would delay a random time between 0 and 60 seconds prior to the new setting taking effect. This setting is provided to accommodate communication systems that might address large numbers of devices in groups. (Optional) | DPF |  | TRUE | 0 | 60 | 0 | 60 | LIMITTIMEWINDOW
157 | Inverter Model |  | NUMDYNREACMODES | NUMDYNREACFUNCTION_INVERTERMOD | Integer |  |  | The number of Dynamic Reactive Current Support modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMDYNREACMODES
158 | Inverter Model |  | NUMDYNVLTWMODES | NUMDYNVLTWFUNCTION_INVERTERMOD | Integer |  |  | The number of Dynamic Volt-Watt modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMDYNVLTWMODES
159 | Inverter Model |  | NUMFREQWATTMODES | NUMFREQWATTFUNCTION_INVERTERMOD | Integer |  |  | The number of Freq-Watt modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMFREQWATTMODES
160 | Inverter Model |  | NUMHFRTMODES | NUMHFRTFUNCTION_INVERTERMOD | Integer |  |  | The number of High Frequency Ride Through modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMHFRTMODES
161 | Inverter Model |  | NUMHVRTMODES | NUMHVRTFUNCTION_INVERTERMOD | Integer |  |  | The number of High Voltage Ride Through modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMHVRTMODES
162 | Inverter Model |  | NUMLFRTMODES | NUMLFRTFUNCTION_INVERTERMOD | Integer |  |  | The number of Low Frequency Ride Through modes/curves configured in the inverter | DPF |  | FALSE |  |  |  |  | NUMLFRTMODES
163 | Inverter Model |  | NUMLVRTMODES | NUMLVRTFUNCTION_INVERTERMOD | Integer |  |  | The number of Low Voltage Ride Through modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMLVRTMODES
164 | Inverter Model |  | NUMVOLTVARMODES | NUMVOLTVARFUNCTION_INVERTERMOD | Integer |  |  | The number of Volt-VAR modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMVOLTVARMODES
165 | Inverter Model |  | NUMVOLTWATTMODES | NUMVOLTWATTFUNCTION_INVERTERMOD | Integer |  |  | The number of Volt-Watt modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMVOLTWATTMODES
166 | Inverter Model |  | SupportsFixedPowerFactorModes | SUPPORTSFIXEDPOWERFACTORMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Fixed Power Factor modes (true = does support Fixed Power Factor modes/curves). | DPF |  | FALSE |  |  |  |  | SPTFIXEDPFMODES
167 | Inverter Model |  | NumFixedPowerFactorModes | NUMFIXEDPOWERFACTORFUNCTION_INVERTERMOD | Integer |  |  | The number of Fixed Power Factor modes/curves configured in the inverter. | DPF | [6 empty] | NUMFIXEDPFMODES
168 | Inverter Model |  | SupportsMaxPowerLimitingModes | SUPPORTSMAXPOWERLIMITINGMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Maximum Power Limiting modes (true = does support Maximum Power Limiting modes/curves). | DPF |  | FALSE |  |  |  |  | SPTMAXPOWERLIMITINGMODES
169 | Inverter Model |  | NumMaxPowerLimitingModes | NUMMAXPOWERLIMITINGFUNCTION_INVERTERMOD | Integer |  |  | The number of Maximum Power Limiting modes/curves configured in the inverter. | DPF | [6 empty] | NUMMAXPOWERLIMITINGMODES
170 | Inverter Model |  | NUMWATTPFMODES | NUMWATTPFFUNCTION_INVERTERMOD | Integer |  |  | The number of Watt-Power Factor modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMWATTPFMODES
171 | Inverter Model |  | NUMWATTVARMODES | NUMWATTVARFUNCTION_INVERTERMOD | Integer |  |  | The number of Watt-Power Factor modes/curves configured in the inverter. | DPF |  | FALSE |  |  |  |  | NUMWATTVARMODES
172 | Inverter Model |  | PEAKPOWERLIMIT | PEAKPOWERLIMIT_INVERTERMOD | Float | W | W | The peak power target power level limit (Watts). | DPF |  | TRUE | 0 | 1000 | 0 | 1000 | PEAKPOWERLIMIT
173 | Inverter Model |  | PFREVERSIONTIMEOUT | PFREVERSIONTIMEOUT_INVERTERMOD | Integer | second | second | Time after which a DER will return to its default power factor setting (sec). A value of 0 means there is no timeout. | DPF |  | TRUE | 0 | 60 | 0 | 60 | PFREVERSIONTIMEOUT
174 | Inverter Model |  | POWERFACTORTYPE | POWERFACTORTYPE_INVERTERMOD | Integer | enumeration | enumeration | An enumeration to identify how the power factor setting is to be interpreted. The enumeration has the following values: 1 = IEC Convention - supplying or generating active power is positive and demanding active power is negative (quadrants 2 and 3 have negative power factor, quadrants 1 and 4 have a positive power factor). 2 = IEEE Convention - leading(capacitive) power factor is positive and a lagging(inductive) power factor is negative" | DPF |  | FALSE |  |  |  |  | POWERFACTORTYPE
175 | Inverter Model |  | SHORTCIRCUITRATING | SHORTCIRCUITRATING_INVERTERMOD | Float |  |  | The short circuit rating specified as a multiplier of the nameplate AC rating (typically between 2 - 5 times). Range is from 0.0 to 15.0 (floating point value). | DPF |  | TRUE | 0 | 15 | 0 | 15 | SHORTCIRCUITRATING
176 | Inverter Model |  | SupportsDynReacModes | SUPPORTSDYNREACMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Dynamic Reactive Current Support modes (true = does support Dynamic Reactive Current Support modes/curves). | DPF |  | FALSE |  |  |  |  | SPTDYNREACMODES
177 | Inverter Model |  | SupportsDynVltWModes | SUPPORTSDYNVLTWMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Dynamic Volt-Watt modes (true = does support Dynamic Volt-Watt modes/curves). | DPF |  | FALSE |  |  |  |  | SPTDYNVLTWMODES
178 | Inverter Model |  | SupportsFreqWattModes | SUPPORTSFREQWATTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Freq-Watt modes (true = does support Freq-Watt modes/curves). | DPF |  | FALSE |  |  |  |  | SPTFREQWATTMODES
179 | Inverter Model |  | SupportsHFRTModes | SUPPORTSHFRTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more High Frequency Ride Through modes (true = does support HFRT modes/curves). | DPF |  | FALSE |  |  |  |  | SPTHFRTMODES
180 | Inverter Model |  | SupportsHVRTModes | SUPPORTSHVRTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more High Voltage Ride Through modes (true = does support HVRT modes/curves). | DPF |  | FALSE |  |  |  |  | SPTHVRTMODES
181 | Inverter Model |  | SupportsLFRTModes | SUPPORTSLFRTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Low Frequency Ride Through modes (true = does support LFRT modes/curves). | DPF |  | FALSE |  |  |  |  | SPTLFRTMODES
182 | Inverter Model |  | SupportsLVRTModes | SUPPORTSLVRTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Low Voltage Ride Through modes (true = does support LVRT modes/curves). | DPF |  | FALSE |  |  |  |  | SPTLVRTMODES
183 | Inverter Model |  | SupportsVoltVarModes | SUPPORTSVOLTVARMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Volt-VAR modes (true = does support Volt-VAR modes/curves). The Volt-VAR autonomous function // provide a mechanism through which a DER may be configured to manage its own VAR output in response to the local service voltage. | DPF |  | FALSE |  |  |  |  | SPTVOLTVARMODES
184 | Inverter Model |  | SupportsVoltWattModes | SUPPORTSVOLTWATTMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Volt-Watt modes (true = does support Volt-Watt modes/curves). The Volt-Watt autonomous function provide a mechanism whereby an inverter system could gradually reduce its own maximum power output as the voltage at the Point of Common Coupling (PCC) exceeds a configurable, utility defined limit. | DPF |  | FALSE |  |  |  |  | SPTVOLTWATTMODES
185 | Inverter Model |  | SupportsWattPFModes | SUPPORTSWATTPFMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Watt-Power Factor modes (true = does support Watt-Power Factor modes/curves). The Watt-Power Factor autonomous mode expresses real power on the X axis (expressed as %Wmax) and the Y axis contains the controlled parameter which is power factor (expressed as a signed value greater than 0 and less than or equal to 1.0). | DPF |  | FALSE |  |  |  |  | SPTWATTPFMODES
186 | Inverter Model |  | SupportsWattVarModes | SUPPORTSWATTVARMODES_INVERTERMOD | Boolean |  |  | Inverter supports one or more Watt-VAR modes (true = does support Watt-VAR modes/curves). The Watt-VAR autonomous mode provides a mechanism through which the DER actively controls the reactive power output as a function of the real power output following a target real power reactive power curve. | DPF |  | FALSE |  |  |  |  | SPTWATTVARMODES
187 | Inverter Model |  | VACHARGEMAX | VACHARGEMAX_INVERTERMOD | Float | kVA | kVA | The maximum apparent power the DER can absorb from the grid (kVA, for energy storage charging). | DPF |  | TRUE | 0 | 500 | 0 | 500 | VACHARGEMAX
188 | Inverter Model |  | VAMAX | VAMAX_INVERTERMOD | Float | kVA | kVA | The maximum apparent power the DER can deliver to the grid (kVA). | DPF |  | TRUE | 0 | 500 | 0 | 500 | VAMAX
189 | Inverter Model |  | VARCHARGEMAX | VARCHARGEMAX_INVERTERMOD | Float | kVAR | kVAR | The maximum reactive power the DER can absorb from the grid (kVAR), for energy storage charging). | DPF |  | TRUE | 0 | 500 | 0 | 500 | VARCHARGEMAX
190 | Inverter Model |  | VARMAX | VARMAX_INVERTERMOD | Float | kVAR | kVAR | The maximum reactive power the DER can deliver to the grid (kVAR). | DPF |  | TRUE | 0 | 500 | 0 | 500 | VARMAX
191 | Inverter Model |  | VOLTREF | VOLTREF_INVERTERMOD | Float | V | V | The normal operating voltage for the DER site/service connection (V). | DPF |  | TRUE | 0 | 500 | 0 | 500 | VOLTREF
192 | Inverter Model |  | VOLTREFOFFSET | VOLTREFOFFSET_INVERTERMOD | Float | V | V | An offset voltage that represents an adjustment for this DER, relative to VRef, in Volts. VRefOfs is defined as the voltage at the ECP, relative to the PCC. For example, if the PCC VRef is 120 V, and the nominal voltage at the DERs ECP is 123 V, then VRefOfs = +3V. All inverters behind one Point of Common Coupling(PCC) have a common reference voltage, but may differ in the voltage between their own Electrical Connection Point(ECP) and the PCC due to instrumentation errors or voltage shifts within a plant.These differences can be corrected by the parameter VRefOfs that is to be applied by each inverter. | DPF |  | TRUE | 0 | 7 | 0 | 7 | VOLTREFOFFSET
193 | Inverter Model |  | WCHARGEMAX | WCHARGEMAX_INVERTERMOD | Float | kW | kW | The maximum real power the DER can absorb from the grid (kW, for energy storage charging). | DPF |  | TRUE | 0 | 500 | 0 | 500 | WCHARGEMAX
194 | Inverter Model |  | WMAX | WMAX_INVERTERMOD | Float | kW | kW | The maximum real power the DER can deliver to the grid (kW). | DPF |  | TRUE | 0 | 500 | 0 | 500 | WMAX
195 | Inverter Model | #N/A | DynReacFunctionName | DYNREACFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Dynamic Reactive Current Support function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
196 | Inverter Model | #N/A | DynVltWFunctionName | DYNVLTWFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Dynamic Volt-Watt function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
197 | Inverter Model | #N/A | FreqWattFunctionName | FREQWATTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Freq-Watt function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
198 | Inverter Model | #N/A | HFRTFunctionName | HFRTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the High Frequency Ride Through function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
199 | Inverter Model | #N/A | HVRTFunctionName | HVRTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the High Voltage Ride Through function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
200 | Inverter Model | #N/A | LFRTFunctionName | LFRTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Low Frequency Ride Through function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
201 | Inverter Model | #N/A | LVRTFunctionName | LVRTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | Inverter supports one or more Low Voltage Ride Through modes (true = does support LVRT function). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
202 | Inverter Model | #N/A | VoltVarFunctionName | VOLTVARFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Volt-VAR function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
203 | Inverter Model | #N/A | VoltWattFunctionName | VOLTWATTFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Volt-Watt function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
204 | Inverter Model | #N/A | WattPFFunctionName | WATTPFFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Watt-Power Factor function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
205 | Inverter Model | #N/A | WattVarFunctionName | WATTVARFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Watt-Power Factor function. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
206 | Inverter Model | #N/A | FixedPowerFactorFunctionName | FIXEDPOWERFACTORFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Fixed Powre Factor function. | DPF
207 | Inverter Model | #N/A | MaxPowerLimitingFunctionName | MAXPOWERLIMITINGFUNCTIONNAMEn_INVERTERMOD | String | #N/A | #N/A | The name of the Maximum Power Limiting function. | DPF
208 | Inverter_Function |  | Name | NAME_INVERTERFUNC | String |  |  | The unique inverter function name |  |  | FALSE |  |  |  |  | NAME
209 | Inverter_Function |  | Description | DESCRIPTION_INVERTERFUNC | String |  |  | Description of the Inverter Function |  |  | FALSE |  |  |  |  | DESCRIPTION
210 | Inverter_Function |  | Type | TYPE_INVERTERFUNC | String |  |  | An enumeration which specifies the type of inverter Function. |  |  | FALSE |  |  |  |  | TYPE
211 | Inverter_Function |  | ScadaMeasValue | SCADAMEASVALUE_INVERTERFUNC | Float |  |  | SCADA analog value for the inverter function | DPF
212 | Inverter_Function |  | AxisTypeX | XAXISTYPE_INVERTERFUNC | String |  |  | X axis type |  |  | FALSE |  |  |  |  | XAXISTYPE
213 | Inverter_Function |  | AxisUnitsX | XAXISUNITS_INVERTERFUNC | String |  |  | X axis units |  |  | FALSE |  |  |  |  | XAXISUNITS
214 | Inverter_Function |  | AxisTypeY | YAXISTYPE_INVERTERFUNC | String |  |  | Y axis type |  |  | FALSE |  |  |  |  | YAXISTYPE
215 | Inverter_Function |  | AxisUnitsY | YAXISUNITS_INVERTERFUNC | String |  |  | Y axis units |  |  | FALSE |  |  |  |  | YAXISUNITS
216 | Inverter_Function |  | AxisScalingType | YAXISSCALING_INVERTERFUNC | Integer |  |  | Axis scaling type 0 = None 1 = Percent Maximum Rated Active Power 2 = Percent Maximum Rated Reactive Power VARs (for Watt-VAR and Volt-VAR functions) 3 = Percent Maximum Rated Reactive Power Watts 4 = Percent Maximum Available Reactive Power Watts 5 = Percent Maximum Rated Apparent Power (for Watt-VAR function) |  |  | FALSE |  |  |  |  | AXISSCALINGTYPE
217 | Inverter_Function |  | TimeoutWindow | TIMEOUTWINDOW_INVERTERFUNC | Integer | sec | sec | Time after which the mode is disabled (sec). This timeout window begins when the mode becomes effective (as a result of a direct command or schedule). A value of zero shall be used to indicate that the setting does not expire. |  |  | FALSE |  |  |  |  | TIMEOUTWINDOW
218 | Inverter_Function |  | TimeRandomWindow | TIMERANDOMWINDOW_INVERTERFUNC | Integer | sec | sec | Delay before a new command or newly activated mode begins to take effect (sec). |  |  | FALSE |  |  |  |  | TIMERANDOMWINDOW
219 | Inverter_Function |  | RampInputUp | RAMPINPUTUP_INVERTERFUNC | Float |  |  | Ramp rate for increasing input (for storage systems only). |  |  | FALSE |  |  |  |  | RAMPINPUTUP
220 | Inverter_Function |  | RampInputDn | RAMPINPUTDN_INVERTERFUNC | Float |  |  | Ramp input down |  |  | FALSE |  |  |  |  | RAMPINPUTDN
221 | Inverter_Function |  | RampOutputUp | RAMPOUTPUTUP_INVERTERFUNC | Float |  |  | Ramp rate for increasing output. |  |  | FALSE |  |  |  |  | RAMPOUTPUTUP
222 | Inverter_Function |  | RampOutputDn | RAMPOUTPUTDN_INVERTERFUNC | Float |  |  | Ramp rate for decreasing input (for storage systems only). |  |  | FALSE |  |  |  |  | RAMPOUTPUTDN
223 | Inverter_Function |  | ApplyLowPassFilter | APPLYLOWPASSFILTER_INVERTERFUNC | Boolean |  |  | This parameter determines if a low pass filter is used for limiting the rate of change of the upper Watt limit produced by the inverter or absorbed for energy storage devices (true means filter is applied). This may be applicable to the Volt-Watt function. (Optional) |  |  | FALSE |  |  |  |  | APPLYLOWPASSFILTER
224 | Inverter_Function |  | TimeLowPassFilter | TIMECONSTANT_INVERTERFUNC | Integer |  |  | Time constant for the low pass filter (sec). (Optional) |  |  | FALSE |  |  |  |  | TIMELOWPASSFILTER
225 | Inverter_Function |  | ApplyRateOfChgLimiter | APPLYRATEOFCHANGELIMITER_INVERTERFUNC | Boolean |  |  | This parameter determines if a rising rate and falling rate are used for limiting the rate of change of the upper Watt limit produced by the inverter or absorbed for energy storage devices (true means rates are applied). This may be applicable to the Volt-Watt function. (Optional) |  |  | FALSE |  |  |  |  | APPLYRATEOFCHANGELIMITER
226 | Inverter_Function |  | RiseLimit | RISELIMIT_INVERTERFUNC | Float | W | W | The maximum rate at which the Max Watt limit may be increased in response to changes in the local voltage (WMax per second). |  |  | FALSE |  |  |  |  | RISELIMIT
227 | Inverter_Function |  | FallLimit | FALLLIMIT_INVERTERFUNC | Float | W | W | The maximum rate at which the Max Watt limit may be decreased in response to changes in the local voltage (WMax per second). |  |  | FALSE |  |  |  |  | FALLLIMIT
228 | Inverter_Function |  | RiseLimitCharge | RISELIMITCHARGE_INVERTERFUNC | Float |  |  | The maximum rate at which the Max Watt limit may be increased in response to changes in the local voltage (% of WCHARGEMAX per second). This parameter only applies to energy storage systems. |  |  | FALSE |  |  |  |  | RISELIMITCHARGE
229 | Inverter_Function |  | FallLimitCharge | FALLLIMITCHARGE_INVERTERFUNC | Float | W | W | The maximum rate at which the Max Watt limit may be decreased in response to changes in the local voltage (% of WCHARGEMAX per second). This parameter only applies to energy storage systems. |  |  | FALSE |  |  |  |  | FALLLIMITCHARGE
230 | Inverter_Function |  | MinimumDeadband | VMINIMUMDEADBAND_INVERTERFUNC | Float |  |  | This is the minimum voltage deviation relative to Vaverage (% Vref). For negative voltage deviations (voltage below the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. |  |  | FALSE |  |  |  |  | VMINIMUMDEADBAND
231 | Inverter_Function |  | MaximumDeadband | VMAXIMUMDEADBAND_INVERTERFUNC | Float |  |  | This is the maximum voltage deviation relative to Vaverage (% Vref). For positive voltage deviations (voltage above the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. |  |  | FALSE |  |  |  |  | VMAXIMUMDEADBAND
232 | Inverter_Function |  | GradientSag | GRADIENTSAG_INVERTERFUNC | Float |  |  | This is a gradient, expressed in unit-less terms of %/%, to establish the ratio by which Capacitive % VAR production is increased as %Delta-Voltage decreases below the minimum deadband voltage. |  |  | FALSE |  |  |  |  | GRADIENTSAG
233 | Inverter_Function |  | GradientSwell | GRADIENTSWELL_INVERTERFUNC | Float |  |  | This is a gradient, expressed in unit-less terms of %/%, to establish the ratio by which Inductive % VAR production is increased as %Delta-Voltage increases above the maximum deadband voltage. |  |  | FALSE |  |  |  |  | GRADIENTSWELL
234 | Inverter_Function |  | UseAlternativeGradient | USEALTERNATIVEGRADIENT_INVERTERFUNC | Boolean |  |  | Option (boolean) to enable the alternative gradient behavior (gradients trend toward zero at the center). |  |  | FALSE |  |  |  |  | USEALTERNATIVEGRADIENT
235 | Inverter_Function |  | BlockingZone | BLOCKINGZONEV_INVERTERFUNC | Float |  |  | This setting is a voltage limit (% of VRef) used to define a lower voltage boundary, below which dynamic reactive current support is not active. |  |  | FALSE |  |  |  |  | BLOCKINGZONEV
236 | Inverter_Function |  | HystBlockingZone | HYSTBLOCKINGZONEV_INVERTERFUNC | Float | p.u. | p.u. | This setting defines a hysteresis added to m_vBlockingZone in order to create a hysteresis range (% of VRef). |  |  | FALSE |  |  |  |  | HYSTBLOCKINGZONEV
237 | Inverter_Function |  | CurtailWatts | CURTAILWATTS_INVERTERFUNC | Boolean |  |  | This setting (boolean) determines whether or not Watts should be curtailed in order to produce the reactive current required by the Dynamic Reactive-Current Support function. |  |  | FALSE |  |  |  |  | CURTAILWATTS
238 | Inverter_Function |  | DynamicWattGradient | DYNAMICWATTGRADIENT_INVERTERFUNC | Float |  |  | This is a signed unit-less quantity that establishes the ratio of dynamic Watts (% WMax) to the present delta-voltage of the reference ECP (% VRef). |  |  | FALSE |  |  |  |  | DYNAMICWATTGRADIENT
239 | Inverter_Function |  | DeadbandLo | VDEADBANDLO_INVERTERFUNC | Float |  |  | Optional low voltage deadband setting (%Vref) that allow the creation of a dead-band inside which the dynamic Volt-Watt function does not produce any additional Watts. |  |  | FALSE |  |  |  |  | VDEADBANDLO
240 | Inverter_Function |  | DeadbandHi | VDEADBANDHI_INVERTERFUNC | Float |  |  | Optional high voltage deadband setting (%Vref) that allow the creation of a dead-band inside which the dynamic Volt-Watt function does not produce any additional Watts. For example, setting m_vDeadbandLo = 10 and m_vDeadbandHi = |  |  | FALSE |  |  |  |  | VDEADBANDHi
241 | Inverter_Function |  | NUMPOINTS | NUMPOINTS_INVERTERFUNC | Integer |  |  | The number of X, Y value pairs. This is a repeating field. |  |  | FALSE |  |  |  |  | NUMPOINTS
242 | Inverter_Function |  | X | Xn_INVERTERFUNC | String |  |  | Array of X axis point values. |  |  | FALSE |  |  |  |  | XPOINTS
243 | Inverter_Function |  | Y | Yn_INVERTERFUNC | String |  |  | Array of Y axis point values. |  |  | FALSE |  |  |  |  | YPOINTS
244 | Inverter_Function |  | NUMSCHEDULES | NUMSCHEDULES_INVERTERFUNC | Integer |  |  | The number of pre-programmed schedules. This is a repeating field. |  |  | FALSE |  |  |  |  | NUMSCHEDULES
245 | Inverter_Function |  | SCHEDULE | SCHEDULEn_INVERTERFUNC | String |  |  | Pointer to schedules |  |  | FALSE |  |  |  |  | SCHEDULES
246 | Load Category | Name | Name | NAME_LOADCAT | String | #N/A | #N/A | Unique load category name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
247 | Load Category | #N/A | PCostInt | PCOSTINT_LOADCAT | Float | $/kW | $/kW | Value of uninterrupted service. | DPF |  | FALSE | 0 | 6000 | 0 | 6000 | PCOSTINT
248 | Load Category | #N/A | ECostInt | ECOSTINT_LOADCAT | Float | $/kWh | $/kWh | Value of uninterrupted service. | DPF |  | FALSE | 0 | 6000 | 0 | 6000 | ECOSTINT
249 | Load Category | #N/A | BillSchedule | BILLSCH_LOADCAT | String | #N/A | #N/A | Associated billing schedule. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | BILLSCH
250 | Load Category | #N/A | Accuracy | ACCURACY_LOADCAT | Float | percent | percent | Load data accuracy/variability (percent used in determining the allocated loads, low value decreases BLA scaling while high value increases BLA scaling). | DPF |  | TRUE | 0 | 100 | 0 | 100 | ACCURACY
251 | Load Category | #N/A | LoadVoltSched1 | LOADVOLT1_LOADCAT | String | #N/A | #N/A | Associated load to voltage sensitivity coefficient schedule (coefficients A and D). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOADVOLT1
252 | Load Category | #N/A | LoadVoltSched2 | LOADVOLT2_LOADCAT | String | #N/A | #N/A | Associated load to voltage sensitivity coefficient schedule (coefficients B and E). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOADVOLT2
253 | Load Category | #N/A | LoadVoltSched3 | LOADVOLT3_LOADCAT | String | #N/A | #N/A | Associated load to voltage sensitivity coefficient schedule (coefficients C and F). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOADVOLT3
254 | Load Category | #N/A | LoadSchedules | NUMLOADSCHED_LOADCAT | Integer | count | count | Number of load schedules. | DPF |  | TRUE | 1 | 200 | 1 | 200 | NUMLOADSCHED
255 | Load Category | #N/A | DefaultPValue | DEFAULTPLOAD_LOADCAT | Float | #N/A | #N/A | Default per phase real power value (in kW) if historical energy usage data is not provided. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | DEFAULTPVALUE
256 | Load Category | #N/A | CIMDnom.Schedule.Name | LOADSCHEDn_LOADCAT | String | #N/A | #N/A | Associated load schedule collection, specified for different seasons and day types. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | LOADSCHED
257 | Load Category | #N/A | VdropSchedule | VDROPSCH_LOADCAT | String | #N/A | #N/A | Associated secondary voltage drop schedule (as a function of transformer loading). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | VDROPSCH
258 | Load Category | #N/A | Vlimits | VLIMITS_LOADCAT | integer | enumeration | enumeration | Enumerated units flag for the six voltage limits. The enumeration has the following values: 1 = per unit, 2 = Voltage on a configurable voltage base. | DPF |  | TRUE | 1 | 2 | 1 | 2 | VLIMITS
259 | Load Category | #N/A | VoltageBase | VOLTAGEBASE_LOADCAT | Float | V | V | Voltage Base value which is used to determine the per unit voltage limit values. | DPF |  | FALSE | 10 | 45000 | 10 | 45000 | VOLTAGEBASE
260 | Load Category | #N/A | VnrmHigh | VNRMHIGH_LOADCAT | Float | per unit or Volt | per unit or Volt | Normal high voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VNRMHIGH
261 | Load Category | #N/A | VnrmLow | VNRMLOW_LOADCAT | Float | per unit or Volt | per unit or Volt | Normal low voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VNRMLOW
262 | Load Category | #N/A | VemergHigh | VEMRGHIGH_LOADCAT | Float | per unit or Volt | per unit or Volt | Emergency high voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGHIGH
263 | Load Category | #N/A | VemergLow | VEMRGLOW_LOADCAT | Float | per unit or Volt | per unit or Volt | Emergency low voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGLOW
264 | Load Category | #N/A | VoptNrmHigh | VOPTNRMHIGH_LOADCAT | Float | per unit or Volt | per unit or Volt | Additional optimization normal high voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGHIGH
265 | Load Category | #N/A | VoptNrmLow | VOPTNRMLOW_LOADCAT | Float | per unit or Volt | per unit or Volt | Additional optimization normal low voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGLOW
266 | Load Category | #N/A | VoptEmergHigh | VOPTEMRGHIGH_LOADCAT | Float | per unit or Volt | per unit or Volt | Additional optimization emergency high voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGHIGH
267 | Load Category | #N/A | VoptEmergLow | VOPTEMRGLOW_LOADCAT | Float | per unit or Volt | per unit or Volt | Additional optimization emergency low voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VEMRGLOW
268 | Load Category | #N/A | VstabHigh | VSTABHIGH_LOADCAT | Float | per unit or Volt | per unit or Volt | Load stability high voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VSTABHIGH
269 | Load Category | #N/A | VstabLow | VSTABLOW_LOADCAT | Float | per unit or Volt | per unit or Volt | Load stability low voltage limit (per unit or on a configurable voltage base). | DPF | Both per unit and the 120.0 Volt base limits are shown in the Low and High Value columns. | TRUE | 0.8/96.0 | 1.2/144.0 | 0.8/96.0 | 1.2/144.0 | VSTABLOW
270 | Load Category | #N/A | VstabLimit | VSTABLIMIT_LOADCAT | Boolean | #N/A | #N/A | Flag indicating stablity limit is provided | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
271 | Load Category | #N/A | VLimitCost | VLIMCOST_LOADCAT | Float | $/p.u. V or $/V | $/p.u. V or $/V | Voltage limit violation cost ($/p.u. V or $/V). | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | VLIMCOST
272 | Load Category | #N/A | VubfCost | VUBFCOST_LOADCAT | Float | $/p.u. V or $/V | $/p.u. V or $/V | Voltage imbalance violation cost ($/p.u. V or $/V). | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | VUBFCOST
273 | Load Category | #N/A | Vimbalance | VIMBALANCE_LOADCAT | Float | #N/A | #N/A | Voltage imbalance factor for three-phase loads (percent). | DPF |  | FALSE | 0 | 20 | 0 | 20 | VIMBALANCE
274 | Load Category | #N/A | PeakLoad | PEAKLOAD_LOADCAT | Boolean | #N/A | #N/A | Flag indicating the load P and Q nominal values represent peak values (true = peak). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | PEAKLOAD
275 | Load Category | #N/A | QnomFlag | QNOMFLAG_LOADCAT | Boolean | #N/A | #N/A | Flag indicating the reactive power schedule is given (true = reactive power, false = power factor). | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | QNOMFLAG
276 | Load Category | #N/A | DailyStudyInt | NUMDAILYSTUDYINT_LOADCAT | Integer | count | count | The number of daily study intervals (for use by study DPF). | DPF |  | FALSE |  |  |  |  | NUMDAILYSTUDYINT
277 | Load Category | #N/A | name | STUDYINTNAME_LOADCAT | String | #N/A | #N/A | The name of the study interval. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | STUDYINTNAME
278 | Load Category | #N/A | TimerPeriods | NUMTIMEPERIODS_LOADCAT | Integer | count | count | The number of subintervals for the study interval (time intervals do not have to be consecutive, interval may cover 9–11 AM and 3–5 PM). | DPF |  | FALSE | 0 | 100 | 0 | 100 | NUMTIMEPERIODS
279 | Load Category | #N/A | Starttime | STARTTIMEn_LOADCAT | Float | hour | hour | Subinterval start time (hours). | DPF |  | FALSE |  |  |  |  | STARTTIME
280 | Load Category | #N/A | Endtime | ENDTIMEn_LOADCAT | Float | hour | hour | Subinterval end time (hours). | DPF |  | FALSE |  |  |  |  | ENDTIME
281 | Load Category | #N/A | ProfileMultiplierSchedule | PROFILEMULTIPLIERSCH_LOADCAT | String | #N/A | #N/A | The name of an optional load multiplier schedule for a load category. If a schedule is provided, the nominal real power (and reactive power if specified in kVAR) is multiplied by the appropriate load schedule value (based on season, day type, and time of day) and the multiplier from this load multiplier schedule. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | SCHEDMULTIPLIERNAME
282 | Measurement Accuracy | Name | Name | NAME_MEASACC | String | #N/A | #N/A | Unique easurement accuracy name. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
283 | Measurement Accuracy | #N/A | AccuType | TYPE_MEASACC | Integer | enumeration | enumeration | Measurement type enumeration: 1 = Single-Phase amps, 2 = Single-Phase Volts, 3 = Single-Phase Power Factor, 4 = Single-Phase Watt, 5 = Single-Phase VAR, 6 = Three-Phase Watt, 7 = Three-Phase VAR, 8 = Three-Phase VA. | DPF |  | FALSE | 1 | 8 | 1 | 8
284 | Measurement Accuracy | #N/A | Accuracy | ACCURACY_MEASACC | Float | Percent | Percent | Measurement accuracy value. | DPF |  | FALSE | 0.1 | 20 | 0.1 | 20
285 | Measurement Accuracy Group | Name | Name | NAME_MEASACCGRP | String | #N/A | #N/A | Measurement accuracy group name. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
286 | Measurement Accuracy Group | #N/A | Default | DEFAULT_MEASACCGRP | Boolean | #N/A | #N/A | Flag indicating that this is the default accuracy group (a non-default measurement group can be set in the Station Name record). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
287 | Measurement Accuracy Group | #N/A | MeasAcc | NUMMEASACC_MEASACCGRP | Integer | count | count | Number of measurement accuracies associated with this group. | DPF |  | FALSE | 0 | 300 | 0 | 300
288 | Measurement Accuracy Group | #N/A | MeasAcc | MEASACCNAMEn_MEASACCGRP | String | #N/A | #N/A | Name of the measurement accuracy record. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
289 | Schedule | Name | Name | NAME_SCHED | String | #N/A | #N/A | Unique schedule name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
290 | Schedule | Schedule Type | SchedType | SCHEDTYPE_SCHED | Integer | enumeration | enumeration | Refer to the "Schedule Point Validation" worksheet. | DPF |  | TRUE | 1 | 16 | 1 | 16 | SCHEDTYPE
291 | Schedule | Type of value on x axis | XaxisType | XAXISTYPE_SCHED | String | #N/A | #N/A | Type of value on X axis (time for a load schedule). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | XAXISTYPE
292 | Schedule | X axis units | XaxisUnits | XAXISUNITS_SCHED | String | #N/A | #N/A | X axis units (hours for a load schedule). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | XAXISUNITS
293 | Schedule | Type of value on y axis | YaxisType | YAXISTYPE_SCHED | String | #N/A | #N/A | Type of value on Y axis (real power, reactive power, or power factor for a load schedule). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | YAXISTYPE
294 | Schedule | Y1 axis units | Y1axisUnits | Y1AXISUNITS_SCHED | String | #N/A | #N/A | Y1 axis units. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y1AXISUNITS
295 | Schedule | Y2 axis units | Y2axisUnits | Y2AXISUNITS_SCHED | String | #N/A | #N/A | Y2 axis units. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | Y2AXISUNITS
296 | Schedule | Schedule Shape | Shape | SHAPE_SCHED | Integer | enumeration | enumeration | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | DPF |  | FALSE | 1 | 2 | 1 | 2 | SHAPE
297 | Schedule | Associated Season | season | SEASON_SCHED | String | #N/A | #N/A | Associated season. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | SEASON
298 | Schedule | Associated Day Type | dayType | DAYTYPE_SCHED | String | #N/A | #N/A | Associated day type. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | DAYTYPE
299 | Schedule | Associated Cold Load Schedule | ColdLoad | COLDLOAD_SCHED | String | #N/A | #N/A | Associated cold load schedule (only for a load schedule). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | COLDLOAD
300 | Schedule | Associated Temperature Adjustment Schedule | TempAdjust | TEMPADJUST_SCHED | String | #N/A | #N/A | Associated temperature adjustment schedule (only for a load schedule). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | TEMPADJUST
301 | Schedule | Associated Embedded Generation Schedule | LoadGen | LOADGEN_SCHED | String | #N/A | #N/A | An optional schedule (for a load schedule only) describing the magnitude of embedded generation within the net load schedule. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOADGEN
302 | Schedule | Peak Schedule | Peak | PEAK_SCHED | Boolean | #N/A | #N/A | Flag indicating that a schedule represents a peak schedule (for a load schedule only). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | PEAK
303 | Schedule | #N/A | Normalized | NORMALIZED_SCHED | Boolean | #N/A | #N/A | Flag indicating that the schedule value is normalized.. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | NORMALIZED
304 | Schedule Point | Name | Name | ID_SCHEDPT | String | #N/A | #N/A | Unique schedule point identifier. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | ID
305 | Schedule Point | X Value | Xvalue | XVALUE_SCHEDPT | Float | #N/A | #N/A | X axis value. | DPF |  | TRUE | 0:00/0 | 23:59/10,000.0 | 0:00/0 | 23:59/10,000.0 | XVALUE
306 | Schedule Point | First Y Value | Y1Value | Y1VALUE_SCHEDPT | Float | #N/A | #N/A | First Y axis value. | DPF |  | FALSE | Low based on schedule type. | High based on schedule type. | Low based on schedule type. | High based on schedule type. | Y1VALUE
307 | Schedule Point | Second Y Value | Y2Value | Y2VALUE_SCHEDPT | Float | #N/A | #N/A | Second Y axis value. | DPF |  | FALSE | Low based on schedule type. | High based on schedule type. | Low based on schedule type. | High based on schedule type. | Y2VALUE
307 | VVC Station Group | #N/A | MaxActivePowerDecreaseRate | MAXACTIVEPOWERDECREASERATE_VVCGROUP | Float | MW/minute | MW/minute | Maximum active power decrease rate for LVM throttling | DPF |  | FALSE | #N/A | 999999.9 | #N/A | 999999.9 | MAXPDECREASERATE
308 | VVC Station Group | #N/A | MaxReactivePowerIncreaseRate | MAXREACTIVEPOWERINCREASERATE_VVCGROUP | Float | MVAR/minute | MVAR/minute | Maximum reactive power increase rate for LVM throttling | DPF |  | FALSE | #N/A | 999999.9 | #N/A | 999999.9 | MAXQINCREASERATE
309 | VVC Station Group | #N/A | MaxReactivePowerDecreaseRate | MAXREACTIVEPOWERDECREASERATE_VVCGROUP | Float | MVAR/minute | MVAR/minute | Maximum reactive power decrease rate for LVM throttling | DPF |  | FALSE | #N/A | 999999.9 | #N/A | 999999.9 | MAXQDECREASERATE
311 | Schedule Point | Associated Schedule | Sched | SCHED_SCHEDPT | String | #N/A | #N/A | Associated schedule. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | SCHED
312 | Season | Name | Name | NAME_SEASON | String | #N/A | #N/A | Unique season name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
313 | Season | Description | Desc | DESC_SEASON | String | #N/A | #N/A | Description of season. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | DESC
314 | Season | Date Range | DateRanges | NUMDATERANGE_SEASON | Integer | count | count | The number of data ranges for the season. | DPF |  | FALSE | 1 | 20 | 1 | 20 | NUMDATERANGE
315 | Season | #N/A | StartDate | STARTDATE_SEASON | string | #N/A | #N/A | Season start date (month/day). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | STARTDATE
316 | Season | #N/A | EndDate | ENDDATE_SEASON | String | #N/A | #N/A | Season end date (month/day). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | ENDDATE
317 | Series Reactor Model | Name | Name | NAME_SERIESMOD | String | #N/A | #N/A | Unique series reactor model name. | DPF |  | TRUE | #N/A | #N/A |  |  | NAME
318 | Series Reactor Model | Series Reactor - R | R | R_SERIESMOD | Float | ohms | ohms | Nominal resistance. | DPF |  | FALSE | 0 | 100 | 0 | 100 | R
319 | Series Reactor Model | Series Reactor - X | X | X_SERIESMOD | Float | ohms | ohms | Nominal reactance. | DPF |  | FALSE | 0 | 100 | 0 | 100 | X
320 | Series Reactor Model | Series Reactor - Oplimits | OpLimits | NUMOPLIMIT_SERIESMOD | Integer | count | count | The number of operation limits. | DPF |  | FALSE | 0 | 5 | 0 | 5 | NUMLIMIT
321 | Series Reactor Model | Series Reactor - Oplimits Name | Name | OPLIMITNAMEn_SERIESMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMNAME
322 | Series Reactor Model | Series Reactor - Oplimits Unit | Unit | OPLIMITUNITn_SERIESMOD | Integer | enumeration | enumeration | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | LIMUNIT
323 | Series Reactor Model | Series Reactor - Oplimits Limit | Limit | OPLIMITn_SERIESMOD | Float | Amps/kVA/MVA | Amps kVA/MVA | The value of the operational limit. | DPF |  | FALSE | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | LIMVALUE
324 | Series Reactor Model | Series Reactor - Oplimits Season | Season | OPLIMITSEASONn_SERIESMOD | String | #N/A | #N/A | The name of an associated season when the limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | LIMSEAS
325 | Series Reactor Model | Series Reactor - Oplimits Limit Event | LimitEvent | OPLIMITEVENTn_SERIESMOD | Boolean | #N/A | #N/A | The flag for issuing an alarm when there is a violation of this limit. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENT
326 | Shunt Impedance Model | Name | Name | NAME_SHIMPMOD | String | #N/A | #N/A | Unique shunt impedance model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
327 | Shunt Impedance Model | Shunt Impedance - Ptotal | Ptotal | PTOTAL_SHIMPMOD | Float | W | W | Real power loss for a capacitor bank (kW). | DPF |  | FALSE | 0 | 15000 | 0 | 15000 | PLOSS
328 | Shunt Impedance Model | Shunt Impedance - Switch Cost | Switchcost | SWITCOST_SHIMPMOD | Float | cost/operation | cost/operation | Relative cost of performing a switching operation ($/operation). | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | SWITCOST
329 | Shunt Impedance Model | #N/A | SwitchcostSched | SWITCOSTSCHED_SHIMPMOD | String | #N/A | #N/A | The name of a switching cost biasing schedule (similar to a tap changer cost schedule). | DPF | The cost schedule must be found in the file (if the field is not blank). Optional. | FALSE | #N/A | #N/A | #N/A | #N/A | SWCSTSCH.NAME
330 | Shunt Impedance Model | #N/A | Oplimits | NUMOPLIMIT_SHIMPMOD | Integer | count | count | The number of operation limits. The limit fields will be deprecated. In a future release. | DPF |  | FALSE | 0 | 20 | 0 | 20 | NUMLIMIT
331 | Shunt Impedance Model | Name | Name | OPLIMITNAMEn_SHIMPMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). The limit fields will be deprecated. In a future release. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMNAME
332 | Shunt Impedance Model | Unit | Unit | OPLIMITUNITn_SHIMPMOD | Integer | enumeration | enumeration | Enumerated limit units, 1 = amps, 2 = KVA, 3 = MVA. The limit fields will be deprecated. In a future release. | DPF |  | FALSE | 1 | 3 | 1 | 3 | LIMUNIT
333 | Shunt Impedance Model | Limit | Limit | OPLIMITn_SHIMPMOD | Float | kVA/MVA | kVA/MVA | Value of the operational limit. The limit fields will be deprecated. In a future release. | DPF |  | FALSE | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | LIMVALUE
334 | Shunt Impedance Model | Shunt Impedance - Close Switch | CloseSwitch | CLOSESW_SHIMPMOD | Float |  |  | Limit on switching electrically close capacitors (ohms separation). This field will be deprecated in a future release. | DPF |  | FALSE |  |  |  |  | CLOSESW
335 | Shunt Impedance Model | Shunt Impedance - Ind. Phase Op. | IndPhaseOp | INDPHASEOP_SHIMPMOD | Boolean | #N/A | #N/A | Independent phase switching flag (True = device can be switched phase independently, False = ganged operation). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | INDPHOPS
336 | Shunt Impedance Model | #N/A | #N/A | NUMOPERATIONSCHED_SHIMPMOD | Integer | #N/A | #N/A | The number of time or temperature operating schedules (Optional). These schedules have the highest priority, followed by the individual schedule defined in the capacitor. The single pair of on and off level values are the lowest priority. | DPF |  | FALSE | 0 | 100 | 0 | 100 | NUMOPSCH
337 | Shunt Impedance Model | #N/A | #N/A | OPERATIONSCHEDn_SHIMPMOD | String | #N/A | #N/A | The time or temperature schedule name. | DPF | The schedule must match a schedule given in the file (if the field is not blank). Optional. | FALSE | #N/A | #N/A | #N/A | #N/A | SHIMPMODSCHED1 SHIMPMODSCHED2 SHIMPMODSCHED3 SHIMPMODSCHED4
338 | Station Name | Name | Name | NAME_SUBNAME | String | #N/A | #N/A | Unique substation name. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
339 | Station Name | SCADA Name (8 Characters Max.) | EMSName | EMSMAPNAME_SUBNAME | String | #N/A | #N/A | The eight character e-terramodeler substation ID. This station name is used to tie together station model files and the EMS portion of the network. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
340 | Station Name | ID | Id | UNIQUEID_SUBNAME | String | #N/A | #N/A | Unique station ID or Index. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
341 | Station Name | #N/A | PermArea | PERMAREA_SUBNAME | String | #N/A | #N/A | Associated permission area name. | N/A |  | FALSE | #N/A | #N/A | #N/A | #N/A
342 | Station Name | #N/A | R1 | R1_SUBNAME | Float | ohms | ohms | Source equivalent positive sequence equivalent resistance for station bus (ohms). | DPF |  | FALSE | 0 | 300 | 0 | 300
343 | Station Name | #N/A | X1 | X1_SUBNAME | Float | ohms | ohms | Source equivalent positive sequence equivalent reactance for station bus (ohms). | DPF |  | FALSE | 0 | 300 | 0 | 300
344 | Station Name | #N/A | R0 | R0_SUBNAME | Float | ohms | ohms | Source equivalent zero sequence equivalent resistance for station bus (ohms). | DPF |  | FALSE | 0 | 300 | 0 | 300
345 | Station Name | #N/A | X0 | X0_SUBNAME | Float | ohms | ohms | Source equivalent zero sequence equivalent reactance for station bus (ohms). | DPF |  | FALSE | 0 | 300 | 0 | 300
346 | Station Name | #N/A | MeasAccGrp | MEASACCGRP_SUBNAME | String | #N/A | #N/A | Associated measurement accuracy group. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
347 | SVC Model | Name | Name | NAME_SVCMOD | String | #N/A | #N/A | Unique SVC model name. The SVC object and SVC model are not currently supported. | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME
348 | SVC Model | #N/A | Caprating | CAPRATE_SVCMOD | Float | kVAR | kVAR | Capacitive rating (kVAR). | DPF |  | FALSE | 0 | 3000 | 0 | 3000 | CAPRATE
349 | SVC Model | #N/A | Indrating | INDRATE_SVCMOD | Float | kVAR | kVAR | Inductive rating (kVAR). | DPF |  | FALSE | 0 | 3000 | 0 | 3000 | INDRATE
350 | SVC Model | #N/A | #N/A | NUMOPLIMITn_SVCMOD | Integer | count | count | The number of operation limits. | DPF |  | FALSE | 0 | 20 | 0 | 20 | NUMLIMIT
351 | SVC Model | #N/A | #N/A | OPLIMITNAMEn_SVCMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMNAME
352 | SVC Model | #N/A | #N/A | OPLIMITUNITn_SVCMOD | Integer | enumeration | enumeration | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | LIMUNIT
353 | SVC Model | #N/A | #N/A | OPLIMITn_SVCMOD | Float | kVA/MVA | kVA/MVA | Value of the operational limit. | DPF |  | FALSE | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | 1.0/0.01/0.00001 | 1000.0/30,000.0/30.0 | LIMVALUE
354 | Switch Model | Name | Name | NAME_SWMOD | String | #N/A | #N/A | Unique switch model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
355 | Switch Model | Switch - Type | SwType | SWTYPE_SWMOD | Integer | enumeration | enumeration | User enumerated switch type. | DPF |  | FALSE |  |  |  |  | ISWTTYPE
356 | Switch Model | Switch - Load Brk | LoadBrk | LOADBRK_SWMOD | Boolean | #N/A | #N/A | Flag indicating switch has load break capability (True = has load break capability). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LOADBRK
357 | Switch Model | Switch - Load Break Rating | LoadBreakRating | LOADBRKR_SWMOD | Float | Amps | Amps | Load break Amp limit (Amp/ phase) beyond which the switching reconfiguration applications such as Fault Isolation and Service Restoration (FISR) will not use the switch for any reconfiguration switching. | OPS |  | FALSE | 0 | 9000 | 0 | 9000 | LOADBRKR
358 | Switch Model | Switch - Cost | SwitCost | SWITCOST_SWMOD | Float | cost/operation | cost/operation | Relative cost of performing a switching operation (units). | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | SWCOST
359 | Switch Model | #N/A | SwitCostSched | SWITCOSTSCHED_SWMOD | String | #N/A | #N/A | Associated switching cost biasing schedule. | DPF | The schedule must match a schedule given in the file (if the field is not blank). Optional. | TRUE | #N/A | #N/A | #N/A | #N/A | SWCSTSCH.NAME
360 | Switch Model | Switch - Ganged? | Ganged | GANGED_SWMOD | Boolean | #N/A | #N/A | Flag indicating ganged switch operation (True = ganged). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A
361 | Switch Model | Switch - Reversible? | Reversible | REVERSEREC_SWMOD | Boolean | #N/A | #N/A | Flag indicating reversible recloser (True = reversible). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | REVERSIBLEREC
362 | Switch Model | Switch - Unique Name? | UniqueName | UNIQUENAME_SWMOD | Boolean | #N/A | #N/A | Flag that indicates that the device has a unique name (True = unique). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | UNIQUEID
363 | Switch Model | Switch - Telemetered? | Telemetered | TELEMETERED_SWMOD | Boolean | #N/A | #N/A | Flag that indicates that the device is telemetered (True = telemetered). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
364 | Switch Model | Switch - Controllable? | Controllable | CONTROLLABLE_SWMOD | Boolean | #N/A | #N/A | Flag that indicates if the device is controllable (True = controllable). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A
365 | Switch Model | Switch - Size | Size | SIZE_SWMOD | Float | Amps | Amps | Device size (given as an Amp rating). | OPS |  | FALSE | 1 | 9000 | 1 | 9000 | SIZE
366 | Switch Model | #N/A | RectypDsec | RECTYPEDESC_SWMOD | String | #N/A | #N/A | Recloser type description. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | RECTYPE
367 | Switch Model | Switch - Bitmap Scheme | BitmapSCheme | BITMAPSCHEME_SWMOD | String | #N/A | #N/A | Name of the bitmap scheme (default is blank). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | BTMAPSCH
368 | Switch Model | Recloser - DMS Type | DMSRecloserType | DMSRECLOSERTYPE_SWMOD | Integer | enumeration | enumeration | Enumerated flag indicating the recloser type: 0 = Unknown, 1 = Electronic, 2 = Hydraulic). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | DMSRCTYP
369 | Switch Model | Switch - Elbow Switch | ElbowSwitch | ELBOWSWITCH_SWMOD | Boolean | #N/A | #N/A | Elbow switch flag (True=elbow). | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | ELBOWFLG
370 | Switch Model | #N/A | Oplimits | NUMOPLIMIT_SWMOD | Integer | count | count | The number of operation limits. | DPF |  | FALSE | 0 | 20 | 0 | 20 | NUMLIMIT
371 | Switch Model | Switch - Oplimits Name | Name | OPLIMITNAMEn_SWMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMNAME
372 | Switch Model | Switch - Oplimits Unit | Unit | OPLIMITUNITn_SWMOD | Integer | enumeration | enumeration | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | LIMUNIT
373 | Switch Model | Switch - Oplimits Limit | Limit | OPLIMITn_SWMOD | Float | kVA/MVA | kVA/MVA | Value of the operational limit. | DPF |  | FALSE | 1.0/0.01/0.00001 | 9000.0/30,000.0/30.0 | 1.0/0.01/0.00001 | 9000.0/30,000.0/30.0 | LIMVALUE
374 | Switch Model | Switch - Oplimits Season | Season | OPLIMITSEASONn_SWMOD | String | #N/A | #N/A | The name of an associated season when the limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. | FALSE | #N/A | #N/A | #N/A | #N/A | LIMSEAS
375 | Switch Model | Switch - Oplimits LimitEvent | LimitEvent | OPLIMITEVENTn_SWMOD | Boolean | #N/A | #N/A | Flag indicating a SCADA alarm is issued by the Dsitribution Power Flow when there is a violation of this limit (True = issue alarm). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENT
376 | Tap Changer Model | Name | Name | NAME_TAPMOD | String | #N/A | #N/A | Unique tap changer model name. | DPF | Required to solve DPF. | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
377 | Tap Changer Model | Tap - Max Tap | MaxTap | MAXTAP_TAPMOD | Integer | units | units | Maximum tap step (maybe +16). | DPF |  | FALSE | 0 | 50 | 0 | 50 | MAXTAP
378 | Tap Changer Model | Tap - Min Tap | MinTap | MINTAP_TAPMOD | Integer | units | units | Minimum tap step (maybe -16). | DPF |  | FALSE | -50 | 20 | -50 | 20 | MINTAP
379 | Tap Changer Model | Tap - Incr. | TapIncr | TAPINCR_TAPMOD | Float | percent | percent | Tap increment (percent V). | DPF | Required to solve DPF. | TRUE | -10 | 10 | -10 | 10 | TAPSTEP
380 | Tap Changer Model | Tap - Nominal | Nominal | NOMINAL_TAPMOD | Integer | units | units | Nominal tap setting (maybe 0). | DPF |  | FALSE | -50 | 50 | -50 | 50 | NOMTAP
381 | Tap Changer Model | Tap - Time Delay 1 | TimeDelay1 | TIMEDELAY1_TAPMODEL | Float | second | second | Initial time delay (seconds). | DPF |  | FALSE | 0 | 120 | 0 | 120 | TMDELAY
382 | Tap Changer Model | Tap - Time Delay 2 | TimeDelay2 | TIMEDELAY2_TAPMODEL | Float | second | second | Subsequent time delay (seconds). | DPF |  | FALSE | 0 | 120 | 0 | 120 | TMDELAYT
383 | Tap Changer Model | Tap - Cost | Tapcost | TAPCOST_TAPMODEL | Float | cost/operation | cost/operation | Tap changer relative cost (units). | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | TAPCOST
384 | Tap Changer Model | Tap - Cost Schedule | TapcostSched | TAPCOSTSCHED_TAPMODEL | String | #N/A | #N/A | The name of a tap changer cost schedule. This schedule can be used to bias the operating range of a regulator or TCUL. This is currently not supported. | DPF | The tap changer cost schedule must be found in the file (if the field is not blank). Optional. | TRUE | #N/A | #N/A | #N/A | #N/A | CSTSCHED
385 | Tap Changer Model | Tap - Voltage Reduction Steps | VoltageReductionSteps | VOLTREDSTEPS_TAPMOD | Integer | #N/A | #N/A | The number of voltage reduction steps supported. 0 = no voltage reduction capability. 1-3 = number of steps used by controller | DPF |  | TRUE | 0 | 3 | 0 | 3 | VOLTREDSTEPS
386 | Tap Changer Model | Tap - Voltage Reduction 1 | VoltageReduction1 | VOLTRED1_TAPMOD | Float | percent | percent | Voltage reduction percent for step 1 (if 1 or more steps supported) | DPF | Must be less than maximum voltage reduction field | FALSE | 0 | Max Field | 0 | Max Field | VOLTRED1
387 | Tap Changer Model | Tap - Voltage Reduction 2 | VoltageReduction2 | VOLTRED2_TAPMOD | Float | percent | percent | Voltage reduction percent for step 2 (if 2 or more steps supported) | DPF | Must be less than maximum voltage reduction field | FALSE | 0 | Max Field | 0 | Max Field | VOLTRED2
388 | Tap Changer Model | Tap - Voltage Reduction 3 | VoltageReduction3 | VOLTRED3_TAPMOD | Float | percent | percent | Voltage reduction percent for step 3 (if 3 or more steps supported) | DPF | Must be less than maximum voltage reduction field | FALSE | 0 | Max Field | 0 | Max Field | VOLTRED3
389 | Tap Changer Model | Tap - Max Voltage Reduction | MaxVoltageReduction | MAXVOLTRED_TAPMOD | Float | percent | percent | Maximum voltage reduction percent for voltage reduction steps 1-3, and for advanced regulation, manual and SCADA overrides. | DPF |  | TRUE | 0 | 20 | 0 | 20 | MAXVOLTRED
390 | Tap Changer Model | Tap - Regulator Control Definition | RegControlDefinition | REGCONTROLDEFINITION_TAPMOD | String | #N/A | #N/A | The ID of a Regulator Control Definition object defined in the RegulatorControl.csv file. This field is optional. | DPF | Optional (a transformer can also be associated to a Regulator Control Definition using the transformer ID). | FALSE | #N/A | #N/A | #N/A | #N/A | TFREGCONTROLDEFINITIONID
391 | Transformer Model | Name | Name | NAME_TFMOD | String | #N/A | #N/A | Unique transformer model name. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
392 | Transformer Model | Transformer - Primary Resistance (per unit) | PrimR1 | PRIMR1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Primary winding positive sequence resistance (per unit on transformer power base). | DPF |  | TRUE | 0 | 1 | 0 | 1 | PRIMR1
393 | Transformer Model | Transformer - Primary Reactance (per unit) | PrimX1 | PRIMX1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Primary winding positive sequence reactance (per unit on transformer power base). | DPF |  | TRUE | 0 | 1 | 0 | 1 | PRIMX1
394 | Transformer Model | Transformer - Secondary Resistance (per unit) | Sec1R1 | SEC1R1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Secondary winding positive sequence resistance (per unit on transformer power base). | DPF |  | TRUE | 0 | 1 | 0 | 1 | SEC1R1
395 | Transformer Model | Transformer - Secondary Reactance (per unit) | Sec1X1 | SEC1X1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Secondary winding positive sequence reactance (per unit on transformer power base). | DPF |  | TRUE | 0 | 1 | 0 | 1 | SEC1X1
396 | Transformer Model | Transformer - Tertiary Resistance (per unit, three-winding) | Sec2R1 | SEC2R1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Tertiary winding positive sequence resistance (per unit on transformer power base). | DPF |  | FALSE | 0 | 1 | 0 | 1 | SEC2R1
397 | Transformer Model | Transformer - Tertiary Reactance (per unit, three-winding) | Sec2X1 | SEC2X1_TFMOD | Float | per unit on transformer power base | per unit on transformer power base | Tertiary winding positive sequence resistance (per unit on transformer power base). | DPF |  | FALSE | 0 | 1 | 0 | 1 | SEC2X1
398 | Transformer Model | Transformer - Core Loss (W) | Coreloss | CORELOSS_TFMOD | Float | W | W | Transformer core loss (W). | DPF |  | FALSE | 0 | 100000 | 0 | 100000 | CORELOSS
399 | Transformer Model | Transformer - Magnetizing Power Factor (optional if excitation % is given) | MagPf | MAGPF_TFMOD | Float | #N/A | #N/A | Magnetization power factor. | DPF |  | FALSE | 0 | 1 | 0 | 1 | MAGPF
400 | Transformer Model | Transformer - Excitation Current (%, optional if power factor is given) | ExciteCurrent | EXCITECURRENT_TFMOD | Float | percent | percent | Average percent excitation current. | DPF |  | FALSE | 0 | 10 | 0 | 10 | EXCITECURRENT
401 | Transformer Model | Transformer - Zero Sequence Magnetizing Shunt Susceptance (per unit, optional) | MagB0 | MAGB0_TFMOD | Float | Siemens | Siemens | Zero sequence magnetization susceptance. | DPF |  | FALSE | 0 | 5 | 0 | 5 | MAGB0
402 | Transformer Model | Transformer - Zero Sequence Magnetizing Shunt Conductance (per unit, optional) | MagG0 | MAGG0_TFMOD | Float | Siemens | Siemens | Zero sequence magnetization conductance. | DPF |  | FALSE | 0 | 5 | 0 | 5 | MAGG0
403 | Transformer Model | Transformer - DMS Type | Type | TYPE_TFMOD | Integer | enumeration | enumeration | Enumerated transformer type. The following values are used: 1 = Secondary transformer, 2 = Voltage regulator, 3 = Power transformer, 4 = Auto-transformer, 5 = Step Up/Down transformer, 6 = Zigzag transformer. | DPF |  | FALSE | 1 | 6 | 1 | 6 | TYPE
404 | Transformer Model | #N/A | Oplimits | NUMOPLIMIT_TFMOD | Integer | count | count | The number of operation limits. | DPF | This value is set when static limits are used. | FALSE | 0 | 20 | 0 | 20 | NUMOPLIMIT
405 | Transformer Model | #N/A | OplimitsSec | NUMOPLIMITSEC_TFMOD | Integer | count | count | The number of operation limits (Secondary Winding). | DPF | This value is set when static limits are used. | FALSE | 0 | 20 | 0 | 20 | NUMOPLIMITSEC
406 | Transformer Model | #N/A | OplimitsTer | NUMOPLIMITTER_TFMOD | Integer | count | count | The number of operation limits (Tertiary Winding). | DPF | This value is set when static limits are used. | FALSE | 0 | 20 | 0 | 20 | NUMOPLIMITTER
407 | Transformer Model | Transformer - Operational Limits Name | Name | OPLIMITNAMEn_TFMOD | String | #N/A | #N/A | The name of the limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | NAME
408 | Transformer Model | Transformer - Operational Limits (Secondary Winding) Name | Name | OPLIMITNAMESECn_TFMOD | String | #N/A | #N/A | The name of the secondary winding limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | OPLIMITNAMESEC
409 | Transformer Model | Transformer - Operational Limits (Tertiary Winding) Name | Name | OPLIMITNAMETERn_TFMOD | String | #N/A | #N/A | The name of the tertiary winding limit (such as Long Term, Medium Term, or Short Term). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | OPLIMITNAMETER
410 | Transformer Model | Transformer - Operational Limits Unit | Unit | OPLIMITUNITn_TFMOD | Integer | enumeration | enumeration | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | OPLIMITUNIT
411 | Transformer Model | Transformer - Operational Limits (Secondary Winding) Unit | Unit | OPLIMITUNITSECn_TFMOD | Integer | enumeration | enumeration | Enumerated secondary winding limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | OPLIMITUNITSEC
412 | Transformer Model | Transformer - Operational Limits (Tertiary Winding) Unit | Unit | OPLIMITUNITTERn_TFMOD | Integer | enumeration | enumeration | Enumerated tertiary winding limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | DPF |  | FALSE | 1 | 3 | 1 | 3 | OPLIMITUNITTER
413 | Transformer Model | Transformer - Operational Limits Limit | Limit | OPLIMITn_TFMOD | Float | Amps, kVA, or MVA | Amps, kVA, or MVA | Value of the operational limit. Limits in Amps are per-phase values while limits in kVA or MVA are total values. | DPF |  | FALSE | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | OPLIMIT
414 | Transformer Model | Transformer - Operational Limits (Secondary Winding) Limit | Limit | OPLIMITSECn_TFMOD | Float | Amps, kVA, or MVA | Amps, kVA, or MVA | Value of the operational secondary winding limit. Limits in Amps are per-phase values while limits in kVA or MVA are total values. | DPF |  | FALSE | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | OPLIMITSEC
415 | Transformer Model | Transformer - Operational Limits (Tertiary Winding) Limit | Limit | OPLIMITTERn_TFMOD | Float | Amps, kVA, or MVA | Amps, kVA, or MVA | Value of the operational tertiary winding limit. Limits in Amps are per-phase values while limits in kVA or MVA are total values. | DPF |  | FALSE | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | 1.00/0.01/0.0001 | 1000.0/30,000.0/30.0 | OPLIMITTER
416 | Transformer Model | Transformer - Operational Limits Season | Season | OPLIMITSEASONn_TFMOD | String | #N/A | #N/A | The name of an associated season when the limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. Required for limit monitoring. | FALSE | #N/A | #N/A | #N/A | #N/A | LIMSEAS
417 | Transformer Model | Transformer - Operational Limits (Secondary Winding) Season | Season | OPLIMITSEASONSECn_TFMOD | String | #N/A | #N/A | The name of an associated season when the secondary winding limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. Required for limit monitoring. | FALSE | #N/A | #N/A | #N/A | #N/A | OPLIMITSEASONSEC
418 | Transformer Model | Transformer - Operational Limits (Tertiary Winding) Season | Season | OPLIMITSEASONTERn_TFMOD | String | #N/A | #N/A | The name of an associated season when the tertiary winding limit is applicable. If no season is provided, it is assumed that the limit is applicable for the entire year. | DPF | The name of the season must match a season given in the file. Required for limit monitoring. | FALSE | #N/A | #N/A | #N/A | #N/A | OPLIMITSEASONTER
419 | Transformer Model | Transformer - Operational Limits LimitEvent | LimitEvent | OPLIMITEVENTn_TFMOD | Boolean | #N/A | #N/A | Flag indicating a SCADA alarm is issued by the Dsitribution Power Flow when there is a violation of this limit (True = issue alarm). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENT
420 | Transformer Model | Transformer - Operational Limits (Secondary Winding) LimitEvent | LimitEvent | OPLIMITEVENTSECn_TFMOD | Boolean | #N/A | #N/A | Flag indicating a SCADA alarm is issued by the Dsitribution Power Flow when there is a violation of this limit (True = issue alarm). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENTSEC
421 | Transformer Model | Transformer - Operational Limits (Tertiary Winding) LimitEvent | LimitEvent | OPLIMITEVENTTERn_TFMOD | Boolean | #N/A | #N/A | Flag indicating a SCADA alarm is issued by the Dsitribution Power Flow when there is a violation of this limit (True = issue alarm). | DPF |  | FALSE | #N/A | #N/A | #N/A | #N/A | LIMITEVENTTER
422 | Transformer Model | #N/A | Reglimits | NUMREGLIMIT_TFMOD | Integer | count | count | The number of regulator step limits. | DPF | This value is set when Dynamic limits are used. | FALSE | 0 | 5 | 0 | 5 | NUMREGLIMIT
423 | Transformer Model | Transformer - Regulation Limits Regulation Step | RegStep | REGSTEPn_TFMOD | Float | percent | percent | The regulation step such as 5.0% or 10.0%. | DPF |  | FALSE | 0 | 20 | 0 | 20 | REGSTEP
424 | Transformer Model | Transformer - Regulation Limits Regulation Limit | Reglimit | REGLIMITn_TFMOD | Float | Amps | Amps | Regulator step limit. | DPF |  | FALSE | 0 | 1000 | 0 | 1000 | REGLIMIT
425 | Transformer Model | Transformer - Size Units | Units | UNITS_TFMOD | Integer | enumeration | enumeration | Transformer size rating display units: 1=KVA, 2=MVA, 3=Regulated KVA. | DPF |  | TRUE | 1 | 3 | 1 | 3 | UNITS
426 | Transformer Model | Transformer - Size | Srating | SRATING_TFMOD | Float | kVA or MVA or regulated kVA (regulator) | kVA or MVA or regulated kVA (regulator) | Transformer rating (in kVA or MVA) or the regulated kVA for a regulator. | DPF |  | TRUE | 1/0.01 | 30,000/30.0 | 1/0.01 | 30,000/30.0 | SRATING
427 | Transformer Model | Transformer - Regulation Units | RegUnits | REGUNITS_TFMOD | Integer | enumeration | enumeration | Enumerated flag indicating the voltage units that should be used for transformers with voltage regulation capability. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on a configurable voltage base). | DPF |  | FALSE | 1 | 2 | 1 | 2 | REGUNITS
428 | Transformer Model | Transformer - Power Flow Type (Integer from DMS transformer library) | TfType | TFTYPE_TFMOD | Integer | enumeration | enumeration | Enumerated transformer type for linking the transformer model to a transformer type that is needed by the GE ADMS power flow. | DPF |  | TRUE | 1 | 123 | 1 | 123 | TFTYPE
429 | Transformer Model | Transformer - Bitmap Scheme | BitMapScheme | BITMAPSCHEME_TFMOD | String | #N/A | #N/A | Name of the bitmap scheme (default is blank). This field is no longer used. | OPS |  | FALSE | #N/A | #N/A | #N/A | #N/A | BITMAPSCHEME
430 | VVC Station Group | #N/A | Name | NAME_VVCGROUP | String | #N/A | #N/A | Unique name of the LVM substation group. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NAME
431 | VVC Station Group | #N/A | ObjFunctSchedules | NUMOBJFUNCTSCHED_VVCGROUP | Integer | #N/A | #N/A | Number of the associated objective function schedules. | DPF |  | TRUE | #N/A | #N/A | #N/A | #N/A | NUMOBJFUNCSCH
432 | VVC Station Group | #N/A | ObjFunctSched | OBJFUNCTSCHEDn_VVCGROUP | String | #N/A | #N/A | A familly of the associated objective function schedules. | DPF | The name of the schedule must match a schedule given in the file. | TRUE | #N/A | #N/A | #N/A | #N/A | AOBJFUNCSCHARRAY
433 | VVC Station Group | #N/A | MaxActivePowerIncreaseRate | MAXACTIVEPOWERINCREASERATE_VVCGROUP | Float | MW/minute | MW/minute | Maximum active power increase rate for LVM throttling | DPF |  | FALSE | #N/A | 999999.9 | #N/A | 999999.9 | MAXPINCREASERATE

## Defaults CSV Input
Sort | Type | CSV Field Name | Description | Attribute Type | Units (Imperial) | Units (Metric) | Scope | Low Value Imperial Units | High Value Imperial Units | Low Value Metric Units | High Value Metric Units
1 | Default Generator | WYECONN_DEFGEN | Flag indicating generator is wye connected. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
2 | Default Generator | GROUNDED_DEFGEN | Flag indicating generator is grounded. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
3 | Default Generator | RGROUND_DEFGEN | Resistance to ground. | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
4 | Default Generator | XGROUND_DEFGEN | Reactance to ground. | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
5 | Default Generator | VMAXSEP_DEFGEN | Maximum voltage before separation from network (per unit or on configurable voltage base depending on the flag set on the generator model). | Float | per unit or volt | per unit or volt | DPF | 0.8 per unit | 1.2 per unit | 0.8 per unit | 1.2 per unit
6 | Default Generator | VMINSEP_DEFGEN | Minimum voltage before separation from network (per unit or on configurable voltage base depending on the flag set on the generator model). | Float | per unit or volt | per unit or volt | DPF | 0.8 per unit | 1.2 per unit | 0.8 per unit | 1.2 per unit
7 | Default Bus | R_DEFBUS | Bus source resistance (ohms – for fault analysis function). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
8 | Default Bus | X_DEFBUS | Bus source reactance (ohms – for fault analysis function). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
10 | Default Bus | VNRMHIGH_DEFBUS | Normal high voltage limit. | Float | per unit | per unit | DPF | 0.8 | 1.2 | 0.8 | 1.2
11 | Default Bus | VNRMLOW_DEFBUS | Normal low voltage limit. | Float | per unit | per unit | DPF | 0.8 | 1.2 | 0.8 | 1.2
12 | Default Bus | VEMRGHIGH_DEFBUS | Emergency high voltage limit. | Float | per unit | per unit | DPF | 0.8 | 1.2 | 0.8 | 1.2
13 | Default Bus | VEMRGLOW_DEFBUS | Emergency low voltage limit. | Float | per unit | per unit | DPF | 0.8 | 1.2 | 0.8 | 1.2
14 | Default Line | SUSTFRATE_DEFLINE | Sustained interruption frequency (default override – value can be obtained from associated conductor model). This field should be blank if the default is taken from the conductor model. | Float | percent | percent | DPF | 0 | 100 | 0 | 100
15 | Default Line | MOMFRATE_DEFLINE | Momentary interruption frequency (default override – value can be obtained from associated conductor model). This field should be left blank if the default is taken from the conductor model. | Float | percent | percent | DPF | 0 | 100 | 0 | 100
16 | Default Line | REPAIR_DEFLINE | Average time to repair (default override – value can be obtained from associated conductor model). This field should be left blank if the default is taken from the conductor model. | Float | hours |  | DPF | 0 | 500 | 0 | 500
17 | Default Breaker | PHASEOPS_DEFBREAKER | Total number of phase reclose operations. | Integer | count | count | DPF | 1 | 5 | 1 | 5
18 | Default Breaker | GROUNOPS_DEFBREAKER | Total number of ground reclose operations. | Integer | count | count | DPF | 1 | 5 | 1 | 5
19 | Default Breaker | NOTETCMS_DEFBREAKER | Notify Outage Management System (OMS) flag. | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A
20 | Default Recloser | MAXINT_DEFRECLOSER | Maximum interruption rating (amps). | Float | amps | amps | DPF | 0 | 40000 | 0 | 40000
21 | Default Recloser | PHTRIP_DEFRECLOSER | Phase trip rating (amps). | Float | amps | amps | DPF | 0 | 5000 | 0 | 5000
22 | Default Recloser | NUMBOPS_DEFRECLOSER | Total number of phase reclose operations. | Integer | count | count | DPF | 1 | 5 | 1 | 5
23 | Default Recloser | NOTETCMS_DEFRECLOSER | Notify Outage Management System (OMS) flag. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
24 | Default Sectionalizer | COUNTS_DEFSECT | Counts (reclose operations) before device opens. | Integer | count | count | OPS | 1 | 5 | 1 | 5
25 | Default Load | WYECONN_DEFLOAD | Flag indicating load is wye connected (true = wye connected). A load that is connected from phase to neutral is considered a wye load. | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A
26 | Default Load | GROUNDED_DEFLOAD | Flag indicating load is grounded (true = grounded). | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A
27 | Default Load | SUPPLIER_DEFLOAD | Energy supplier (enumeration). | String | enumeration | enumeration | OPS | 1 | 2 | 1 | 2
28 | Default Shunt Impedance | WYECONN_DEFSHIMP | Flag indicating shunt impedance is wye connected. Wye connected shunt impedance is a connection from phase to neutral. | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A
29 | Default Shunt Impedance | GROUNDED_DEFSHIMP | Flag indicating equipment is grounded (true = grounded). | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A
30 | Default Shunt Impedance | RGROUND_DEFSHIMP | Equipment grounding resistance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
31 | Default Shunt Impedance | XGROUND_DEFSHIMP | Equipment grounding reactance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
32 | Default Shunt Impedance | NUMSTEPS_DEFSHIMP | The number of steps for the controller. A fixed bank has one step. A switched bank that is either all on or all off also has one step. | Integer | count | count | DPF | 1 | 50 | 1 | 50
33 | Default Shunt Impedance | MAXSWITCHES_DEFSHIMP | Daily maximum number of switching operations. | Integer | count | count | DPF | 0 | 20 | 0 | 20
34 | Default Shunt Impedance | CONSECSW_DEFSHIMP | Time interval between consecutive switching operations (hours). | Float | hour | hour | DPF | 0 | 48 | 0 | 48
35 | Default Shunt Impedance | TDELAY_DEFSHIMP | Controller time delay setting. | Float | hour | hour | DPF | 0 | 48 | 0 | 48
36 | Default Ground | R_DEFGROUND | Ground resistance (ohms) | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
37 | Default Ground | X_DEFGROUND | Ground reactance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
38 | Default Time Overcurrent Relay | RGROUNDPRIM_DEFTF | Phase trip (amps). | Float | amps | amps | DPF | 0 | 5000 | 0 | 5000
39 | Default Time Overcurrent Relay | XGROUNDPRIM_DEFTF | Ground trip (amps). | Float | amps | amps | DPF | 0 | 5000 | 0 | 5000
40 | Default Transformer | RGROUNDPRIM_DEFTF | Primary grounding resistance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
41 | Default Transformer | XGROUNDPRIM_DEFTF | Primary grounding reactance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
42 | Default Transformer | RGROUNDSEC_DEFTF | Secondary grounding resistance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
43 | Default Transformer | XGROUNDSEC_DEFTF | Secondary grounding reactance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
44 | Default Transformer | RGROUNDTERT_DEFTF | Tertiary grounding resistance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
45 | Default Transformer | XGROUNDTERT_DEFTF | Tertiary grounding reactance (ohms). | Float | ohms | ohms | DPF | 0 | 100 | 0 | 100
46 | Default Transformer | PRNORMTAP_DEFTF | Primary normal tap setting. | Integer | count | count | DPF | -50 | 50 | -50 | 50
47 | Default Transformer | SCNORMTAP_DEFTF | Secondary normal tap setting. | Integer | count | count | DPF | -50 | 50 | -50 | 50
48 | Default Transformer | TENORMTAP_DEFTF | Tertiary normal tap setting. | Integer | count | count | DPF | -50 | 50 | -50 | 50
52 | Default Transformer | PRREVERSEREG_DEFTF | Flag indicating primary winding tap changer has reverse regulation capability. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
53 | Default Transformer | SCREVERSEREG_DEFTF | Flag indicating secondary winding tap changer has reverse regulation capability. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
54 | Default Transformer | TEREVERSEREG_DEFTF | Flag indicating tertiary winding tap changer has reverse regulation capability. | Boolean | Boolean | Boolean | DPF | #N/A | #N/A | #N/A | #N/A
55 | Default Transformer | PRCTFULLAMPS_DEFTF | Primary winding CT full load secondary rating in amps. | Float | amps | amps | DPF | 0 | 20 | 0 | 20
56 | Default Transformer | SCCTFULLAMPS_DEFTF | Secondary winding CT full load secondary rating in amps. | Float | amps | amps | DPF | 0 | 20 | 0 | 20
57 | Default Transformer | TECTFULLAMPS_DEFTF | Tertiary winding CT full load secondary rating in amps. | Float | amps | amps | DPF | 0 | 20 | 0 | 20
58 | Default Transformer | NOTLOADED_DEFTF | A flag indicating the transformer has no secondary loads attached (true = no loads are connected). | Boolean | Boolean | Boolean | OPS | #N/A | #N/A | #N/A | #N/A

## Query Objects
Sort | Query Object Type | Record Description | Record Name | Input or Output | Queryable Field Name | Description | Attribute Type | Scope | Units (Metric) | Units (Imperial) | Related Record
1 | Virtual Object | Abnormal | ABNRML | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
2 | Virtual Object | Abnormal | ABNRML |  | DNOMRECORDNAME | The DNOM record name | String
3 | Virtual Object | Abnormal | ABNRML |  | ISORPHAN | Flag indicating that the abnormal component is an orphan | Boolean
4 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | ALARMSTATUS | Alarm status (None, DER Fault Over Current, DER Fault Over Voltage, DER Fault Under Voltage, DER Fault Over Frequency, DER Fault Under Frequency, DER Fault Voltage Imbalance, DER Fault Current Imbalance, DER Fault Emergency Local, DER Fault Emergency Remote, DER Fault Low Power Input, or DER Fault Phase Rotation). | String
5 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | AUTOMATICRECONNECTCAPABILITY | Specifies whether the energy resource can automatically reconnect to the system when the system voltage is restored. | Boolean
6 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | COMMUNICATIONSTATUS | Communication status (Online, Suspect, Offline, Replaced, or Unknown). | String
7 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | CONNECTEDSTATUS | Connection status (0 = Disconnected, 1 = Connected). | Enumeration
8 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | CONNECTIONSTATUSTXT | Connection status (Connected or Disconnected). | String
9 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | CONTROLTYPENAME | DER connection source (SCADA, 2030.5 Gateway, or None) | String
10 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXCHARGERATE | Maximum charging rate in kW. | Float |  | kW | kW
11 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXDISCHARGERATE | Maximum discharge rate in kW. | Float |  | kW | kW
12 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXKVA | Maximum apparent power in kVA | Float |  | kVA | kVA
13 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXKVAR | Maximum reactive power in kVAR. | Float |  | kVAR | kVAR
14 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXKVARNEG | Maximum negative reactive power in kVAR | Float |  | kVAR | kVAR
15 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MAXKW | Maximum real power in kW. | Float |  | kW | kW
16 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MINPFOVEREXCITED | Minimum power factor when overexcited. | Float
17 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | MINPFUNDEREXCITED | Minimum power factor when underexcited. | Float
18 | DNOM Component | All Energy Sources | ALLENERGYSOURCE | input | PLANNEDRESTORATIONTIMEVALUE | Planned restoration time after re-energization of the feeder (seconds). | Integer |  | seconds
19 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESCAP | All energy resource capacity | Float
20 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESMANCONTRIBUTESTOFAULTCURRENTTARGET | Manual value of the "Can contribute to fault current during SSC or PRV" flag. Used instead of ALLESMANLVRTTARGET. | Boolean
21 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESMANLVRTTARGET | Manual value of the low voltage ride through" flag. Deprecated, use ALLESMANCONTRIBUTESTOFAULTCURRENTTARGET instead. | Boolean
22 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESMANPTARGET | Manual real power target (percent) | Float
23 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESMANQTARGET | Manual reactive power target (percent) | Float
24 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESMANVTARGET | Manual voltage target (percent) | Float
25 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESPTARGET | Real power target | Float
26 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESQTARGET | Reactive power target | Float
27 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ALLESVTARGET | Voltage target | Float
28 | Virtual Object | All Energy Sources | ALLENERGYSOURCE | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
29 | Virtual Object | All Energy Sources | ALLENERGYSOURCE | input | CHARGESCHDNAME | Charge schedule name | String
30 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | CONNECTSTATUS | Connection status of the energy resouce (Connected or Disconnected) | String
31 | Virtual Object | All Energy Sources | ALLENERGYSOURCE | input | ENERGYPRIMARYSOURCE | Primary energy source? | Boolean
32 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ESMANSOC | Manually entered state of charge value, which is the amount of charge that is currently stored in the DER storage device. State of Charge is specified as a percentage of the device's capacity in kWh (for example, 60 = 60%). | Float
33 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASCONTRIBUTESTOFAULTCURRENTOVERRIDE | Can contribute to fault current during SSC or PRV? Used instead of HASLVRTOVERRIDE. | Boolean
34 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASLVRTOVERRIDE | Low voltage ride through enabled? (Deprecated, use HASCONTRIBUTESTOFAULTCURRENTOVERRIDE instead) | Boolean
35 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASMANUALENTRY | Indicates if one or some fields of the energy resource have value override | Boolean
36 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASOUTPUTOVERRIDE | Indicates whether the device has real or reactive power output override value | Boolean
37 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASPTARGETOVERRIDE | Indicates whether the device has real power override target | Boolean
38 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASQTARGETOVERRIDE | Indicates whether the device has reactive power override target | Boolean
39 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASSOCOVERRIDE | Indicates whether the device has a manually entered state of charge value | Boolean
40 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | HASVTARGETOVERRIDE | Indicates whether the device has voltage override target | Boolean
41 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ISCONNECTED | Is connected? | Boolean
42 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | ISENGYRES | Indicates whether the device is energy resource | Boolean
43 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMCONTRIBUTESTOFAULTCURRENTTARGET | Nominal value of the "Can contribute to fault current during SSC or PRV" flag. Used instead of NOMLVRTTARGET. | Boolean
44 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMLVRTTARGET | Nominal value of the low voltage ride through" flag. Deprecated, use NOMCONTRIBUTESTOFAULTCURRENTTARGET instead. | Boolean
45 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMPTARGET | Nominal real power target (percent) | Float
46 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMQTARGET | Nominal reactive power target (percent) | Float
47 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMVOLT | Nominal voltage (kV line to ground) | Float |  | kV
48 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | NOMVTARGET | Nominal voltage target (percent) | Float
49 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | PHASESENSED | Phases that are sensed (measured). Valid entries include A, B, C, AB, BC, CA, or ABC. | String
50 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | PSCHDNAME | Name of the real power schedule | String
51 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | QSCHDNAME | Name of the reactive power schedule | String
52 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | RATEDAPM | All energy resource rated current | Float |  | Amps | Amps
53 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | RATEDPOWERFACTOR | All energy resource rated power factor | Float
54 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | SCADASETONOFF | Specifies whether the connection status SCADA measurement is available for an energy resource. If available (=True), the Connection Status toolbar button is disabled for an energy resource. | Boolean
55 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | SUSPECTSTATUS | The generator/energy resource connection status is suspect? | Boolean
56 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | TYPENAME | Name of the device type(e.g. SUB, LOAD) | String
57 | Virtual Object | All Energy Sources | ALLENERGYSOURCE |  | VSCHDNAME | Name of the voltage schedule | String
58 | Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | output | COMPLEXAMPA | Phase A current in Amps | Float |  | Amps | Amps
59 | Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | output | COMPLEXAMPB | Phase B current in Amps | Float |  | Amps | Amps
60 | Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | output | COMPLEXAMPC | Phase C current in Amps | Float |  | Amps | Amps
61 | Virtual Object | Transformer Component | ALLTF | input | ALTID | Returns the ADDRESS | String
62 | Virtual Object | Transformer Component | ALLTF | output | AUTOTFVOLTDROPLIMT | Auto transformer voltage drop limit | Float
63 | Virtual Object | Transformer Component | ALLTF | input | CONNECTLOAD1 | The ID of connected load 1 | String
64 | Virtual Object | Transformer Component | ALLTF | input | CONNECTLOAD2 | The ID of connected load 2 | String
65 | Virtual Object | Transformer Component | ALLTF | input | CONNECTLOAD3 | The ID of connected load 3 | String
66 | Virtual Object | Transformer Component | ALLTF | input | CONNECTLOAD4 | The ID of connected load 4 | String
67 | Virtual Object | Transformer Component | ALLTF | output | COPPERLOSSKVAR | Total reactive power copper loss (kVAR) | Float
68 | Virtual Object | Transformer Component | ALLTF | output | COPPERLOSSKW | Total real power copper loss (kW). | Float
69 | Virtual Object | Transformer Component | ALLTF | output | COPPERLOSSVAR | Total reactive power copper loss (VAR) | Float
70 | Virtual Object | Transformer Component | ALLTF | output | COPPERLOSSW | Total real power copper loss (W). | Float
71 | Virtual Object | Transformer Component | ALLTF | output | CORELOSSKVAR | Total reactive power core loss (kVAR). | Float
72 | Virtual Object | Transformer Component | ALLTF | output | CORELOSSKW | Total real power core loss (kW) | Float
73 | Virtual Object | Transformer Component | ALLTF | output | CORELOSSVAR | Total reactive power core loss (VAR). | Float
74 | Virtual Object | Transformer Component | ALLTF | output | CORELOSSW | Total real power core loss (W) | Float
75 | Virtual Object | Transformer Component | ALLTF | input | DELTASECPHASEGRND | Grounded phase winding for a transformer with a delta connected secondary. | String
76 | Virtual Object | Transformer Component | ALLTF | output | DISTTFVOLTDROPLIMT | Distribution transformer voltage drop limit | Float
77 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW1 | Connecting elbow switch 1 name (for underground transformers). | String
78 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW2 | Connecting elbow switch 2 name (for underground transformers). | String
79 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW3 | Connecting elbow switch 3 name (for underground transformers). | String
80 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW4 | Connecting elbow switch 4 name (for underground transformers). | String
81 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW5 | Connecting elbow switch 5 name (for underground transformers). | String
82 | Virtual Object | Transformer Component | ALLTF | input | ELBOWSW6 | Connecting elbow switch 6 name (for underground transformers). | String
83 | Virtual Object | Transformer Component | ALLTF |  | ELBOWSWLIST | Enumeration of elbow switches that are connected to the transformer | String
84 | Virtual Object | Transformer Component | ALLTF | input | NOMCORELOSSKW | Nominal magnetizing loss in KW. | Float
85 | Virtual Object | Transformer Component | ALLTF | input | NOMCORELOSSW | Nominal magnetizing loss in W. | Float
86 | Virtual Object | Transformer Component | ALLTF | output | NOMTFLIM1 | The flow violation limits level. | Float
87 | Virtual Object | Transformer Component | ALLTF | input | NUMCUSTA | The number of phase A only connected customers. | Integer
88 | Virtual Object | Transformer Component | ALLTF | input | NUMCUSTABC | The total number of connected customers. | Integer
89 | Virtual Object | Transformer Component | ALLTF | input | NUMCUSTB | The number of phase B only connected customers. | Integer
90 | Virtual Object | Transformer Component | ALLTF | input | NUMCUSTC | The number of phase C only connected customers. | Integer
91 | Virtual Object | Transformer Component | ALLTF | output | POWERTFVOLTDROPLIMT | Power transformer voltage drop limit | Float
92 | Virtual Object | Transformer Component | ALLTF | output | PRIMAWINDAMPS | High side phase A amps. | Float
93 | Virtual Object | Transformer Component | ALLTF | output | PRIMBWINDAMPS | High side phase B amps. | Float
94 | Virtual Object | Transformer Component | ALLTF | output | PRIMCWINDAMPS | High side phase C amps. | Float
95 | Virtual Object | Transformer Component | ALLTF | output | PRIMPHAGEROTATONANGLE | Not applicable (always returns "--") | Float
96 | Virtual Object | Transformer Component | ALLTF | input | PRIMTFWIND | Primary winding connection type. Return “Delta”, “Wye”, “Open Delta”, or “Open Wye”. | String
97 | Virtual Object | Transformer Component | ALLTF | output | REGULATORVOLTDROPLIMT | Regulator voltage drop limit | Float
98 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJAVAILCAPKVA1 | Level 1 limit minus reserved capacity adjusted flow. | String
99 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA1SEC | Level 1 limit minus reserved capacity adjusted flow, secondary side | String |  |  | kVA
100 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA1TERT | Level 1 limit minus reserved capacity adjusted flow, tertiary side. | String |  |  | kVA
101 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJAVAILCAPKVA2 | Level 2 limit minus reserved capacity adjusted flow. | String
102 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA2SEC | Level 2 limit minus reserved capacity adjusted flow, secondary side. | String |  |  | kVA
103 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA2TERT | Level 2 limit minus reserved capacity adjusted flow, tertiary side. | String |  |  | kVA
104 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJAVAILCAPKVA3 | Level 3 limit minus reserved capacity adjusted flow. | String
105 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA3SEC | Level 3 limit minus reserved capacity adjusted flow, secondary side. | String |  |  | kVA
106 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA3TERT | Level 3 limit minus reserved capacity adjusted flow, tertiary side. | String |  |  | kVA
107 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJAVAILCAPKVA4 | Level 4 limit minus reserved capacity adjusted flow. | String
108 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA4SEC | Level 4 limit minus reserved capacity adjusted flow, secondary side. | String |  |  | kVA
109 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA4TERT | Level 4 limit minus reserved capacity adjusted flow, tertiary side. | String |  |  | kVA
110 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJAVAILCAPKVA5 | Level 5 limit minus reserved capacity adjusted flow. | String
111 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA5SEC | Level 5 limit minus reserved capacity adjusted flow, secondary side. | String |  |  | kVA
112 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJAVAILCAPKVA5TERT | Level 5 limit minus reserved capacity adjusted flow, tertiary side. | String |  |  | kVA
113 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJFLOW | The transformer loading in kVA plus reserved capacity in kVA. | String
114 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJFLOWSEC | The transformer loading in kVA plus reserved capacity in kVA, secondary side. | String |  |  | kVA
115 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJFLOWTERT | The transformer loading in kVA plus reserved capacity in kVA, tertiary side. | String |  |  | kVA
116 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJLOADING1 | The percentage loading using level 1 limit and reserved capacity adjusted flow. | String
117 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING1SEC | The percentage loading using level 1 limit and reserved capacity adjusted flow, secondary side | String |  |  | %
118 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING1TERT | The percentage loading using level 1 limit and reserved capacity adjusted flow, tertiary side | String |  |  | %
119 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJLOADING2 | The percentage loading using level 2 limit and reserved capacity adjusted flow. | String
120 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING2SEC | The percentage loading using level 2 limit and reserved capacity adjusted flow, secondary side | String |  |  | %
121 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING2TERT | The percentage loading using level 2 limit and reserved capacity adjusted flow, tertiary side | String |  |  | %
122 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJLOADING3 | The percentage loading using level 3 limit and reserved capacity adjusted flow. | String
123 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING3SEC | The percentage loading using level 3 limit and reserved capacity adjusted flow, secondary side | String |  |  | %
124 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING3TERT | The percentage loading using level 3 limit and reserved capacity adjusted flow, tertiary side | String |  |  | %
125 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJLOADING4 | The percentage loading using level 4 limit and reserved capacity adjusted flow. | String
126 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING4SEC | The percentage loading using level 4 limit and reserved capacity adjusted flow, secondary side | String |  |  | %
127 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING4TERT | The percentage loading using level 4 limit and reserved capacity adjusted flow, tertiary side | String |  |  | %
128 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYADJLOADING5 | The percentage loading using level 5 limit and reserved capacity adjusted flow. | String
129 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING5SEC | The percentage loading using level 5 limit and reserved capacity adjusted flow, secondary side | String |  |  | %
130 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYADJLOADING5TERT | The percentage loading using level 5 limit and reserved capacity adjusted flow, tertiary side | String |  |  | %
131 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYDERATEDLIMITLOADING1 | The percentage loading using level 1 derated limit and actual flow. | String
132 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING1SEC | The percentage loading using level 1 derated limit and actual flow, secondary side | String |  |  | %
133 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING1TERT | The percentage loading using level 1 derated limit and actual flow, tertiary side | String |  |  | %
134 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYDERATEDLIMITLOADING2 | The percentage loading using level 2 derated limit and actual flow. | String
135 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING2SEC | The percentage loading using level 2 derated limit and actual flow, secondary side | String |  |  | %
136 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING2TERT | The percentage loading using level 2 derated limit and actual flow, tertiary side | String |  |  | %
137 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYDERATEDLIMITLOADING3 | The percentage loading using level 3 derated limit and actual flow. | String
138 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING3SEC | The percentage loading using level 3 derated limit and actual flow, secondary side | String |  |  | %
139 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING3TERT | The percentage loading using level 3 derated limit and actual flow, tertiary side | String |  |  | %
140 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYDERATEDLIMITLOADING4 | The percentage loading using level 4 derated limit and actual flow. | String
141 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING4SEC | The percentage loading using level 4 derated limit and actual flow, secondary side | String |  |  | %
142 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING4TERT | The percentage loading using level 4 derated limit and actual flow, tertiary side | String |  |  | %
143 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYDERATEDLIMITLOADING5 | The percentage loading using level 5 derated limit and actual flow. | String
144 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING5SEC | The percentage loading using level 5 derated limit and actual flow, secondary side | String |  |  | %
145 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYDERATEDLIMITLOADING5TERT | The percentage loading using level 5 derated limit and actual flow, tertiary side | String |  |  | %
146 | Virtual Object | Transformer Component | ALLTF | input | RESERVEDCAPACITYKVA | The capacity reserved due to the impact of reserved capacity objects. | String |  | kVA | kVA
147 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYKVASEC | The capacity reserved due to the impact of reserved capacity objects, secondary side. | String |  |  | kVA
148 | Virtual Object | Transformer Component | ALLTF |  | RESERVEDCAPACITYKVATERT | The capacity reserved due to the impact of reserved capacity objects, tertiary side. | String |  |  | kVA
149 | Virtual Object | Transformer Component | ALLTF |  | SEC1ABCWINDKVA | Low side three phase apparent power (kVA) | Float |  | kVA | kVA
150 | Virtual Object | Transformer Component | ALLTF | output | SEC1ABCWINDPF | Low side phase ABC power factor. | Float
151 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDKVA | Low side phase A apparent power (kVA). | Float
152 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDKVAR | Low side phase A reactive power flow (kVAR). | Float
153 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDKVARFABS | Reactive flow value of secondary Phase A (absolute value). | Float
154 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDKW | Low side phase A real power flow (kW). | Float
155 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDKWFABS | Real power flow value of secondary Phase A (absolute value). | Float
156 | Virtual Object | Transformer Component | ALLTF | output | SEC1AWINDPF | Low side phase A power factor. | Float
157 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDKVA | Low side phase B apparent power (kVA). | Float
158 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDKVAR | Low side phase B reactive power flow (kVAR). | Float
159 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDKVARFABS | Reactive flow value of secondary Phase B (absolute value). | Float
160 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDKW | Low side phase B real power flow (kW). | Float
161 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDKWFABS | Real power flow value of secondary Phase B (absolute value). | Float
162 | Virtual Object | Transformer Component | ALLTF | output | SEC1BWINDPF | Low side phase B power factor. | Float
163 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDKVA | Low side phase C apparent power (kVA). | Float
164 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDKVAR | Low side phase C reactive power flow (kVAR). | Float
165 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDKVARFABS | Reactive flow value of secondary Phase C (absolute value). | Float
166 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDKW | Low side phase C real power flow (kW). | Float
167 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDKWFABS | Real power flow value of secondary Phase C (absolute value). | Float
168 | Virtual Object | Transformer Component | ALLTF | output | SEC1CWINDPF | Low side phase C power factor. | Float
169 | Virtual Object | Transformer Component | ALLTF | output | SECAWINDAMPS | Low side phase A amps. | Float
170 | Virtual Object | Transformer Component | ALLTF | output | SECBWINDAMPS | Low side phase B amps. | Float
171 | Virtual Object | Transformer Component | ALLTF | output | SECCWINDAMPS | Low side phase C amps. | Float
172 | Virtual Object | Transformer Component | ALLTF | output | SECLAGSPRIMPHAGEANGLE | Secondary to primary winding phase angle shift in degrees. | Float
173 | Virtual Object | Transformer Component | ALLTF | input | SECTFWIND | Secondary winding connection type. Return “Delta”, “Wye”, “Open Delta”, or “Open Wye”. | String
174 | Virtual Object | Transformer Component | ALLTF | output | STEPTFVOLTDROPLIMT | StepUpDown transformer voltage drop limit | Float
175 | Virtual Object | Transformer Component | ALLTF | output | TERTLAGSPRIMPHAGEANGLE | Tertiary to primary winding phase angle shift in degrees (not applicable for two winding transformers). | Float
176 | Virtual Object | Transformer Component | ALLTF | input | TERTTFWIND | Tertiary winding connection type. Return “Delta”, “Wye”, “Open Delta”, or “Open Wye”. | String
177 | Virtual Object | Transformer Component | ALLTF | output | TFAVERAGEVOLTDIFF | Average voltage drop between primary and secondary side | Float
178 | Virtual Object | Transformer Component | ALLTF | output | TFAVERAGEVOLTPRIM | Primary side average voltage | Float
179 | Virtual Object | Transformer Component | ALLTF | output | TFAVERAGEVOLTSEC | Secondary side average voltage | Float
180 | Virtual Object | Transformer Component | ALLTF | input | TFBANKCODE | Bank code | String
181 | Virtual Object | Transformer Component | ALLTF | input | TFBANKCONNECTED | Flag indicating whether the transformer bank is connected to the network | Boolean
182 | Virtual Object | Transformer Component | ALLTF | input | TFBANKDISCONNECTED | Flag indicating whether the transformer bank is disconnected from the network | Boolean
183 | Virtual Object | Transformer Component | ALLTF | input | TFBANKLIST | The list of transformers of the same type in the same transformer bank. | String
184 | Virtual Object | Transformer Component | ALLTF | input | TFCONNECTED | Flag indicating whether the transformer is connected to the network | Boolean
185 | Virtual Object | Transformer Component | ALLTF | input | TFDERATEDLIM1 | Transformer derated limit 1 | String |  | kVA | kVA
186 | Virtual Object | Transformer Component | ALLTF | input | TFDERATEDLIM2 | Transformer derated limit 2 | String |  | kVA | kVA
187 | Virtual Object | Transformer Component | ALLTF | input | TFDERATEDLIM3 | Transformer derated limit 3 | String |  | kVA | kVA
188 | Virtual Object | Transformer Component | ALLTF | input | TFDERATEDLIM4 | Transformer derated limit 4 | String |  | kVA | kVA
189 | Virtual Object | Transformer Component | ALLTF | input | TFDERATEDLIM5 | Transformer derated limit 5 | String |  | kVA | kVA
190 | Virtual Object | Transformer Component | ALLTF | input | TFDYNLIM1 | Transformer dynamic limit 1 | String |  | kVA | kVA
191 | Virtual Object | Transformer Component | ALLTF | input | TFDYNLIM2 | Transformer dynamic limit 2 | String |  | kVA | kVA
192 | Virtual Object | Transformer Component | ALLTF | input | TFDYNLIM3 | Transformer dynamic limit 3 | String |  | kVA | kVA
193 | Virtual Object | Transformer Component | ALLTF | input | TFDYNLIM4 | Transformer dynamic limit 4 | String |  | kVA | kVA
194 | Virtual Object | Transformer Component | ALLTF | input | TFDYNLIM5 | Transformer dynamic limit 5 | String |  | kVA | kVA
195 | Virtual Object | Transformer Component | ALLTF | input | TFDYNREGSTEP1 | Transformer dynamic regulation step 1 | String
196 | Virtual Object | Transformer Component | ALLTF | input | TFDYNREGSTEP2 | Transformer dynamic regulation step 2 | String
197 | Virtual Object | Transformer Component | ALLTF | input | TFDYNREGSTEP3 | Transformer dynamic regulation step 3 | String
198 | Virtual Object | Transformer Component | ALLTF | input | TFDYNREGSTEP4 | Transformer dynamic regulation step 4 | String
199 | Virtual Object | Transformer Component | ALLTF | input | TFDYNREGSTEP5 | Transformer dynamic regulation step 5 | String
200 | Virtual Object | Transformer Component | ALLTF | input | TFEXCITCURR | Average excitation current in percent based on transformer rating (optional if the power factor is given). | Float
201 | Virtual Object | Transformer Component | ALLTF | output | TFFROMA | PhaseA voltage in primary side | Float
202 | Virtual Object | Transformer Component | ALLTF | output | TFFROMB | PhaseB voltage in primary side | Float
203 | Virtual Object | Transformer Component | ALLTF | output | TFFROMC | PhaseC voltage in primary side | Float
204 | Virtual Object | Transformer Component | ALLTF | output | TFFROMNODEAMPG | From side zero sequence amp flow (amps magnitude and angle). | Float
205 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHV | High side average voltage magnitude on configurable voltage base. | Float
206 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVAACTLL | High side phase A voltage (line to line, magnitude on configurable voltage base and angle). | Float
207 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVAANGLE | High side phase Aline to ground voltage angle (Degree). | Float
208 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANA | High side phase A voltage (magnitude on configurable voltage base and angle). | Float
209 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANALG | High side phase A LG voltage (magnitude on configurable voltage base and angle). | Float
210 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANALL | High side phase A LL voltage (magnitude on configurable voltage base and angle). | Float
211 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANB | High side phase B voltage (magnitude on configurable voltage base and angle). | Float
212 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANBLG | High side phase B LG voltage (magnitude on configurable voltage base and angle). | Float
213 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANBLL | High side phase B LL voltage (magnitude on configurable voltage base and angle). | Float
214 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANC | High side phase C voltage (magnitude on configurable voltage base and angle). | Float
215 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANCLG | High side phase C LG voltage (magnitude on configurable voltage base and angle). | Float
216 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANCLL | High side phase C LL voltage (magnitude on configurable voltage base and angle). | Float
217 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANN | High side phase N voltage (magnitude on configurable voltage base and angle). | Float
218 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANNLG | High side phase N LG voltage (magnitude on configurable voltage base and angle). | Float
219 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVANNLL | High side phase N LL voltage (magnitude on configurable voltage base and angle). | Float
220 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVAVG | High side average voltage magnitude on configurable voltage base. | Float
221 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVBACTLL | High side phase B voltage (line to line, magnitude on configurable voltage base and angle). | Float
222 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVBANGLE | High side phase B line to ground voltage angle (Degree). | Float
223 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVCACTLL | High side phase C voltage (line to line, magnitude on configurable voltage base and angle). | Float
224 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVCANGLE | High side phase C line to ground voltage angle (Degree). | Float
225 | Virtual Object | Transformer Component | ALLTF | input | TFHIGHVNOMLL | Primary rated voltage level voltage (kV line to line). | Float
226 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVOLT120 | High side average voltage magnitude (in 120 V base). | Float
227 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVOPA | High side phase A voltage magnitude on configurable voltage base. | Float
228 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVOPB | High side phase B voltage magnitude on configurable voltage base. | Float
229 | Virtual Object | Transformer Component | ALLTF | output | TFHIGHVOPC | High side phase C voltage magnitude on configurable voltage base. | Float
230 | Virtual Object | Transformer Component | ALLTF | input | TFIMPEDANCE | Impedance (R+jX) (per unit on transformer rating). | Float
231 | Virtual Object | Transformer Component | ALLTF | input | TFISBANKED | If the transformer in a transformer bank. | Boolean
232 | Virtual Object | Transformer Component | ALLTF | input | TFISOPEN | Is transformer connected to the network or not | Boolean
233 | Virtual Object | Transformer Component | ALLTF | output | TFKVAD | The KVA demand. | Float
234 | Virtual Object | Transformer Component | ALLTF | output | TFKVARD | The KVAR demand. | Float
235 | Virtual Object | Transformer Component | ALLTF |  | TFKVARLOSS | Reactive power of transformer loss (core loss and copper loss) | Float |  | kV
236 | Virtual Object | Transformer Component | ALLTF | output | TFKWD | The KW demand. | Float
237 | Virtual Object | Transformer Component | ALLTF |  | TFKWLOSS | Real power of transformer loss (core loss and copper loss) | Float |  | kW
238 | Virtual Object | Transformer Component | ALLTF | input | TFLIM1 | Transformer first level nominal flow limit value (MVA, kVA, or amps) | String
239 | Virtual Object | Transformer Component | ALLTF | input | TFLIM1NAME | Transformer first level flow limit name. | String
240 | Virtual Object | Transformer Component | ALLTF | input | TFLIM1SEASON | Transformer first level season name. | String
241 | Virtual Object | Transformer Component | ALLTF | input | TFLIM2 | Transformer second level nominal flow limit value (MVA, kVA, or amps). | String
242 | Virtual Object | Transformer Component | ALLTF | input | TFLIM2NAME | Transformer second level flow limit name. | String
243 | Virtual Object | Transformer Component | ALLTF | input | TFLIM2SEASON | Transformer second level season name. | String
244 | Virtual Object | Transformer Component | ALLTF | input | TFLIM3 | Transformer third level nominal flow limit value (MVA, kVA, or amps). | String
245 | Virtual Object | Transformer Component | ALLTF | input | TFLIM3NAME | Transformer third level flow limit name | String
246 | Virtual Object | Transformer Component | ALLTF | input | TFLIM3SEASON | Transformer third level season name | String
247 | Virtual Object | Transformer Component | ALLTF | input | TFLIM4 | Transformer fourth level nominal flow limit value (MVA, kVA, or amps). | String
248 | Virtual Object | Transformer Component | ALLTF | input | TFLIM4NAME | Transformer fourth level flow limit name. | String
249 | Virtual Object | Transformer Component | ALLTF | input | TFLIM4SEASON | Transformer fourth level season name. | String
250 | Virtual Object | Transformer Component | ALLTF | input | TFLIM5 | Transformer fifth level nominal flow limit value (MVA, kVA, or amps). | String
251 | Virtual Object | Transformer Component | ALLTF | input | TFLIM5NAME | Transformer fifth level flow limit name | String
252 | Virtual Object | Transformer Component | ALLTF | input | TFLIM5SEASON | Transformer fifth level season name | String
253 | Virtual Object | Transformer Component | ALLTF | output | TFLOADPERCENT | Transformer loading level percentage against level 1 limit | Float
254 | Virtual Object | Transformer Component | ALLTF | output | TFLOADRATINGPERCENT | Transformer loading level percentage against rating | Float
255 | Virtual Object | Transformer Component | ALLTF | output | TFLOWV | Low side average voltage magnitude on configurable voltage base. | Float
256 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVAACTLL | Low side phase A voltage (line to line, magnitude on configurable voltage base and angle). | Float
257 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVAANGLE | Low side phase A line to ground voltage angle (Degree). | Float
258 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVACTLL | Low side average voltage magnitude on configurable voltage base. | Float
259 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANA | Low side phase A voltage (magnitude on configurable voltage base and angle). | Float
260 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANALG | Low side phase A LG voltage (magnitude on configurable voltage base and angle). | Float
261 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANALL | Low side phase A LL voltage (magnitude on configurable voltage base and angle). | Float
262 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANB | Low side phase B voltage (magnitude on configurable voltage base and angle). | Float
263 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANBLG | Low side phase B LG voltage (magnitude on configurable voltage base and angle). | Float
264 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANBLL | Low side phase B LL voltage (magnitude on configurable voltage base and angle). | Float
265 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANC | Low side phase C voltage (magnitude on configurable voltage base and angle). | Float
266 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANCLG | Low side phase C LG voltage (magnitude on configurable voltage base and angle). | Float
267 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANCLL | Low side phase C LL voltage (magnitude on configurable voltage base and angle). | Float
268 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANN | Low side phase N voltage (magnitude on configurable voltage base and angle). | Float
269 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANNLG | Low side phase N LG voltage (magnitude on configurable voltage base and angle). | Float
270 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVANNLL | Low side phase N LL voltage (magnitude on configurable voltage base and angle). | Float
271 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVAVG | Low side average voltage magnitude on configurable voltage base. | Float
272 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVBACTLL | Low side phase B voltage (line to line, magnitude on configurable voltage base and angle). | Float
273 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVBANGLE | Low side phase B line to ground voltage angle (Degree). | Float
274 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVCACTLL | Low side phase C voltage (line to line, magnitude on configurable voltage base and angle). | Float
275 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVCANGLE | Low side phase C line to ground voltage angle (Degree). | Float
276 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVKV | Low side average voltage magnitude (configurable voltage base). | Float
277 | Virtual Object | Transformer Component | ALLTF | input | TFLOWVNOMLL | Secondary rated voltage level voltage (kV line to line). | Float
278 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVOLT120 | Low side average voltage magnitude (in 120 V base). | Float
279 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVOPA | Low side phase A voltage magnitude on configurable voltage base | Float
280 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVOPB | Low side phase B voltage magnitude on configurable voltage base | Float
281 | Virtual Object | Transformer Component | ALLTF | output | TFLOWVOPC | Low side phase C voltage magnitude on configurable voltage base | Float
282 | Virtual Object | Transformer Component | ALLTF | input | TFMAGNETIZINGPF | Magnetizing power factor (optional if excitation current is provided). | Float
283 | Virtual Object | Transformer Component | ALLTF |  | TFMANLIM | Manual limit value for the transformer | String
284 | Virtual Object | Transformer Component | ALLTF | input | TFMODELSTRINGTYPE | Transformer type. Return “Distribution”, “Regulator”, Power_Tf”, “Auto”, "Step" or "Zigzag". | String
285 | Virtual Object | Transformer Component | ALLTF | input | TFMODELTYPEINDEX | Transformer model type and index. For example, StarStarX (1). | String
286 | Virtual Object | Transformer Component | ALLTF | input | TFNOMHIV | Nominal high side voltage (kV, line to line if the high side winding is delta connected, otherwise line to ground). | Float
287 | Virtual Object | Transformer Component | ALLTF | input | TFNOMLOV | Nominal low side voltage (kV, line to line if the low side winding is delta connected, otherwise line to ground). | Float
288 | Virtual Object | Transformer Component | ALLTF |  | TFPLOSS | Real power losses in the transformer | Float
289 | Virtual Object | Transformer Component | ALLTF | input | TFPRIMIMPEDANCE | Primary winding impedance (R+jX) (per unit on transformer rating). | Float
290 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM1 | Level 1 limit value for the primary tap of the transformer | String
291 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM1NAME | Level 1 limit name for the primary tap of the transformer | String
292 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM1SEASON | Level 1 limit season for the primary tap of the transformer | String
293 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM2 | Level 2 limit value for the primary tap of the transformer | String
294 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM2NAME | Level 2 limit name for the primary tap of the transformer | String
295 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM2SEASON | Level 2 limit season for the primary tap of the transformer | String
296 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM3 | Level 3 limit value for the primary tap of the transformer | String
297 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM3NAME | Level 3 limit name for the primary tap of the transformer | String
298 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM3SEASON | Level 3 limit season for the primary tap of the transformer | String
299 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM4 | Level 4 limit value for the primary tap of the transformer | String
300 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM4NAME | Level 4 limit name for the primary tap of the transformer | String
301 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM4SEASON | Level 4 limit season for the primary tap of the transformer | String
302 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM5 | Level 5 limit value for the primary tap of the transformer | String
303 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM5NAME | Level 5 limit name for the primary tap of the transformer | String
304 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMLIM5SEASON | Level 5 limit season for the primary tap of the transformer | String
305 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMRATING | Primary side rating | Float |  | kVA | kVA
306 | Virtual Object | Transformer Component | ALLTF |  | TFPRIMRATINGUNIT | Primary side regulation capability and rating (kVA or MVA) | Float |  | kVA or MVA | kVA or MVA
307 | Virtual Object | Transformer Component | ALLTF |  | TFQLOSS | Reactive power losses in the transformer | Float
308 | Virtual Object | Transformer Component | ALLTF | input | TFRATING | Rated capacity in kVA. | Float |  | kVA | kVA
309 | Virtual Object | Transformer Component | ALLTF |  | TFRATINGUNIT | Transformer regulation capability and rating (kVA or MVA) | Float |  | kVA or MVA | kVA or MVA
310 | Virtual Object | Transformer Component | ALLTF |  | TFSECDERATEDLIM1 | Transformer secondary side derated limit value due to reserved capacity limit 1 | Float
311 | Virtual Object | Transformer Component | ALLTF |  | TFSECDERATEDLIM2 | Transformer secondary side derated limit value due to reserved capacity limit 2 | Float
312 | Virtual Object | Transformer Component | ALLTF |  | TFSECDERATEDLIM3 | Transformer secondary side derated limit value due to reserved capacity limit 3 | Float
313 | Virtual Object | Transformer Component | ALLTF |  | TFSECDERATEDLIM4 | Transformer secondary side derated limit value due to reserved capacity limit 4 | Float
314 | Virtual Object | Transformer Component | ALLTF |  | TFSECDERATEDLIM5 | Transformer secondary side derated limit value due to reserved capacity limit 5 | Float
315 | Virtual Object | Transformer Component | ALLTF | input | TFSECIMPEDANCE | Secondary winding impedance (R+jX) (per unit on transformer rating). | Float
316 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM1 | Level 1 limit value for the secondary tap of the transformer | String
317 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM1NAME | Level 1 limit name for the secondary tap of the transformer | String
318 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM1SEASON | Level 1 limit season for the secondary tap of the transformer | String
319 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM2 | Level 2 limit value for the secondary tap of the transformer | String
320 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM2NAME | Level 2 limit name for the secondary tap of the transformer | String
321 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM2SEASON | Level 2 limit season for the secondary tap of the transformer | String
322 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM3 | Level 3 limit value for the secondary tap of the transformer | String
323 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM3NAME | Level 3 limit name for the secondary tap of the transformer | String
324 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM3SEASON | Level 3 limit season for the secondary tap of the transformer | String
325 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM4 | Level 4 limit value for the secondary tap of the transformer | String
326 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM4NAME | Level 4 limit name for the secondary tap of the transformer | String
327 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM4SEASON | Level 4 limit season for the secondary tap of the transformer | String
328 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM5 | Level 5 limit value for the secondary tap of the transformer | String
329 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM5NAME | Level 5 limit name for the secondary tap of the transformer | String
330 | Virtual Object | Transformer Component | ALLTF |  | TFSECLIM5SEASON | Level 5 limit season for the secondary tap of the transformer | String
331 | Virtual Object | Transformer Component | ALLTF |  | TFSECRATING | Secondary side rating | Float |  | kVA | kVA
332 | Virtual Object | Transformer Component | ALLTF |  | TFSECRATINGUNIT | Secondary side regulation capability and rating (kVA or MVA) | Float |  | kVA or MVA | kVA or MVA
333 | Virtual Object | Transformer Component | ALLTF | input | TFSIZE | Rated capacity in kVA or MVA. | Float |  | kVA or MVA | kVA or MVA
334 | Virtual Object | Transformer Component | ALLTF | output | TFSVCV | Estimated average service drop voltage magnitude (configurable voltage base). | Float
335 | Virtual Object | Transformer Component | ALLTF |  | TFSZIZE | Transformer rating (kVA or MVA) | Float |  | kVA or MVA | kVA or MVA
336 | Virtual Object | Transformer Component | ALLTF | output | TFTERNODEAMPG | Tertiary side zero sequence amp flow (amps magnitude and angle). | Float
337 | Virtual Object | Transformer Component | ALLTF |  | TFTERTDERATEDLIM1 | Transformer tertiary side derated limit value due to reserved capacity limit 1 | Float
338 | Virtual Object | Transformer Component | ALLTF |  | TFTERTDERATEDLIM2 | Transformer tertiary side derated limit value due to reserved capacity limit 2 | Float
339 | Virtual Object | Transformer Component | ALLTF |  | TFTERTDERATEDLIM3 | Transformer tertiary side derated limit value due to reserved capacity limit 3 | Float
340 | Virtual Object | Transformer Component | ALLTF |  | TFTERTDERATEDLIM4 | Transformer tertiary side derated limit value due to reserved capacity limit 4 | Float
341 | Virtual Object | Transformer Component | ALLTF |  | TFTERTDERATEDLIM5 | Transformer tertiary side derated limit value due to reserved capacity limit 5 | Float
342 | Virtual Object | Transformer Component | ALLTF | input | TFTERTIMPEDANCE | Tertiary winding impedance (R+jX) (per unit on transformer rating). | Float
343 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM1 | Level 1 limit value for the tertiary tap of the transformer | String
344 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM1NAME | Level 1 limit name for the tertiary tap of the transformer | String
345 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM1SEASON | Level 1 limit season for the tertiary tap of the transformer | String
346 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM2 | Level 2 limit value for the tertiary tap of the transformer | String
347 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM2NAME | Level 2 limit name for the tertiary tap of the transformer | String
348 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM2SEASON | Level 2 limit season for the tertiary tap of the transformer | String
349 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM3 | Level 3 limit value for the tertiary tap of the transformer | String
350 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM3NAME | Level 3 limit name for the tertiary tap of the transformer | String
351 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM3SEASON | Level 3 limit season for the tertiary tap of the transformer | String
352 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM4 | Level 4 limit value for the tertiary tap of the transformer | String
353 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM4NAME | Level 4 limit name for the tertiary tap of the transformer | String
354 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM4SEASON | Level 4 limit season for the tertiary tap of the transformer | String
355 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM5 | Level 5 limit value for the tertiary tap of the transformer | String
356 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM5NAME | Level 5 limit name for the tertiary tap of the transformer | String
357 | Virtual Object | Transformer Component | ALLTF |  | TFTERTLIM5SEASON | Level 5 limit season for the tertiary tap of the transformer | String
358 | Virtual Object | Transformer Component | ALLTF |  | TFTERTRATING | Tertiary side rating | Float |  | kVA | kVA
359 | Virtual Object | Transformer Component | ALLTF |  | TFTERTRATINGUNIT | Tertiary side rating (kVA or MVA) | Float |  | kVA or MVA | kVA or MVA
360 | Virtual Object | Transformer Component | ALLTF | output | TFTERV | Tertiary side average voltage magnitude on configurable voltage base. | Float
361 | Virtual Object | Transformer Component | ALLTF | output | TFTOA | PhaseA voltage in secondary side | Float
362 | Virtual Object | Transformer Component | ALLTF | output | TFTOB | PhaseB voltage in secondary side | Float
363 | Virtual Object | Transformer Component | ALLTF | output | TFTOC | PhaseC voltage in secondary side | Float
364 | Virtual Object | Transformer Component | ALLTF | output | TFTONODEAMPG | To side zero sequence amp flow (amps magnitude and angle). | Float
365 | Virtual Object | Transformer Component | ALLTF | output | TFTOTALPF | Transformer total power factor | Float
366 | Virtual Object | Transformer Component | ALLTF | input | TFTYPE | Transformer type. | String
367 | Virtual Object | Transformer Component | ALLTF | output | TFVOLTDROPEXCEEDED | Flag if the voltage drop of the transformer(power/auto/step/regulator) exceed limit | Integer
368 | Virtual Object | Transformer Component | ALLTF | input | VOLTTE | Nominal tertiary voltage (kV line to ground) | Float
369 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMG_FROM_MISL_ID | ID of the from node | String
370 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMG_TO_MISL_ID | ID of the to node | String
371 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_ISVALID | A flag indicating that the measurement group is invalid | Boolean
372 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KVARA | Phase A reactive power | Float |  | kVAR | kVAR
373 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KVARB | Phase B reactive power | Float |  | kVAR | kVAR
374 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KVARC | Phase C reactive power | Float |  | kVAR | kVAR
375 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KWA | Phase A real power | Float |  | kW | kW
376 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KWB | Phase B real power | Float |  | kW | kW
377 | DNOM Component | Analog Measurement Group | AMSGRP |  | AMSG_KWC | Phase C real power | Float |  | kW | kW
378 | DNOM Component | Analog Measurement Group | AMSGRP |  | ANMGTYPE | Analog measurement group type (based on measurements that form the group) | Enumeration
379 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE | Pointer to the common node for all of the measurements | String
380 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.AREAID | Index in the station permission area list | Integer |  |  |  | DNMOBJ
381 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
382 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
383 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
384 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.ID | ID of the node | String |  |  |  | DNMOBJ
385 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
386 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
387 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.NTPFL | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
388 | DNOM Component | Analog Measurement Group | AMSGRP | input | COMMNODE.VOLTC | Node mask | Integer |  |  |  | NODE
389 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT | Pointer to the associated feeder (for a manual entry) | String
390 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.ADDRESS | The feeder address | String |  |  |  | FDR
391 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.ALTERNATENAME | Alternate name of the looped feeder | String |  |  |  | FDR
392 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
393 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
394 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.DEFCOLOR | Default color | Integer |  |  |  | FDR
395 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
396 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
397 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
398 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
399 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
400 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
401 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
402 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
403 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.ID | Unique and persistent ID of the looped feeder | String |  |  |  | DNMOBJ
404 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
405 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
406 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
407 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
408 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
409 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
410 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
411 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
412 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
413 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
414 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
415 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NAME | Name of the looped feeder | String |  |  |  | DNMOBJ
416 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
417 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
418 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
419 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String |  |  |  | FDR
420 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
421 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
422 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
423 | DNOM Component | Analog Measurement Group | AMSGRP | input | FDMANENT.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
424 | DNOM Component | Analog Measurement Group | AMSGRP | input | ID | Object unique ID | String |  |  |  | DNMOBJ
425 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL | Array of analog measurements | String
426 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.AREANAME | Area name - only for area load measurements (MW) | String |  |  |  | MEAS
427 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.DEFQUALITY | Default quality | Integer |  |  |  | MEAS
428 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.DEFVALUE | Analog measurement default value | Integer |  |  |  | MEAS
429 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.DNAFTRIG | Flag indicating that DNAF should consider this measurement when performing a rate of change trigger check (such as feeder head amps or voltage measurements) | Boolean |  |  |  | MEAS
430 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.DNOMID | DNOM ID | String |  |  |  | MEAS
431 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.EFFECTIVEDEVICEID | ID of the effective device | String |  |  |  | MEAS
432 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.iMeasurementTypeId | Converter - Measurement type (flow, status, other). | Integer |  |  |  | MEAS
433 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.iPhase | The phase the measurement is on (A, B, C, or three-phase) | Integer |  |  |  | MEAS
434 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.ISANALOG | Flag indicating whether the measurement is an analog or a status measurement (true = analog, false = status) | Boolean |  |  |  | MEAS
435 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.ISSTATMS | A flag indicating that the measurement is associated with the station and not a specific node or component | Boolean |  |  |  | MEAS
436 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.iTerminalId | Converter - Terminal ID (from-0/to-1/tertiary-2) the measurement is on | Integer |  |  |  | MEAS
437 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.iUnits | Measurement units - kilo or mega for P, Q, S and V measurements | Integer |  |  |  | MEAS
438 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.MBITMASK | Bitmask field for measurements. (bit 0 - normal status value, 1 - current status value, 2 - last status value, 3 - invert value, 4 - BLA obtained, 5 - DDNOM multi state measurement, the combination of SDIS and XDIS is hard coded, 6 - scada multi state measurement, the combination with XDIS = true is defined in config file, 7 - not used now, 8 - has effective device set, 9 - extended current status value, 10 - extended last status value, 11 - extended invert value, 12 - extended BLA obtained, 13 - multi state false value 01, 14 - multi state false value 11, 15 - Not used now, 16 - multichange normal status value, 17 - multichange current status value, 18 - multichange last status value, 19 - multichange invert value, 20 - multi state True value 01, 21 - multi state True value 11, 23 - Meas DNAF flag, 24 - Possible interface voltage measurement, 25 - analogue and status measurement initialized, 26 - Not used now, 27 - Indicates this is a Group Multi-Phase Measurement for a device that has individual phase measurements for the same function. | Integer |  |  |  | MEAS
439 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.MEASBASE | Voltage measurement base value | Integer |  |  |  | MEAS
440 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.MEASCLAS | Measurement classification (analog, status, set point, or control point) | Integer |  |  |  | MEAS
441 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.NOTINIT | Flag indicating that the associated object (component or node) is initially unset from the Converter (model file) | Boolean |  |  |  | MEAS
442 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.OPERATETIME | Measurement operate time | Integer |  |  |  | MEAS
443 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.SIMONLY | A flag indicating a simulated measurement | Boolean |  |  |  | MEAS
444 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.SITENAME | Name of the site | String |  |  |  | MEAS
445 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.STDDEV | Measurement standard deviation | Integer |  |  |  | MEAS
446 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.TIMEOUT | Measurement timeout | Integer |  |  |  | MEAS
447 | DNOM Component | Analog Measurement Group | AMSGRP | input | MEASCOLL.WAITTIME | Measurement wait time | Integer |  |  |  | MEAS
448 | DNOM Component | Analog Measurement Group | AMSGRP |  | NUMMEAS | The number of measurements in the group | Integer
449 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF | Associated transformer - for the State Estimator value | String
450 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
451 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.DNOMX | X coordinate of the object | Float |  |  |  | DNMOBJ
452 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.DNOMY | Y coordinate of the object | Float |  |  |  | DNMOBJ
453 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
454 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.ID | ID of the object | String |  |  |  | DNMOBJ
455 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
456 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
457 | DNOM Component | Analog Measurement Group | AMSGRP | input | SETRANSF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
458 | DNOM Component | Analog Measurement Group | AMSGRP |  | TELLOAD | A flag indicating telemetered loading | Boolean
459 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT | Pointer to the telemetered load | String
460 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
461 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
462 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
463 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.DRRATIO | Demand response component of the load (in percent) | Integer |  |  |  | LOAD
464 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
465 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.GENRATING | Nameplate kVA rating of the generation component of the load | Integer |  |  |  | LOAD
466 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.GENTYPE | User defined enumeration type for generation component | Integer |  |  |  | LOAD
467 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
468 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.ID | Object unique ID | String |  |  |  | DNMOBJ
469 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NAME | Object name | String |  |  |  | DNMOBJ
470 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
471 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
472 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
473 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NUMCUST | Customer count. | Integer |  |  |  | LOAD
474 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NUMDRCUSTOMER | The number of customers participating in demand response program | Integer |  |  |  | LOAD
475 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NUMGENCUSTOMER | The number of customers that have generation | Integer |  |  |  | LOAD
476 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NUMREGDT | The number of regular day types | Integer |  |  |  | LOAD
477 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.NUMSTBIN | The total number of historical data bins for study mode. | Integer |  |  |  | LOAD
478 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.PNOMA | Nominal phase A real power demand | Float |  | kW | kW | LOAD
479 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.PNOMB | Nominal phase B real power demand | Float |  | kW | kW | LOAD
480 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.PNOMC | Nominal phase C real power demand | Float |  | kW | kW | LOAD
481 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.PRIMCONN | Composite flag (mask) | Integer |  |  |  | LOAD
482 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.QNOMA | Nominal phase A reactive power demand | Float |  | kW | kW | LOAD
483 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.QNOMB | Nominal phase B reactive power demand | Float |  | kW | kW | LOAD
484 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.QNOMC | Nominal phase C reactive power demand | Float |  | kW | kW | LOAD
485 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.STDELTAC | The load delta iteration counter | Integer |  |  |  | LOAD
486 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.STDELTAP | The values of the schedule correction factors for power. | String |  |  |  | LOAD
487 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.SUPPLIER | Energy supplier | Integer |  |  |  | LOAD
488 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELLOADPNT.WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
489 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELTELLOADPNTPNT.BLAFLAGS | BLA flags | Integer |  |  |  | LOAD
490 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELTELLOADPNTPNT.CRITICALCUSTNUM | Number of critical customers | Integer |  |  |  | LOAD
491 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELTELLOADPNTPNT.STDELTAQ | The values of the schedule correction factors for reactive power. | String |  |  |  | LOAD
492 | DNOM Component | Analog Measurement Group | AMSGRP | input | TELTELLOADPNTPNT.TYPE | Type of the load | Integer |  |  |  | LOAD
493 | DNOM Component | Analog Measurement Group | AMSGRP |  | THRPHALL | Flag indicating that only three-phase measurements are present | Boolean
494 | DNOM Component | Area Name | AREANM |  | AFRCLOSEDLOOP | AFR Closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
495 | DNOM Component | Area Name | AREANM |  | AREAID | ID of the area | String
496 | DNOM Component | Area Name | AREANM |  | AREANAME | Name of the area | String
497 | DNOM Component | Area Name | AREANM |  | FISRCLOSEDLOOP | FISR closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
498 | DNOM Component | Area Name | AREANM |  | LVMCLOSEDLOOP | LVM closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
499 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED | Power factor schedule for the VVC application. This schedule is applied at the high side of the station power transformer. | String
500 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
501 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
502 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
503 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
504 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
505 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
506 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
507 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
508 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
509 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
510 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
511 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
512 | DNOM Component | Area Power Factor | AREAPF | input | PFSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
513 | DNOM Component | Automation Scheme | ATMSCHEME | input | COMMANDSTRING | List of teams in the scheme (used for navigation purposes) | String
514 | DNOM Component | Automation Scheme | ATMSCHEME | input | DESCRIPTION | Description of the automation scheme | String
515 | DNOM Component | Automation Scheme | ATMSCHEME | input | GETTEAMSDELIMITED | Comma-separated list of team IDs | String
516 | DNOM Component | Automation Scheme | ATMSCHEME | input | ID | ID of the automation scheme | String
517 | DNOM Component | Automation Scheme | ATMSCHEME | input | NAME | Name of the automation scheme | String
518 | DNOM Component | Automation Scheme | ATMSCHEME | input | NUMSTATIONS | Number of stations in the automation scheme | String
519 | DNOM Component | Automation Scheme | ATMSCHEME | input | NUMTEAMS | Number of teams in the automation scheme | String
520 | DNOM Component | Automation Scheme | ATMSCHEME | input | PRIMARYSTATIONNAME | The name of the primary station. | String
521 | DNOM Component | Automation Scheme | ATMSCHEME | input | SUBNAMESSTR | Names of stations in the automation scheme | String
522 | DNOM Component | Automation Scheme | ATMSCHEME | input | TEAMS | Pointer to teams in the automation scheme | String
523 | DNOM Component | Automation Scheme | ATMSCHEME | input | TEAMSTNNAMES | Names of stations associated with the automation scheme teams | String
524 | DNOM Component | Automation Scheme Team | ATMTEAM | input | DESCRIPTION | Description of the automation scheme team | String
525 | DNOM Component | Automation Scheme Team | ATMTEAM | input | ID | ID of the automation scheme team | String
526 | DNOM Component | Automation Scheme Team | ATMTEAM | input | NAME | Name of the automation scheme team | String
527 | DNOM Component | Automation Scheme Team | ATMTEAM | input | NUMSWITCHES | Number of switches in the automation scheme team | String
528 | DNOM Component | Automation Scheme Team | ATMTEAM | input | PRIMARYSTATIONNAME | The name of the primary station. | String
529 | DNOM Component | Automation Scheme Team | ATMTEAM | input | SUBNAMESSTR | Names of stations in the automation scheme team | String
530 | DNOM Component | Automation Scheme Team | ATMTEAM | input | SWTIDSDELIMITED | Comma-separated list of team switch IDs | String
531 | DNOM Component | Automation Scheme Team | ATMTEAM | input | TEAMSSWITCHES | Pointer to the switches in the automation scheme team | String
532 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | CONTROL_MEAS_ID | Control measurement ID | String
533 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | CONTROL_MEAS_TYPE | Control measurement type (for example, Control Prohibit Restoration) | String
534 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | CONTROL_STATUS | Control measurement status (Enabled/Disabled) | String
535 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | CONTROL_TIME | Time when the last control was sent | String
536 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | CONTROL_TYPE | The control method used for the device (Arm/Disarm) | String
537 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | ENERFEEDER | Name of the energizing feeder | String
538 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | ENERGYSTATIONNAME | Name of the energizing station | String
539 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | ID | ID of the switching device | String
540 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | NAME | Name of the switching device | String
541 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | NOMFEEDER | Name of the nominal feeder | String
542 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | ROLE | Switching device role (primary or secondary) | String
543 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | SCHEMEID | Name of the associated automation scheme | String
544 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | STATION1 | The first station that is associated with the switching device | String
545 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | STATION2 | The second station that is associated with the switching device (For boundary switches) | String
546 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | STATIONNAME | Name of the nominal station | String
547 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | SWITCH | Pointer to the switch | String
548 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | TEAMID | ID of the automation scheme team that the switch is associated with | String
549 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | output | SWTAUTORECLSTATUS | Auto Reclosing Enabled(ARE) Status | String
550 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | output | SWTGTESTATUS | Ground Trip Enabled(GTE) Status | String
551 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | output | SWTRESTSTATUS | Prohibit Restoration(REST) Status | String
552 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | output | COMHASTAG | Flag to indicate whether Tag Placed on Device | String
553 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | output | SWTSTATUS | The current device status | String
554 | DNOM Component | Automation Scheme Team Switch | ATMTEAMSWITCH | input | SWTSCADASTNNAME | Scada name of the substation that is associated with the device. | String
555 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | output | BLACHECKSTATUSSTR | BLA inconsistency check - human-readable explanation, which can be one of the following: - Consistent - Non-zero current flow measurement detected on a deenergized device - Zero current flow measurement detected on an energized device - Non-zero current flow measurement detected on an isolating switching device - Non-zero voltage measurement detected on a deenergized device - Zero voltage measurement detected on an energized device - Non-zero voltage measurement detected on an isolating switching device - Non-zero real power flow measurement detected on a deenergized device - Non-zero real power reverse flow measurement detected on a deenergized device - Zero real power flow measurement detected on an energized device - Zero real power reverse flow measurement detected on an energized device - Non-zero real power flow measurement detected on an isolating switching device - Non-zero real power reverse flow measurement detected on an isolating switching device - Non-zero reactive power flow measurement detected on a deenergized device - Non-zero reactive power reverse flow measurement detected on a deenergized device - Zero reactive power flow measurement detected on an energized device - Zero reactive power reverse flow measurement detected on an energized device - Non-zero reactive power flow measurement detected on an isolating switching device - Non-zero reactive power reverse flow measurement detected on an isolating switching device - Non-zero Volt-Amp flow measurement detected on a deenergized device - Zero Volt-Amp flow measurement detected on an energized device - Non-zero Volt-Amp flow measurement detected on an isolating switching device - Reactive power flow direction mismatch - Reactive power reverse flow direction mismatch - Real power flow direction mismatch - Real power reverse flow direction mismatch - Non-zero current flow measurement detected on an open switching device - Non-zero real power flow measurement detected on an open switching device - Non-zero real power reverse flow measurement detected on an open switching device - Non-zero reactive power flow measurement detected on an open switching device - Non-zero reactive power reverse flow measurement detected on an open switching device - Non-zero Volt-Amp flow measurement detected on an open switching device - Real power forward and reverse flow measurement inconsistent reading - Reactive power forward and reverse flow measurement inconsistent reading - Non-zero amps measurement detected on an energized device, while it is supposed to have zero flow - Non-zero real power measurement detected on an energized device, while it is supposed to have zero flow - Non-zero reactive power measurement detected on an energized device, while it is supposed to have zero flow - Non-zero apparent power measurement detected on an energized device, while it is supposed to have zero flow | String
556 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | output | BLASTATUSPHASE | Inconsistent switch phase. | String
557 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | output | BLASWTID | Inconsistent switch ID. | String
558 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | output | BLASWTNAME | Inconsistent switch name. | String
559 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | input | MEASILINDEX | Measurement Island Index. | String
560 | DNAF Object | BLA Consistency Check Switches | BLACONSISTSWT | input | MEASILNAME | Measurement Island name. | String
561 | Virtual Object | Branch | BRANCH | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
562 | Virtual Object | Branch | BRANCH | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
563 | Virtual Object | Branch | BRANCH |  | BOUNDARY | The boundary flag | Integer
564 | Virtual Object | Branch | BRANCH | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
565 | Virtual Object | Branch | BRANCH |  | TERMFR. | From end terminal | Enumeration
566 | Virtual Object | Branch | BRANCH |  | TERMTO. | To end terminal | Enumeration
567 | Virtual Object | Branch | BRANCH | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
568 | Virtual Object | Branch | BRANCH | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
569 | Virtual Object | Branch | BRANCH | input | ID | Object unique ID | String |  |  |  | DNMOBJ
570 | Virtual Object | Branch | BRANCH | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
571 | Virtual Object | Branch | BRANCH | input | NAME | Object name | String |  |  |  | DNMOBJ
572 | Virtual Object | Branch | BRANCH | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
573 | Virtual Object | Branch | BRANCH | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
574 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | ACTUALWA | Actual real power phase A | String |  | Watts | Watts
575 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | ACTUALWB | Actual real power phase B | String |  | Watts | Watts
576 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | ACTUALWC | Actual real power phase C | String |  | Watts | Watts
577 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
578 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPA | Current flow of Phase A, display actual value without angle. | Float
579 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPAANGLE | Phase A current angle of from node (Degree). | Float
580 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPANDANGLEA | Current flow of Phase A, display actual value with angle. | Float
581 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPANDANGLEB | Current flow of Phase B, display actual value with angle. | Float
582 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPANDANGLEC | Current flow of Phase C, display actual value with angle. | Float
583 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPANDANGLEN | Current flow of Phase N, display actual value with angle. | Float
584 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPANDANGLENEUT | Vector summation of Phase A,B,C current flows, display actual value with angle | Float
585 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPB | Current flow of Phase B, display actual value without angle | Float
586 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPBANGLE | Phase B current angle of from node (Degree). | Float
587 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPC | Current flow of Phase C, display actual value without angle. | Float
588 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPCANGLE | Phase C current angle of from node (Degree). | Float
589 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPG | Current flow of Phase N, display actual value without angle. | Float
590 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | AMPGANGLE | Phase N current angle of from node (Degree). | Float
591 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHKVAA | Apparent power flow of Phase A in kVA. | Float
592 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | BRANCHKVAABC | Three phase apparent power flow in kVA | Float |  | kVA | kVA
593 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHKVAB | Reactive power flow of Phase B in kVA. | Float
594 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHKVAC | Reactive power flow of Phase C in kVA. | Float
595 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPA | Real power flow of phase A in kW. | Float
596 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPB | Real power flow of phase B in kW. | Float
597 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPC | Real power flow of phase C in kW. | Float
598 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPFACTORFROMA | From node power factor of Phase A. | Float
599 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPFACTORFROMABC | From node power factor of Phase ABC. | Float
600 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPFACTORFROMB | From node power factor of Phase B. | Float
601 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHPFACTORFROMC | From node power factor of Phase C. | Float
602 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHQA | Reactive power flow of phase A in kVAR. | Float
603 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHQB | Reactive power flow of Phase B in kVAR. | Float
604 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | BRANCHQC | Reactive power flow of Phase C in kVAR. | Float
605 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | KVA3PH | Apparent power flow of phase ABC in kVA | Float |  | kVA | kVA
606 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | KVAA | Apparent power flow of phase A in kVA | Float |  | kVA | kVA
607 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | KVAB | Apparent power flow of phase B in kVA | Float |  | kVA | kVA
608 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | KVAC | Apparent power flow of phase C in kVA | Float |  | kVA | kVA
609 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KVAR3PH | Reactive power flow of phase ABC in kVAR. | Float
610 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KVARA | Reactive power flow of phase A in kVAR. | Float
611 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KVARB | Reactive power flow of phase B in kVAR. | Float
612 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KVARC | Reactive power flow of phase C in kVAR. | Float
613 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | KVLLA | Component phase A line to line voltage magnitude in KV. | Float
614 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | KVLLB | Component phase B line to line voltage magnitude t in KV. | Float
615 | Virtual Object | Branch and Shunt | BRNCHSHUNT | input | KVLLC | Component phase C line to line voltage magnitude in KV. | Float
616 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KW3PH | Real power flow of phase ABC in kW. | Float
617 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KWA | Real power flow of phase A in kW. | Float
618 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KWB | Real power flow of phase B in kW. | Float
619 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | KWC | Real power flow of phase C in kW. | Float
620 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEAMPAANGLE | Phase A current angle of to node (Degree). | Float
621 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEAMPBANGLE | Phase B current angle of to node (Degree). | Float
622 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEAMPCANGLE | Phase C current angle of to node (Degree). | Float
623 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTANAPG | Branch side 2 phase A voltage (magnitude on configurable voltage base and angle). | Float
624 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTANBPG | Branch side 2 phase B voltage (magnitude on configurable voltage base and angle). | Float
625 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTANCPG | Branch side 2 phase C voltage (magnitude on configurable voltage base and angle). | Float
626 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTANNPG | Branch side 2 phase N voltage (magnitude on configurable voltage base and angle). | Float
627 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTAPGACTLN | Branch side 2 phase A line to ground voltage (configurable voltage base with angle in degrees). | Float
628 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTBPGACTLN | Branch side 2 phase B line to ground voltage (configurable voltage base with angle in degrees). | Float
629 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTCPGACTLN | Branch side 2 phase C line to ground voltage (configurable voltage base with angle in degrees). | Float
630 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTOPAPG | Branch side 2 phase A voltage (magnitude on configurable voltage base and no angle). | Float
631 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTOPBPG | Branch side 2 phase B voltage (magnitude on configurable voltage base and no angle). | Float
632 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | TONODEVOLTOPCPG | Branch side 2 phase C voltage (magnitude on configurable voltage base and no angle). | Float
633 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTA | - | -
634 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTA2 | - | -
635 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTA2ACTLN | DPF calculated phase A of branch side 2 line to ground voltage magnitude (configurable voltage base). | Float
636 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTAACTLN | Phase A line to ground voltage magnitude (configurable voltage base). | Float
637 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANA | Phase A - voltage (configurable voltage base with angle in degrees). | Float
638 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANA2 | Phase A of branch side voltage (configurable voltage base with angle in degrees). | Float
639 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANAPG | Component phase A line to ground voltage magnitude in V. | Float
640 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANATO | Branch phase A side 2 voltage (configurable voltage base with angle in degrees). | Float
641 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANATOLG | Branch phase A side 2 LG voltage (configurable voltage base with angle in degrees). | Float
642 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANATOLL | Branch phase A side 2 LL voltage (configurable voltage base with angle in degrees). | Float
643 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANB | Phase B voltage (configurable voltage base with angle in degrees). | Float
644 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANB2 | Phase B of branch side 2 voltage (configurable voltage base with angle in degrees). | Float
645 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANBPG | Component phase B line to ground voltage magnitude in V. | Float
646 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANBTO | Branch phase B side 2 voltage (configurable voltage base with angle in degrees). | Float
647 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANBTOLG | Branch phase B side 2 LG voltage (configurable voltage base with angle in degrees). | Float
648 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANBTOLL | Branch phase B side 2 LL voltage (configurable voltage base with angle in degrees). | Float
649 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANC | Phase C voltage (configurable voltage base with angle in degrees). | Float
650 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANC2 | Phase C of branch side 2 voltage (configurable voltage base with angle in degrees). | Float
651 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANCPG | Component phase C line to ground voltage magnitude in V. | Float
652 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANCTO | Branch phase C side 2 voltage (configurable voltage base with angle in degrees). | Float
653 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANCTOLG | Branch phase C side 2 LG voltage (configurable voltage base with angle in degrees). | Float
654 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANCTOLL | Branch phase C side 2 LL voltage (configurable voltage base with angle in degrees). | Float
655 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEAACTLN | Phase A line to ground voltage (configurable voltage base with angle in degrees). | Float
656 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANA | Phase A voltage (magnitude on configurable voltage base and angle in degrees). | Float
657 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANALG | Phase A LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
658 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANALL | Phase A LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
659 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANB | Phase B voltage (magnitude on configurable voltage base and angle in degrees). | Float
660 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANBLG | Phase B LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
661 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANBLL | Phase B LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
662 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANC | Phase C voltage (magnitude on configurable voltage base and angle in degrees). | Float
663 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANCLG | Phase C LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
664 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANCLL | Phase C LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
665 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANN | Phase N voltage (magnitude on configurable voltage base and angle in degrees). | Float
666 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANNLG | Phase N LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
667 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEANNLL | Phase N LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
668 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEATOACTLN | Phase A of branch side 2 line to ground voltage (configurable voltage base with angle in degrees). | Float
669 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEBACTLN | Phase B line to ground voltage (configurable voltage base with angle in degrees). | Float
670 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEBTOACTLN | Phase B of branch side 2 line to ground voltage (configurable voltage base with angle in degrees). | Float
671 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLECACTLN | Phase C line to ground voltage (configurable voltage base with angle in degrees). | Float
672 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLECTOACTLN | Phase C of branch side 2 line to ground voltage (configurable voltage base with angle in degrees). | Float
673 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEOPA | Phase A voltage (magnitude on configurable voltage base and no angle). | Float
674 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEOPB | Phase B voltage (magnitude on configurable voltage base and no angle). | Float
675 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANDANGLEOPC | Phase C voltage (magnitude on configurable voltage base and no angle). | Float
676 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANNTO | Branch phase N side 2 voltage (configurable voltage base with angle in degrees). | Float
677 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANNTOLG | Branch phase N side 2 LG voltage (configurable voltage base with angle in degrees). | Float
678 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTANNTOLL | Branch phase N side 2 LL voltage (configurable voltage base with angle in degrees). | Float
679 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTB | - | -
680 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTB2 | - | -
681 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTB2ACTLN | DPF calculated phase B of branch side 2 line to ground voltage magnitude (configurable voltage base). | Float
682 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTBACTLN | DPF calculated phase B line to ground voltage magnitude (configurable voltage base in). | Float
683 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTC | - | -
684 | Virtual Object | Branch and Shunt | BRNCHSHUNT |  | VOLTC2 | - | -
685 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTC2ACTLN | DPF calculated phase C of branch side 2 line to ground voltage magnitude (configurable voltage base). | Float
686 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTCACTLN | DPF calculated phase C line to ground voltage magnitude (configurable voltage base). | Float
687 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPA | Phase A voltage magnitude (configurable voltage base). | Float
688 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPA2 | Phase A of branch side 2 voltage magnitude (configurable voltage base). | Float
689 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPAPG | Component phase A line to line voltage magnitude in V. | Float
690 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPATO | Branch phase A side 2 voltage (configurable voltage base and no angle). | Float
691 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPB | Phase B voltage magnitude (configurable voltage base). | Float
692 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPB2 | Phase B of branch side 2 voltage magnitude (configurable voltage base). | Float
693 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPBPG | Component phase B line to line voltage magnitude in V. | Float
694 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPBTO | Branch phase B side 2 voltage (configurable voltage base and no angle). | Float
695 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPC | Phase C voltage magnitude (configurable voltage base). | Float
696 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
697 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
698 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
699 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.CURROPEN | Current open status | Boolean |  |  |  | SWT
700 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
701 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
702 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
703 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
704 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
705 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
706 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.NAME | Name of the object | String |  |  |  | DNMOBJ
707 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
708 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
709 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.NOPEN | Normally Open | Boolean |  |  |  | SWT
710 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
711 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.REMOTE | Remote | Boolean |  |  |  | SWT
712 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
713 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
714 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPC2 | Phase C of branch side 2 voltage magnitude (configurable voltage base). | Float
715 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
716 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
717 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
718 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.CURROPEN | Current open status | Boolean |  |  |  | SWT
719 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
720 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
721 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
722 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
723 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
724 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
725 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.NAME | Name of the object | String |  |  |  | DNMOBJ
726 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
727 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
728 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.NOPEN | Normally Open | Boolean |  |  |  | SWT
729 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
730 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.REMOTE | Remote | Boolean |  |  |  | SWT
731 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
732 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH.SWMASK2 | Second switch attribute mask | Integer |  |  |  | SWT
733 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPCPG | Component phase C line to line voltage magnitude in V. | Float
734 | Virtual Object | Branch and Shunt | BRNCHSHUNT | output | VOLTOPCTO | Branch phase C side 2 voltage (configurable voltage base and no angle). | Float
735 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | ASSOCSGTEMPLATE | Pointer to the associated settings group template | String
736 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BASESW | Pointer to the base switch object | String
737 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
738 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
739 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
740 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.DIRECTIONA | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
741 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
742 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
743 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
744 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
745 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.ID | ID of the object | String |  |  |  | DNMOBJ
746 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.NAME | Object name | String |  |  |  | DNMOBJ
747 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
748 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
749 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | BPSWITCH | Pointer to the bypass switch | String
750 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | BRKRECSECTMASK | Bitmask for the normal upstream side ("From Node" or "To Node") of a recloser/breaker | Integer
751 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | CLOSELATAMP | Sufficient energy that sprints needed to close and latch the onto protector | Integer
752 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | COUNT | Number of counts before operation - sectionalizer | Integer |  | count | count
753 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | FAULTIND | Pointer to the associated fault indicator (may have measurements associated with it) | String
754 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | GRID | The grid is the “feeder” for the low voltage secondary network | String
755 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | GRIDCOLOR | A flag indicating that the secondary network of the network protector is looped | Boolean
756 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | LIMFLAGS | Number of limit violation flags | Integer
757 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | LOADSHEDDEFCLASS | Load shed default circuit classification | Integer
758 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
759 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.ISWTTYPE | Enumerated switch type 1 - OH Single Blade Switch 2 - UG Elbow Switch 3 - Fuse Switch 4 - Jumper 5 - Recloser 6 - Sectionalizer 7 - UG Multi Switch 8 - Automated Field Switch 9 - UG Feeder Switch 11 - Throwover - non Powell ESCO 12 - Throwover - Powell ESCO 13 - 3 Phase TX Switch | Integer |  |  |  | SWMOD
760 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | SWMOD
761 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | SWMOD
762 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | SWMOD
763 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.LIMVALUE | The value of the limit (in amps or kVA) | Float |  | Amps or kVA | Amps or kVA | SWMOD
764 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.NUMLIMIT | The number of operation limits | Integer |  |  |  | SWMOD
765 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA.SWCOST | Default cost of performing a switching operation | Float |  | $/operation | $/operation | SWMOD
766 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | LOADSHEDFDRCLASS | Load shed default circuit classification | Integer
767 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
768 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.ISWTTYPE | Enumerated switch type 1 - OH Single Blade Switch 2 - UG Elbow Switch 3 - Fuse Switch 4 - Jumper 5 - Recloser 6 - Sectionalizer 7 - UG Multi Switch 8 - Automated Field Switch 9 - UG Feeder Switch 11 - Throwover - non Powell ESCO 12 - Throwover - Powell ESCO 13 - 3 Phase TX Switch | Integer |  |  |  | SWMOD
769 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | SWMOD
770 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | SWMOD
771 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | SWMOD
772 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.LIMVALUE | The value of the limit (in amps or kVA) | Float |  | Amps or kVA | Amps or kVA | SWMOD
773 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.NUMLIMIT | The number of operation limits | Integer |  |  |  | SWMOD
774 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB.SWCOST | Default cost of performing a switching operation | Float |  | $/operation | $/operation | SWMOD
775 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | MASTERRCL | The minimum voltage by which the network transformer secondary voltage must exceed the network voltage to permit reclosing when restoration | Integer
776 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
777 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.ISWTTYPE | Enumerated switch type 1 - OH Single Blade Switch 2 - UG Elbow Switch 3 - Fuse Switch 4 - Jumper 5 - Recloser 6 - Sectionalizer 7 - UG Multi Switch 8 - Automated Field Switch 9 - UG Feeder Switch 11 - Throwover - non Powell ESCO 12 - Throwover - Powell ESCO 13 - 3 Phase TX Switch | Integer |  |  |  | SWMOD
778 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | SWMOD
779 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | SWMOD
780 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | SWMOD
781 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.LIMVALUE | The value of the limit (in amps or kVA) | Float |  | Amps or kVA | Amps or kVA | SWMOD
782 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.NUMLIMIT | The number of operation limits | Integer |  |  |  | SWMOD
783 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC.SWCOST | Default cost of performing a switching operation | Float |  | $/operation | $/operation | SWMOD
784 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | MASTERTRIP | Real power flow in the reverse direction to make reverse-power function operate | Integer
785 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | MAXINTRP | Maximum interrupting current rating (breakers and reclosers) | Float
786 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
787 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
788 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | DISTTF
789 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.CUSTMERA | The number of phase A only connected customers | Integer |  |  |  | DISTTF
790 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.CUSTMERB | The number of phase B only connected customers | Integer |  |  |  | DISTTF
791 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.CUSTMERC | The number of phase C only connected customers | Integer |  |  |  | DISTTF
792 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.CUSTOMER | The number of connected customers | Integer |  |  |  | DISTTF
793 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
794 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
795 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | DISTTF
796 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
797 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | DISTTF
798 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | DISTTF
799 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
800 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.NAME | Name of the object | String |  |  |  | DNMOBJ
801 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
802 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
803 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
804 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.PRIMGNDR | Primary grounding branch resistance | Float |  |  |  | DISTTF
805 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.PRIMGNDX | Primary grounding branch reactance | Float |  |  |  | DISTTF
806 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.PRIMOPERVOLT | Primary operating voltage (in kV l-g) | Integer |  |  |  | DISTTF
807 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.PRIMWIND | Primary winding connection type | Integer |  |  |  | DISTTF
808 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | DISTTF
809 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.SEC1GNDR | Secondary grounding branch resistance | Float |  |  |  | DISTTF
810 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.SEC1GNDX | Secondary grounding branch reactance | Float |  |  |  | DISTTF
811 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.SECWIND | Secondary winding connection type | Integer |  |  |  | DISTTF
812 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.TFLOADED | Connected load flag | Boolean |  |  |  | DISTTF
813 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | DISTTF
814 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.VOLTPR | Primary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
815 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF.VOLTSC | Secondary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
816 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELA | Pointer to the associated phase A switch model | String
817 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELB | Pointer to the associated phase B switch model | String
818 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | MODELC | Pointer to the associated phase C switch model | String
819 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | NPNOMOPMODE | Enumeration of the network protector operation mode (0 - NotSet, 1 - Automatic, 2 - Manual) | Enumeration
820 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT | input | NPTF | Pointer of the transformer connected to the network protector | String
821 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | NUMFLFAM | Number of analog fault current measurements for the device | Integer
822 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | NUMGROPS | Number of ground reclose operations - breakers and reclosers | Integer |  | count | count
823 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | NUMPHOPS | Number of phase reclose operations - breakers and reclosers | Integer |  | count | count
824 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | OPCOMMNT | Operator inserted comment | String
825 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | PHAANGRCL | The angle by which the distribution transformer secondary voltage must lead the network voltage to ensure that real power will flow from the transformer to the network when the network protector is closed | Integer
826 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | PHAANGTRIP | The minimum angle set for reverse power operation | Integer
827 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
828 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSHASOPTVHIGHMANENABLE | Flag indicating if user has enabled manual override for optimization high voltage limit | Boolean |  |  |  | BUS
829 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSHASOPTVLOWMANENABLE | Flag indicating if user has enabled manual override for optimization low voltage limit. | Boolean |  |  |  | BUS
830 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSHASVHIGHLMTMANENABLE | Flag indicating whether manual input of bus voltage high limit is used. | Boolean |  |  |  | BUS
831 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSHASVLOWLMTMANENABLE | Flag indicating whether manual input of bus voltage low limit is used. | Boolean |  |  |  | BUS
832 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSOPTVMANHIGH | Manual override value for optimization high voltage limit (values are in DCE selected units) | Float |  |  |  | BUS
833 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSOPTVMANLOW | Manual override value for optimization low voltage limit (values are in DCE selected units) | Float |  |  |  | BUS
834 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSVLMTMANHIGH | Manual input of bus voltage low limit. | Float |  |  |  | BUS
835 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.BUSVLMTMANLOW | Manual input of bus voltage low limit. | Float |  |  |  | BUS
836 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
837 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
838 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
839 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
840 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.ID | Unique and persistent ID of the looped feeder | String |  |  |  | DNMOBJ
841 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.NAME | Name of the looped feeder | String |  |  |  | DNMOBJ
842 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.RBUS | Bus source positive sequence resistance | Float |  |  |  | BUS
843 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VEMRHIGH | Emergency high voltage limit. | Float |  |  |  | BUS
844 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VEMRLOW | Emergency low voltage limit. | Float |  |  |  | BUS
845 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VNRMHIGH | Normal high voltage limit. | Float |  |  |  | BUS
846 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VNRMLOW | Normal low voltage limit. | Float |  |  |  | BUS
847 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOLTAGEBASE | Voltage base value | Float |  |  |  | BUS
848 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOLTUNIT | Flag indicating how the voltage limits are represented (true = configurable voltage base, false = per unit). | Boolean |  |  |  | BUS
849 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOPTEMRGHIGH | Emergency high voltage optimization limit. | Float |  |  |  | BUS
850 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOPTEMRGLOW | Emergency low voltage optimization limit. | Float |  |  |  | BUS
851 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOPTNORMHIGH | High voltage optimization limit. | Float |  |  |  | BUS
852 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.VOPTNORMLOW | Low voltage optimization limit. | Float |  |  |  | BUS
853 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS.XBUS | Bus source positive sequence reactance | Float |  |  |  | BUS
854 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | POSITIONTXT | Switch label position | String
855 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | RATING | A maximum rated device continuous for network protector | Integer
856 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | RCLNOMOPMODE | Enumeration of recloser nominal operating mode (0 - None, should not occur for reclosers, only for breakers and sectionalizers, 1 - Switch_Mode, 2 - Recloser_Mode, 3 - Sectionalizer_Mode | Enumeration |  | enumeration | enumeration
857 | Virtual Object | Breakers, Reclosers, and Sectionalizers | BRSSWT |  | RECENAB | Flag indicating that the reclosing feature of a recloser/breaker is enabled or disabled (true = enabled) | Boolean
858 | DNOM Component Placement | Bus Label Placement | BSLBPL | input | BUS | Pointer to the associated bus | String
859 | DNOM Component | Bus | BUS |  | _KEY | The unique identifier to represent a device | String
860 | DNOM Component | Bus | BUS | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
861 | DNOM Component | Bus | BUS | input | BRANCHENERGIZED | Phases that are currently energized. | String
862 | DNOM Component | Bus | BUS | input | BRANCHDEENERGIZED | Phases that are currently de-energized. | String
863 | DNOM Component | Bus | Bus | input | BUSFEEDERMAIN | Flag indicate if the bus is on feeder main. | Boolean
864 | DNOM Component | Bus | BUS | input | BUSHASOPTVHIGHMANENABLE | Flag indicating if user has enabled manual override for optimization high voltage limit | Boolean
865 | DNOM Component | Bus | BUS | input | BUSHASOPTVLOWMANENABLE | Flag indicating if user has enabled manual override for optimization low voltage limit. | Boolean
866 | DNOM Component | Bus | BUS | input | BUSHASVHIGHLMTMANENABLE | Flag indicating whether manual input of bus voltage high limit is used. | Boolean
867 | DNOM Component | Bus | BUS | input | BUSHASVLOWLMTMANENABLE | Flag indicating whether manual input of bus voltage low limit is used. | Boolean
868 | DNOM Component | Bus | BUS | input | BUSHASVOPTHIGHLMTMANENABLE | Flag indicating if user has enabled manual override for high voltage limit | Boolean
869 | DNOM Component | Bus | BUS | input | BUSHASVOPTLOWLMTMANENABLE | Flag indicating if user has enabled manual override for low voltage limit | Boolean
870 | DNOM Component | Bus | BUS | input | BUSMANVOLTMEASVALUE | SCADA Manual Voltage Measurement Data for Bus. | Float
871 | DNOM Component | Bus | BUS | input | BUSOPTVMANHIGH | Manual override value for optimization high voltage limit (values are in DCE selected units) | Float
872 | DNOM Component | Bus | BUS | input | BUSOPTVMANHIGHALLBASE | Manual override value for optimization high voltage limit (values are in DCE selected units) | Float
873 | DNOM Component | Bus | BUS | input | BUSOPTVMANLOW | Manual override value for optimization low voltage limit (values are in DCE selected units) | Float
874 | DNOM Component | Bus | BUS | input | BUSOPTVMANLOWALLBASE | Manual override value for optimization low voltage limit (values are in DCE selected units) | Float
875 | DNOM Component | Bus | BUS | input | BUSVLMTMANHIGH | Manual input of bus voltage low limit. | Float
876 | DNOM Component | Bus | BUS | input | BUSVLMTMANHIGHALLBASE | Manual override value for high voltage limit (values are in DCE selected units). | Float
877 | DNOM Component | Bus | BUS | input | BUSVLMTMANLOW | Manual input of bus voltage low limit. | Float
878 | DNOM Component | Bus | BUS | input | BUSVLMTMANLOWALLBASE | Manual override value for low voltage limit (values are in DCE selected units). | Float
879 | DNOM Component | Bus | BUS | input | BUSVMANALLBASE | Voltage-base that was set in DNAF Configuration Editor | Float
880 | DNOM Component | Bus | BUS | input | COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
881 | DNOM Component | Bus | BUS | input | CONSTRUCTPHASES | Individual phases that are constructed but are not energized. | String
882 | DNOM Component | Bus | BUS | input | DNOMRECORDNAME | The DNOM record name of the bus | String |  |  |  | DNMOBJ
883 | DNOM Component | Bus | BUS | input | DNOMTABNAME | The DNOM table name of the bus. | String
884 | DNOM Component | Bus | BUS | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
885 | DNOM Component | Bus | BUS | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
886 | DNOM Component | Bus | BUS | input | DYNFEEDERNAME | Dynamic feeder name. | String
887 | DNOM Component | Bus | BUS | input | DYNSTATIONNAME | Dynamic station name. | String
888 | DNOM Component | Bus | BUS | input | FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
889 | DNOM Component | Bus | BUS | input | FUTUREPHASES | Future phases. | String
890 | DNOM Component | Bus | BUS | input | HASMANUALENTRY | If one or some fields of bus has(have) value override. | Boolean
891 | DNOM Component | Bus | BUS | output | HIGHVOLTLIM | Enforced voltage high limit in LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
892 | DNOM Component | Bus | BUS | input | HIGHVOLTLIMSOURCE | The source of high voltage limit. | String
893 | DNOM Component | Bus | BUS | input | ID | Object unique ID | String |  |  |  | DNMOBJ
894 | DNOM Component | Bus | BUS | input | ISENERGIZED | Specifies whether any phase of the bus is energized. | Boolean
895 | DNOM Component | Bus | BUS | input | LIMITCOMPTYPE | Component type, returns "Bus" | String
896 | DNOM Component | Bus | BUS | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
897 | DNOM Component | Bus | BUS | output | LOWVOLTLIM | Enforced voltage low limit in LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
898 | DNOM Component | Bus | BUS | input | LOWVOLTLIMSOURCE | The source of low voltage limit. | String
899 | DNOM Component | Bus | BUS | input | MANUALHIGHVOLTLIM | Manual override value for high voltage limit. | Float
900 | DNOM Component | Bus | BUS | input | MANUALLOWVOLTLIM | Manual override value for low voltage limit. | Float
901 | DNOM Component | Bus | BUS | input | NAME | Object name | String |  |  |  | DNMOBJ
902 | DNOM Component | Bus | BUS | input | NODE | Pointer to the associated node | String |  |  |  | COMELC
903 | DNOM Component | Bus | BUS | input | NODENUM | Node name | String
904 | DNOM Component | Bus | BUS | input | ORIGHIGHVOLTLIM | High voltage limit. | Float
905 | DNOM Component | Bus | BUS | input | ORIGLOWVOLTLIM | Low voltage limit. | Float
906 | DNOM Component | Bus | BUS | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
907 | DNOM Component | Bus | BUS | input | RBUS | Bus source positive sequence resistance | Float
908 | DNOM Component | Bus | BUS | input | REFVOLT120BASE | Voltage in equivalent 120V value | Float |  | Volts | Volts
909 | DNOM Component | Bus | BUS | input | SERVCNTRNAME | Service center name | String
910 | DNOM Component | Bus | BUS | input | USRVLTLV.COLORVLT | Associated color used for display purposes | String |  |  |  | UVLTLV
911 | DNOM Component | Bus | BUS | input | USRVLTLV.DISTVLTL | Flag indicating that the voltage level represents a distribution voltage level (true - distribution, false - transmission) | String |  |  |  | UVLTLV
912 | DNOM Component | Bus | BUS | input | USRVLTLV.ID | ID of the user voltage level | String |  |  |  | DNMOBJ
913 | DNOM Component | Bus | BUS | input | USRVLTLV.KVLLVVAL | Voltage level (line to line) | String |  | kV | kV | UVLTLV
914 | DNOM Component | Bus | BUS |  | STATIONNAME | Name of the station the bus belongs to | String
915 | DNOM Component | Bus | BUS | input | SUBGIVENCOMMONELECT | Substation the component belongs to | String |  |  |  | COMELC
916 | DNOM Component | Bus | BUS | input | SWTCURPOSSTATUSMEASID | ID of the switch status measurement point | String
917 | DNOM Component | Bus | BUS | input | TOPOSUBNAME | Nominal substation name. | String
918 | DNOM Component | Bus | BUS | input | USRVLTLV | Pointer to the user voltage level | String |  | kV | kV
919 | DNOM Component | Bus | BUS | output | VAPOSTPLAN | Phase A bus voltage magnitude after LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
920 | DNOM Component | Bus | BUS | output | VAPREPLAN | Phase A bus voltage magnitude before LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
921 | DNOM Component | Bus | BUS | output | VBPOSTPLAN | Phase B bus voltage magnitude after LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
922 | DNOM Component | Bus | BUS | output | VBPREPLAN | Phase B bus voltage magnitude before LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
923 | DNOM Component | Bus | BUS | output | VCPOSTPLAN | Phase C bus voltage magnitude after LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
924 | DNOM Component | Bus | BUS | output | VCPREPLAN | Phase C bus voltage magnitude before LVM plan (in configurable voltage base). | Float | LVM | Volt | Volt
925 | DNOM Component | Bus | BUS | input | VEMRHIGH | Emergency high voltage limit. | Float
926 | DNOM Component | Bus | BUS | input | VEMRLOW | Emergency low voltage limit. | Float
927 | DNOM Component | Bus | BUS | output | VMISMATCHPHA | The value of a difference between the measured and calculated voltages in phase A | Float
928 | DNOM Component | Bus | BUS | output | VMISMATCHPHAEXCD
929 | DNOM Component | Bus | BUS | output | VMISMATCHPHB | The value of a difference between the measured and calculated voltages in phase B | Float
930 | DNOM Component | Bus | BUS | output | VMISMATCHPHBEXCD
931 | DNOM Component | Bus | BUS | output | VMISMATCHPHC | The value of a difference between the measured and calculated voltages in phase C | Float
932 | DNOM Component | Bus | BUS | output | VMISMATCHPHCEXCD
933 | DNOM Component | Bus | BUS | input | VNRMHIGH | Normal high voltage limit. | Float
934 | DNOM Component | Bus | BUS | input | VNRMLOW | Normal low voltage limit. | Float
935 | DNOM Component | Bus | BUS | input | VOLTAGEBASE | Voltage Base value | Float
936 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANALG | Phase A LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
937 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANALL | Phase A LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
938 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANBLG | Phase B LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
939 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANBLL | Phase B LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
940 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANCLG | Phase C LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
941 | DNOM Component | Bus | BUS | input | VOLTANDANGLEANCLL | Phase C LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
942 | DNOM Component | Bus | BUS | input | VOLTLEVEL | Nominal Voltage level voltage in kV (line to neutral voltage for single phase component and line to line voltage for three phase component) | String
943 | DNOM Component | Bus | BUS | input | VOLTUNIT | Flag indicating how the voltage limits are represented (true = configurable voltage base, false = per unit). | Boolean
944 | DNOM Component | Bus | BUS | input | VOPTEMRGHIGH | Emergency high voltage optimization limit. | Float
945 | DNOM Component | Bus | BUS | input | VOPTEMRGLOW | Emergency low voltage optimization limit. | Float
946 | DNOM Component | Bus | BUS | input | VOPTNORMHIGH | High voltage optimization limit. | Float
947 | DNOM Component | Bus | BUS | input | VOPTNORMLOW | Low voltage optimization limit. | Float
948 | DNOM Component | Bus | BUS | input | XBUS | Bus source positive sequence reactance | Float
949 | DNOM Component | Bus | BUS | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
950 | DNOM Component | Bus | BUS | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
951 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
952 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | input | VMEASPHA | Voltage magnitude measurement values of phase A | Float
953 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | input | VMEASPHB | Voltage magnitude measurement values of phase B | Float
954 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
955 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSHASOPTVHIGHMANENABLE | Flag indicating if user has enabled manual override for optimization high voltage limit | Boolean |  |  |  | BUS
956 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSHASOPTVLOWMANENABLE | Flag indicating if user has enabled manual override for optimization low voltage limit. | Boolean |  |  |  | BUS
957 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSHASVHIGHLMTMANENABLE | Flag indicating whether manual input of bus voltage high limit is used. | Boolean |  |  |  | BUS
958 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSHASVLOWLMTMANENABLE | Flag indicating whether manual input of bus voltage low limit is used. | Boolean |  |  |  | BUS
959 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSOPTVMANHIGH | Manual override value for optimization high voltage limit (values are in DCE selected units) | Float |  |  |  | BUS
960 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSOPTVMANLOW | Manual override value for optimization low voltage limit (values are in DCE selected units) | Float |  |  |  | BUS
961 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSVLMTMANHIGH | Manual input of bus voltage low limit. | Float |  |  |  | BUS
962 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.BUSVLMTMANLOW | Manual input of bus voltage low limit. | Float |  |  |  | BUS
963 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
964 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
965 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
966 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
967 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.ID | Unique and persistent ID of the looped feeder | String |  |  |  | DNMOBJ
968 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.NAME | Name of the looped feeder | String |  |  |  | DNMOBJ
969 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.RBUS | Bus source positive sequence resistance | Float |  |  |  | BUS
970 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VEMRHIGH | Emergency high voltage limit. | Float |  |  |  | BUS
971 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VEMRLOW | Emergency low voltage limit. | Float |  |  |  | BUS
972 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VNRMHIGH | Normal high voltage limit. | Float |  |  |  | BUS
973 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VNRMLOW | Normal low voltage limit. | Float |  |  |  | BUS
974 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOLTAGEBASE | Voltage base value | Float |  |  |  | BUS
975 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOLTUNIT | Flag indicating how the voltage limits are represented (true = configurable voltage base, false = per unit). | Boolean |  |  |  | BUS
976 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOPTEMRGHIGH | Emergency high voltage optimization limit. | Float |  |  |  | BUS
977 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOPTEMRGLOW | Emergency low voltage optimization limit. | Float |  |  |  | BUS
978 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOPTNORMHIGH | High voltage optimization limit. | Float |  |  |  | BUS
979 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.VOPTNORMLOW | Low voltage optimization limit. | Float |  |  |  | BUS
980 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS.XBUS | Bus source positive sequence reactance | Float |  |  |  | BUS
981 | DNOM Component | Switch Cabinet | CABNET | input | ADDRESS.NOAPPSTRING | Address. | String
982 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | input | VMEASPHC | Voltage magnitude measurement values of phase C | Float
983 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | output | VOLTANDANGLEBUSREGOPA | Voltage magnitude of phase A at the bus or low side of the transformer in configurable voltage base. | Float
984 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | output | VOLTANDANGLEBUSREGOPB | Voltage magnitude of phase B at the bus or low side of the transformer in configurable voltage base. | Float
985 | Virtual Object | Bus and Regulator | BUSANDREGULATOR | output | VOLTANDANGLEBUSREGOPC | Voltage magnitude of phase C at the bus or low side of the transformer in configurable voltage base. | Float
986 | DNOM Component Placement | Bus Placement | BUSPLE | input | BUS | Pointer to the associated bus | String
987 | DNOM Component | Switch Cabinet | CABNET | input | ALTERNATENAME | Alias name for switch cabinet | String
988 | DNOM Component | Switch Cabinet | CABNET | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
989 | DNOM Component | Switch Cabinet | CABNET | input | AREAIND | Integer index into station permission area list | Integer |  |  |  | DNMOBJ
990 | DNOM Component | Switch Cabinet | CABNET | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
991 | DNOM Component | Switch Cabinet | CABNET | input | CABFEEDMAIN | Whether the cabinet is connected to the feeder main. Return "YES" or "NO". | String
992 | DNOM Component | Switch Cabinet | CABNET | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
993 | DNOM Component | Switch Cabinet | CABNET | input | DNOMTABNAME | The DNOM table name. | String
994 | DNOM Component | Switch Cabinet | CABNET | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
995 | DNOM Component | Switch Cabinet | CABNET | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
996 | DNOM Component | Switch Cabinet | CABNET | input | EXTRNOBJ | Dynamic array of external device IDs. | String
997 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
998 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
999 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
1000 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
1001 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
1002 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
1003 | DNOM Component | Switch Cabinet | CABNET | input | FEEDMAIN | Flag indicating whether the cabinet is connected to the feeder main. | Boolean
1004 | DNOM Component | Switch Cabinet | CABNET | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1005 | DNOM Component | Switch Cabinet | CABNET | input | ISTELEMETEREDCABINET | Specifies whether the cabinet is telemetered (based on whether the switches inside the cabinet are telemetered) | Boolean
1006 | DNOM Component | Switch Cabinet | CABNET | input | ISWCTYPE | Cabinet type. | Integer
1007 | DNOM Component | Switch Cabinet | CABNET | input | JUNCCONT | Pointer to the junction container | String
1008 | DNOM Component | Switch Cabinet | CABNET | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
1009 | DNOM Component | Switch Cabinet | CABNET | input | NAME | Object name | String |  |  |  | DNMOBJ
1010 | DNOM Component | Switch Cabinet | CABNET | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
1011 | DNOM Component | Switch Cabinet | CABNET | input | NMEXTOBJ | The number of objects owned in external station. | Integer
1012 | DNOM Component | Switch Cabinet | CABNET | input | NMOWNOBJ | The number of objects contained in the switch cabinet. | Integer
1013 | DNOM Component | Switch Cabinet | CABNET | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1014 | DNOM Component | Switch Cabinet | CABNET | input | NUM1PHRECONFIGSW | The number of 1-phase reconfigurable switches contained in the cabinet. | String
1015 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ.AREAIND | Dynamic array of permission area indices of collected objects | String |  |  |  | DNMOBJ
1016 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ.DNOMX | Dynamic array of X coordinations of collected objects | String |  |  |  | DNMOBJ
1017 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ.DNOMY | Dynamic array of Y coordinations of collected objects | String |  |  |  | DNMOBJ
1018 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ.ID | Dynamic array of IDs of collected objects | String |  |  |  | DNMOBJ
1019 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ.NAME | Dynamic array of names of collected objects | String |  |  |  | DNMOBJ
1020 | DNOM Component | Switch Cabinet | CABNET | input | NUM1PHSWITCHES | The number of 1-phase switches contained in the cabinet. | String
1021 | DNOM Component | Switch Cabinet | CABNET | input | NUM3PHRECONFIGSW | The number of reconfigurable 3-phase switches contained in the cabinet. | String
1022 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.AX | Dynamic array of X coordinates | String |  |  |  | CMBPLS
1023 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.AY | Dynamic array of Y coordinates | String |  |  |  | CMBPLS
1024 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
1025 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
1026 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
1027 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
1028 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1029 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1030 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1031 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1032 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1033 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1034 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1035 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1036 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.NUMVERT | Number of vertices (line or polygon) | String |  |  |  | CMBPLS
1037 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.ROTATION | Rotation anagle of the placement | String |  | degrees | degrees | CMBPLS
1038 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.SIZE | Size of the object | String |  |  |  | CMBPLS
1039 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.X | X coordinate of the placement | String |  |  |  | CMBPLS
1040 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT.Y | Y coordinate of the placement | String |  |  |  | CMBPLS
1041 | DNOM Component | Switch Cabinet | CABNET | input | NUM3PHSWITCHES | The number of 3-phase switches contained in the cabinet. | String
1042 | DNOM Component | Switch Cabinet | CABNET | input | NUMOBJ | The number of objects contained in the switch cabinet. | Integer
1043 | DNOM Component | Switch Cabinet | CABNET | input | OWNEDOBJ | Pointer to the dynamic array of objects collected in the switch cabinet (New collections) | String
1044 | DNOM Component | Switch Cabinet | CABNET | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
1045 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ.AREAIND | Dynamic array of permission area indices of collected objects | String |  |  |  | DNMOBJ
1046 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ.DNOMX | Dynamic array of X coordinations of collected objects | String |  |  |  | DNMOBJ
1047 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ.DNOMY | Dynamic array of Y coordinations of collected objects | String |  |  |  | DNMOBJ
1048 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ.ID | Dynamic array of IDs of collected objects | String |  |  |  | DNMOBJ
1049 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ.NAME | Dynamic array of names of collected objects | String |  |  |  | DNMOBJ
1050 | DNOM Component | Switch Cabinet | CABNET | input | PLACEMNT | Pointer to the cabinet placement | String
1051 | DNOM Component | Switch Cabinet | CABNET | input | RECONFIG | Flag indicating whether the cabinet is reconfigurable. | Boolean
1052 | DNOM Component | Switch Cabinet | CABNET | input | SWCABINETEMSNAME | EMS name of the station associated with the switch cabinet | String
1053 | DNOM Component | Switch Cabinet | CABNET | input | SWCABINETSTATNAME | Name of the station associated with the switch cabinet | String
1054 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
1055 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1056 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
1057 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1058 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1059 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
1060 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.EXTRNOBJ | Dynamic array of external device IDs | String |  |  |  | CABNET
1061 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.FEEDMAIN | Flag indicating whether the cabinet is connected to the feeder main. | Boolean |  |  |  | CABNET
1062 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.ID | ID of the object | String |  |  |  | DNMOBJ
1063 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.ISWCTYPE | Cabinet type | Integer |  |  |  | CABNET
1064 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.NAME | Object name | String |  |  |  | DNMOBJ
1065 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.NMOWNOBJ | The number of objects contained in the switch cabinet. | Integer |  |  |  | CABNET
1066 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1067 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.NUM3PHRECONFIGSW | The Number of reconfigurable 3-phase switches contained in the cabinet. | String |  |  |  | CABNET
1068 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.NUMOBJ | The Number of objects contained in the switch cabinet.. | Integer |  |  |  | CABNET
1069 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET.RECONFIG | Flag indicating whether the cabinet is reconfigurable. | Boolean |  |  |  | CABNET
1070 | DNOM Component | Switch Cabinet | CABNET | input | SWCABOBJ | Pointer to the dynamic array of objects collected in the switch cabinet (Old collections) | String
1071 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
1072 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1073 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
1074 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1075 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1076 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
1077 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.EXTRNOBJ | Dynamic array of external device IDs | String |  |  |  | CABNET
1078 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.FEEDMAIN | Flag indicating whether the cabinet is connected to the feeder main. | Boolean |  |  |  | CABNET
1079 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.ID | ID of the object | String |  |  |  | DNMOBJ
1080 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.ISWCTYPE | Cabinet type | Integer |  |  |  | CABNET
1081 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.NAME | Object name | String |  |  |  | DNMOBJ
1082 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.NMOWNOBJ | The number of objects contained in the switch cabinet. | Integer |  |  |  | CABNET
1083 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1084 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.NUM3PHRECONFIGSW | The Number of reconfigurable 3-phase switches contained in the cabinet. | String |  |  |  | CABNET
1085 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.NUMOBJ | The Number of objects contained in the switch cabinet.. | Integer |  |  |  | CABNET
1086 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET.RECONFIG | Flag indicating whether the cabinet is reconfigurable. | Boolean |  |  |  | CABNET
1087 | DNOM Component | Switch Cabinet | CABNET | input | SWCABTYPE | Switch cabinet type: 0 = Unknown 1 = CI Vac Intr 2 = Encap Vac Sw 3 = GRAL 4 = Loop Sectionalizing 5 = PME-10 6 = PME-11 7 = PME-4 8 = PME-9 9 = PMH-11 10 = PMH-6 11 = PMH-9 12 = RA-21 13 = RA-32 14 = RAL 15 = RAM 16 = SRA-21 17 = SRAM33 18 = SRAM44 19 = Vac Fault Intr 20 = Powell ESCO Throwover 21 = PMH-5 22 = PMH-7 23 = PMH-8 24 = PMH-10 25 = PMH-12 26 = PME-6 27 = PME-12 | Integer
1088 | DNOM Component | Switch Cabinet | CABNET | input | CABINETSWITCHES | The list of device names that the switch cabinet contains | String
1089 | DNOM Component | Switch Cabinet | CABNET | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
1090 | DNOM Component | Switch Cabinet | CABNET | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
1091 | DNOM Component Placement | Switch Cabinet Label Placement | CBLBPL | input | CABINET | Pointer to the associated switch cabinet | String
1092 | DNOM Component Placement | Switch Cabinet Placement | CBPLE | input | CABINET | Pointer to the associated switch cabinet | String
1093 | DNOM Component Placement | Combination Placement | CMBPLS | input | AX | Dynamic array of X coordinates | Float
1094 | DNOM Component Placement | Combination Placement | CMBPLS | input | AX | Dynamic array of X coordinates | Float
1095 | DNOM Component Placement | Combination Placement | CMBPLS | input | AX2 | Dynamic array of secondary X coordinates. Secondary X coordinate property type is "double" compared to a common X coordinate, which is "float". It has more precision. This is added for an external interface which needs more accurate coordinates. In uture, it can be used to store secondary geometry. | Double
1096 | DNOM Component Placement | Combination Placement | CMBPLS | input | AY | Dynamic array of Y coordinates | Float
1097 | DNOM Component Placement | Combination Placement | CMBPLS | input | AY | Dynamic array of Y coordinates | Float
1098 | DNOM Component Placement | Combination Placement | CMBPLS | input | AY2 | Dynamic array of secondary Y coordinates. Secondary Y coordinate property type is "double" compared to a common X coordinate, which is "float". It has more precision. This is added for an external interface which needs more accurate coordinates. In uture, it can be used to store secondary geometry. | Double
1099 | DNOM Component Placement | Combination Placement | CMBPLS | input | NUMVERT | Number of vertices (line or polygon) | Integer
1100 | DNOM Component Placement | Combination Placement | CMBPLS | input | ROTATION | Rotation angle of the placement | Integer
1101 | DNOM Component Placement | Combination Placement | CMBPLS | input | SIZE | Size of the point object | Integer
1102 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
1103 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
1104 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
1105 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
1106 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
1107 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
1108 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
1109 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
1110 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
1111 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
1112 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
1113 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
1114 | Global Object | Conductor Model | CNDMOD | input | AMPSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
1115 | DNOM Component Placement | Combination Placement | CMBPLS | input | X | X coordinate of the placement | Float
1116 | DNOM Component Placement | Combination Placement | CMBPLS | input | X2 | X coordinate as double data type coming from GIS. Has more precision compared to common X. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
1117 | DNOM Component Placement | Combination Placement | CMBPLS | input | Y | Y coordinate of the placement | Float
1118 | DNOM Component Placement | Combination Placement | CMBPLS | input | Y2 | Y coordinate as double data type coming from GIS. Has more precision compared to common Y. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
1119 | Global Object | Conductor Model | CNDMOD |  | AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String
1120 | Global Object | Conductor Model | CNDMOD |  | BSHUNT | Shunt susceptance (Siemens x 10-06/kft) if a transmission model is given (blank for a distribution model). | Float
1121 | Global Object | Conductor Model | CNDMOD |  | CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction). | Integer
1122 | Global Object | Conductor Model | CNDMOD |  | CONDSIZE | Conductor size (568, 1.0, other). | String
1123 | Global Object | Conductor Model | CNDMOD |  | CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer
1124 | Global Object | Conductor Model | CNDMOD |  | DIAMETER | Diameter of the conductor (inches/millimeters) if a distribution model is given (blank for a transmission model). | Float
1125 | Global Object | Conductor Model | CNDMOD |  | DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission). | Boolean
1126 | Global Object | Conductor Model | CNDMOD |  | GMRNEUT | Neutral conductor bundle self geometric mean radius (feet/millimeters) for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float
1127 | Global Object | Conductor Model | CNDMOD |  | GMRPHASE | Phase conductor geometric mean radius (feet/millimeters) if a distribution model is given (blank for a transmission model). | Float
1128 | Global Object | Conductor Model | CNDMOD |  | GSHUNT | Shunt conductance (Siemens x 10-06/kft) if a transmission model is given (blank for a distribution model). | Float
1129 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.AENDDT | Season end date | String |  |  |  | SEASON
1130 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1131 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.ASTARTDT | Season start date | String |  |  |  | SEASON
1132 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.DESCRIPT | Season description | String |  |  |  | SEASON
1133 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.ID | Season unique ID | String |  |  |  | DNMOBJ
1134 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
1135 | Global Object | Conductor Model | CNDMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1136 | Global Object | Conductor Model | CNDMOD |  | INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer
1137 | Global Object | Conductor Model | CNDMOD |  | LIMITEVENT | A flag indicating a limit event | Boolean
1138 | Global Object | Conductor Model | CNDMOD |  | LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term). | String
1139 | Global Object | Conductor Model | CNDMOD | input | LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String
1140 | Global Object | Conductor Model | CNDMOD |  | LIMUNIT | Enumerated limit units, 1 = amps, 2 = kVA. | Integer
1141 | Global Object | Conductor Model | CNDMOD |  | LIMVALUE | The value of the limit (in amps or kVA). | Float
1142 | Global Object | Conductor Model | CNDMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
1143 | Global Object | Conductor Model | CNDMOD |  | NEUTDIST | Center to neutral conductor spacing (inches/millimeters) for a concentric neutral cable (blank for a transmission model). | Float
1144 | Global Object | Conductor Model | CNDMOD |  | NUMLIMIT | The number of operational limits. | Integer
1145 | Global Object | Conductor Model | CNDMOD |  | OUTDIAM | Outside diameter over the shield (inches/millimeters) for a non-concentric neutral cable if a distribution model is given (blank for a transmission model). | Float
1146 | Global Object | Conductor Model | CNDMOD |  | PHDIST | Phase conductor spacing (inches/millimeters) for a three conductor cable if a distribution model is given (blank for a transmission model). | Float
1147 | Global Object | Conductor Model | CNDMOD |  | PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year). | Float
1148 | Global Object | Conductor Model | CNDMOD |  | REPTIME | Default mean time to repair (in hours). | Float
1149 | Global Object | Conductor Model | CNDMOD |  | RNEUTRAL | Neutral conductor resistance (ohms/kft) or (ohms/km) at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float
1150 | Global Object | Conductor Model | CNDMOD |  | RPHASE | Phase conductor resistance (ohms/kft) or (ohms/km) at 60 Hz for a transmission or distribution model. | Float
1151 | Global Object | Conductor Model | CNDMOD |  | SHDTHICK | Shield thickness (in inches/millimeters) for a non-concentric neutral cable if a distribution model is given (blank for a transmission model). | Float
1152 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
1153 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
1154 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
1155 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
1156 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
1157 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
1158 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
1159 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
1160 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
1161 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
1162 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
1163 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
1164 | Global Object | Conductor Model | CNDMOD | input | TEMPSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
1165 | Global Object | Conductor Model | CNDMOD |  | SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor). | Boolean
1166 | Global Object | Conductor Model | CNDMOD |  | STRCTYPE | Conductor type (copper, other). | String
1167 | Global Object | Conductor Model | CNDMOD |  | STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Integer
1168 | Global Object | Conductor Model | CNDMOD |  | STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float
1169 | Global Object | Conductor Model | CNDMOD |  | TEMPSCHED | The name of an associated temperature based ampacity schedule. | String
1170 | Global Object | Conductor Model | CNDMOD |  | TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year). | Float
1171 | Global Object | Conductor Model | CNDMOD |  | XPHASE | Phase conductor reactance (ohms/kft) or (ohms/km) if a transmission model is given (blank for a distribution model). | Float
1172 | DNOM Group Object | Common Electrical | COMELC | input | COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer
1173 | DNOM Group Object | Common Electrical | COMELC | input | FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer
1174 | DNOM Group Object | Common Electrical | COMELC | input | NODE | Pointer to the associated node | String
1175 | DNOM Group Object | Common Electrical | COMELC | input | SUBGIVENCOMMONELECT | Substation the component belongs to | String
1176 | Virtual Object | DMS Component | COMP | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
1177 | DNOM Component | Composite Switch | COMPSW | input | ADDRESS.NOAPPSTR | Address of the composite switch | String |  |  |  | NDPFST
1178 | DNOM Component | Composite Switch | COMPSW | input | ADDRESS.NOAPPSTRING | Address. | String
1179 | Virtual Object | DMS Component | COMP | input | STRUCTUREID | ID of a structure (for example, pole) that is associated with the DNOM object | String
1180 | Virtual Object | DMS Component | COMP |  | USRVLTLV | Pointer to the user voltage level | Float |  | kV | kV
1181 | DNOM Component | Composite Switch | COMPSW | input | ABNDATETIME | Date and time of last status change. | String
1182 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.AREAIND | Dynamic array of permission area indices of collected objects | String |  |  |  | DNMOBJ
1183 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.BOUNDARY | Dynamic array of branch masks | String |  |  |  | BRANCH
1184 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.CHGNOPEN | Dynamic array of change the normal open status flags | String |  |  |  | SWT
1185 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.CURROPEN | Dynamic array of current open status flags | String |  |  |  | SWT
1186 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.DEVTYPE | Dynamic array of device types (1 = Switch, 2 = Fuse, 3 = Recloser, 4 = Breaker, 5 = Sectionalizer, 6 = Jumper) | String |  |  |  | SWT
1187 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.DNOMX | Dynamic array of X coordinations of collected objects | String |  |  |  | DNMOBJ
1188 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.DNOMY | Dynamic array of Y coordinations of collected objects | String |  |  |  | DNMOBJ
1189 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.DSOOVER | Dynamic array of enumerations of advanced application eligibility override statuses (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | String |  |  |  | SWT
1190 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.FROMEMS | Dynamic array of flags indicating that the data is from the EMS | String |  |  |  | TOPOLOGYOBJECT
1191 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.ID | Dynamic array of IDs of collected objects | String |  |  |  | DNMOBJ
1192 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.NAME | Dynamic array of names of collected objects | String |  |  |  | DNMOBJ
1193 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.NEWATMSK | Dynamic array of additional attribute masks | String |  |  |  | TOPOLOGYOBJECT
1194 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.NEWATMSK2 | Dynamic array of second additional attribute masks | String |  |  |  | TOPOLOGYOBJECT
1195 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.NOPEN | Dynamic array of normally open status flags | String |  |  |  | SWT
1196 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.NTPFLAG | Dynamic array of NTP flag enumerations | String |  |  |  | TOPOLOGYOBJECT
1197 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.REMOTE | Dynamic array of remote status flags | String |  |  |  | SWT
1198 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.SWMASK | Dynamic array of switch attribute masks | String |  |  |  | SWT
1199 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT.SWMASK2 | Dynamic array of switch attribute masks | String |  |  |  | SWT
1200 | DNOM Component | Composite Switch | COMPSW |  | ABNDATETIME_TICKS | The time when the component’s status changed to abnormal | String
1201 | DNOM Component | Composite Switch | COMPSW | input | ADDRESS | Pointer to a string with the address in the station vector collection | String |  |  |  | NDPFST
1202 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.AREAIND | Permission area index of the composite switch | String |  |  |  | DNMOBJ
1203 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.ID | Type of the composite switch | String |  |  |  | DNMOBJ
1204 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.INITMODE | Initial operating mode (true = automatic, false = manual). | Boolean |  |  |  | CSWMOD
1205 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.NAME | Associated composite switch model. | String
1206 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.NUMLINK | Number of switch links. | Integer |  |  |  | CSWMOD
1207 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.NUMSTATE | The number of different state the switch can be. | Integer |  |  |  | CSWMOD
1208 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.RECONFIG | Reconfigurable flag for geoschematics (true = reconfigurable). | Boolean |  |  |  | CSWMOD
1209 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.STNAME | Array of state names | String |  |  |  | CSWMOD
1210 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.STSCADAVAL | Array of SCADA state values associated with the switch states | String |  |  |  | CSWMOD
1211 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.STVALUE | Array of valid switch states | String |  |  |  | CSWMOD
1212 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD.SWTYPE | Enumerated composite switch model type, 1 = Throwover, 2 = ESCO Throwover, 3 = RAL, 4 = GRAL, 5 = Regulator Bypass, 6 = UG Multi Switch. | Integer |  |  |  | CSWMOD
1213 | DNOM Component | Composite Switch | COMPSW | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
1214 | DNOM Component | Composite Switch | COMPSW | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1215 | DNOM Component | Composite Switch | COMPSW | input | ARRYSWIT | Array of switch pointers (obtained from the indexes) | String
1216 | DNOM Component | Composite Switch | COMPSW | input | CMPSWBMK | Combined state variable which packages up the current state, auto/manual status, and preferred switch state into a single integer value.. | Integer
1217 | DNOM Component | Composite Switch | COMPSW | input | CMPSWMOD | Pointer to the associated composite switch model | String
1218 | DNOM Component | Composite Switch | COMPSW | input | COMPCURSTATE | Current state name. | String
1219 | DNOM Component | Composite Switch | COMPSW | input | COMPHASMULTTAG | Flag indicating whether the component has multiple tag | Boolean
1220 | DNOM Component | Composite Switch | COMPSW | input | COMPHASTAG | Component tag field. | Integer
1221 | DNOM Component | Composite Switch | COMPSW | input | COMPSTATE1 | Composite switch state name 1. | String
1222 | DNOM Component | Composite Switch | COMPSW | input | COMPSTATE2 | Composite switch state name 2. | String
1223 | DNOM Component | Composite Switch | COMPSW | input | COMPSTATE3 | Composite switch state name 3. | String
1224 | DNOM Component | Composite Switch | COMPSW | input | COMPSTATE4 | Composite switch state name 4. | String
1225 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1ABNORMAL | Switch #1 phases Abnormally Energized | String
1226 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1CLOSEDPHASES | Switch #1 closed phases | String
1227 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1DEENERGIZED | Switch #1 phases deenergized | String
1228 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1DYNFEEDERNAME | Switch #1 dynamic feeder name | String
1229 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1DYNFEEDERNAME2 | Switch #1 dynamic feeder 2 name | String
1230 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1DYNSTATIONNAME | Switch #1 dynamic station name | String
1231 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1DYNSTATIONNAME2 | Switch #1 dynamic station 2 name | String
1232 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1ENERGIZED | Switch #1 phases energized | String
1233 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1FEEDERNAME | Switch #1 nominal feeder name | String
1234 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVA3PH | Real power flow of phase ABC in kVA for switch #1 | Float
1235 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVAA | Real power flow of phase A in kVA for switch #1 | Float
1236 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVAB | Real power flow of phase B in kVA for switch #1 | Float
1237 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVAC | Real power flow of phase C in kVA for switch #1 | Float
1238 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVAR3PH | Real power flow of phase ABC in kVAR for switch #1 | Float
1239 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVARA | Real power flow of phase A in kVAR for switch #1 | Float
1240 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVARB | Real power flow of phase B in kVAR for switch #1 | Float
1241 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KVARC | Real power flow of phase C in kVAR for switch #1 | Float
1242 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KW3PH | Real power flow of phase ABC in kW for switch #1 | Float
1243 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KWA | Real power flow of phase A in kW for switch #1 | Float
1244 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KWB | Real power flow of phase B in kW for switch #1 | Float
1245 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1KWC | Real power flow of phase C in kW for switch #1 | Float
1246 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM1 | Level 1 limit value for switch #1 | Float
1247 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM1NAME | Level 1 limit name for switch #1 | String
1248 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM1SEASON | Level 1 limit season for switch #1 | String
1249 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM2 | Level 2 limit value for switch #1 | Float
1250 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM2NAME | Level 2 limit name for switch #1 | String
1251 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM2SEASON | Level 2 limit season for switch #1 | String
1252 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM3 | Level 3 limit value for switch #1 | Float
1253 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM3NAME | Level 3 limit name for switch #1 | String
1254 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM3SEASON | Level 3 limit season for switch #1 | String
1255 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM4 | Level 4 limit value for switch #1 | Float
1256 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM4NAME | Level 4 limit name for switch #1 | String
1257 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM4SEASON | Level 4 limit season for switch #1 | String
1258 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM5 | Level 5 limit value for switch #1 | Float
1259 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM5NAME | Level 5 limit name for switch #1 | String
1260 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LIM5SEASON | Level 5 limit season for switch #1 | String
1261 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1LOOPED | Switch #1 phases currently in a loop. | String
1262 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1NORMALLYDEENERGIZED | Is switch #1 normally de-energized? | Boolean
1263 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1NORMALLYLOOPED | Is the switch #1 normally looped? | Boolean
1264 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1OPENPHASES | Switch #1 open phases | String
1265 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1OPERATINGKV | Switch #1 nominal voltage | Float
1266 | DNOM Component | Composite Switch | COMPSW | output | COMPSW1PFA | Switch #1 phase A power factor | Float
1267 | DNOM Component | Composite Switch | COMPSW | output | COMPSW1PFABC | Switch #1 phase ABC power factor | Float
1268 | DNOM Component | Composite Switch | COMPSW | output | COMPSW1PFB | Switch #1 phase B power factor | Float
1269 | DNOM Component | Composite Switch | COMPSW | output | COMPSW1PFC | Switch #1 phase C power factor | Float
1270 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHAAMPS | Phase A current flow for switch #1 | Float
1271 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHALOADING | Phase A percent loading for switch #1 | Float
1272 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHASEAANGLEDIFF | The voltage angle difference of phase A between two nodes for switch #1 | Float
1273 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHASEBANGLEDIFF | The voltage angle difference of phase B between two nodes for switch #1 | Float
1274 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHASECANGLEDIFF | The voltage angle difference of phase C between two nodes for switch #1 | Float
1275 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHBAMPS | Phase B current flow for switch #1 | Float
1276 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHBLOADING | Phase B percent loading for switch #1 | Float
1277 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHCAMPS | Phase C current flow for switch #1 | Float
1278 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1PHCLOADING | Phase C percent loading for switch #1 | Float
1279 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1REMTOP | Switch #1 phases that are removed from topology due to multiple source energization | String
1280 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1SIZE | Switch #1 size | Float
1281 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1STATIONNAME | Switch #1 nominal station name | String
1282 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1TYPE | Switch #1 type | String
1283 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANA | Phase A side 1 voltage for switch #1 | Float
1284 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANALG | Phase A side 1 LG voltage for switch #1 | Float
1285 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANALL | Phase A side 1 LL voltage for switch #1 | Float
1286 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANATO | Phase A side 2 voltage for switch #1 | Float
1287 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANATOLG | Phase A side 2 LG voltage for switch #1 | Float
1288 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANATOLL | Phase A side 2 LL voltage for switch #1 | Float
1289 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANB | Phase B side 1 voltage for switch #1 | Float
1290 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANBLG | Phase B side 1 LG voltage for switch #1 | Float
1291 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANBLL | Phase B side 1 LL voltage for switch #1 | Float
1292 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANBTO | Phase B side 2 voltage for switch #1 | Float
1293 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANBTOLG | Phase B side 2 LG voltage for switch #1 | Float
1294 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANBTOLL | Phase B side 2 LL voltage for switch #1 | Float
1295 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANC | Phase C side 1 voltage for switch #1 | Float
1296 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANCLG | Phase C side 1 LG voltage for switch #1 | Float
1297 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANCLL | Phase C side 1 LL voltage for switch #1 | Float
1298 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANCTO | Phase C side 2 voltage for switch #1 | Float
1299 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANCTOLG | Phase C side 2 LG voltage for switch #1 | Float
1300 | DNOM Component | Composite Switch | COMPSW | input | COMPSW1VOLTANCTOLL | Phase C side 2 LL voltage for switch #1 | Float
1301 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2ABNORMAL | Switch #2 phases Abnormally Energized | String
1302 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2CLOSEDPHASES | Switch #2 closed phases | String
1303 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2DEENERGIZED | Switch #2 phases deenergized | String
1304 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2DYNFEEDERNAME | Switch #2 dynamic feeder name | String
1305 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2DYNFEEDERNAME2 | Switch #2 dynamic feeder 2 name | String
1306 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2DYNSTATIONNAME | Switch #2 dynamic station name | String
1307 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2DYNSTATIONNAME2 | Switch #2 dynamic station 2 name | String
1308 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2ENERGIZED | Switch #2 phases energized | String
1309 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2FEEDERNAME | Switch #2 nominal feeder name | String
1310 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVA3PH | Real power flow of phase ABC in kVA for switch #2 | Float
1311 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVAA | Real power flow of phase A in kVA for switch #2 | Float
1312 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVAB | Real power flow of phase B in kVA for switch #2 | Float
1313 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVAC | Real power flow of phase C in kVA for switch #2 | Float
1314 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVAR3PH | Real power flow of phase ABC in kVAR for switch #2 | Float
1315 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVARA | Real power flow of phase A in kVAR for switch #2 | Float
1316 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVARB | Real power flow of phase B in kVAR for switch #2 | Float
1317 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KVARC | Real power flow of phase C in kVAR for switch #2 | Float
1318 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KW3PH | Real power flow of phase ABC in kW for switch #2 | Float
1319 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KWA | Real power flow of phase A in kW for switch #2 | Float
1320 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KWB | Real power flow of phase B in kW for switch #2 | Float
1321 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2KWC | Real power flow of phase C in kW for switch #2 | Float
1322 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM1 | Level 1 limit value for switch #2 | Float
1323 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM1NAME | Level 1 limit name for switch #2 | String
1324 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM1SEASON | Level 1 limit season for switch #2 | String
1325 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM2 | Level 2 limit value for switch #2 | Float
1326 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM2NAME | Level 2 limit name for switch #2 | String
1327 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM2SEASON | Level 2 limit season for switch #2 | String
1328 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM3 | Level 3 limit value for switch #2 | Float
1329 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM3NAME | Level 3 limit name for switch #2 | String
1330 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM3SEASON | Level 3 limit season for switch #2 | String
1331 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM4 | Level 4 limit value for switch #2 | Float
1332 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM4NAME | Level 4 limit name for switch #2 | String
1333 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM4SEASON | Level 4 limit season for switch #2 | String
1334 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM5 | Level 5 limit value for switch #2 | Float
1335 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM5NAME | Level 5 limit name for switch #2 | String
1336 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LIM5SEASON | Level 5 limit season for switch #2 | String
1337 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2LOOPED | Switch #2 phases currently in a loop. | String
1338 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2NORMALLYDEENERGIZED | Is switch #2 normally de-energized? | Boolean
1339 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2NORMALLYLOOPED | Is the switch #2 normally looped? | Boolean
1340 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2OPENPHASES | Switch #2 open phases | String
1341 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2OPERATINGKV | Switch #2 nominal voltage | Float
1342 | DNOM Component | Composite Switch | COMPSW | output | COMPSW2PFA | Switch #2 phase A power factor | Float
1343 | DNOM Component | Composite Switch | COMPSW | output | COMPSW2PFABC | Switch #2 phase ABC power factor | Float
1344 | DNOM Component | Composite Switch | COMPSW | output | COMPSW2PFB | Switch #2 phase B power factor | Float
1345 | DNOM Component | Composite Switch | COMPSW | output | COMPSW2PFC | Switch #2 phase C power factor | Float
1346 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHAAMPS | Phase A current flow for switch #2 | Float
1347 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHALOADING | Phase A percent loading for switch #2 | Float
1348 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHASEAANGLEDIFF | The voltage angle difference of phase A between two nodes for switch #2 | Float
1349 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHASEBANGLEDIFF | The voltage angle difference of phase B between two nodes for switch #2 | Float
1350 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHASECANGLEDIFF | The voltage angle difference of phase C between two nodes for switch #2 | Float
1351 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHBAMPS | Phase B current flow for switch #2 | Float
1352 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHBLOADING | Phase B percent loading for switch #2 | Float
1353 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHCAMPS | Phase C current flow for switch #2 | Float
1354 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2PHCLOADING | Phase C percent loading for switch #2 | Float
1355 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2REMTOP | Switch #2 phases that are removed from topology due to multiple source energization | String
1356 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2SIZE | Switch #2 size | Float
1357 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2STATIONNAME | Switch #2 nominal station name | String
1358 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2TYPE | Switch #2 type | String
1359 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANA | Phase A side 1 voltage for switch #2 | Float
1360 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANALG | Phase A side 1 LG voltage for switch #2 | Float
1361 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANALL | Phase A side 1 LL voltage for switch #2 | Float
1362 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANATO | Phase A side 2 voltage for switch #2 | Float
1363 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANATOLG | Phase A side 2 LG voltage for switch #2 | Float
1364 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANATOLL | Phase A side 2 LL voltage for switch #2 | Float
1365 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANB | Phase B side 1 voltage for switch #2 | Float
1366 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANBLG | Phase B side 1 LG voltage for switch #2 | Float
1367 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANBLL | Phase B side 1 LL voltage for switch #2 | Float
1368 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANBTO | Phase B side 2 voltage for switch #2 | Float
1369 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANBTOLG | Phase B side 2 LG voltage for switch #2 | Float
1370 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANBTOLL | Phase B side 2 LL voltage for switch #2 | Float
1371 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANC | Phase C side 1 voltage for switch #2 | Float
1372 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANCLG | Phase C side 1 LG voltage for switch #2 | Float
1373 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANCLL | Phase C side 1 LL voltage for switch #2 | Float
1374 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANCTO | Phase C side 2 voltage for switch #2 | Float
1375 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANCTOLG | Phase C side 2 LG voltage for switch #2 | Float
1376 | DNOM Component | Composite Switch | COMPSW | input | COMPSW2VOLTANCTOLL | Phase C side 2 LL voltage for switch #2 | Float
1377 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3ABNORMAL | Switch #3 phases Abnormally Energized | String
1378 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3CLOSEDPHASES | Switch #3 closed phases | String
1379 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3DEENERGIZED | Switch #3 phases deenergized | String
1380 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3DYNFEEDERNAME | Switch #3 dynamic feeder name | String
1381 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3DYNFEEDERNAME2 | Switch #3 dynamic feeder 2 name | String
1382 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3DYNSTATIONNAME | Switch #3 dynamic station name | String
1383 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3DYNSTATIONNAME2 | Switch #3 dynamic station 2 name | String
1384 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3ENERGIZED | Switch #3 phases energized | String
1385 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3FEEDERNAME | Switch #3 nominal feeder name | String
1386 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVA3PH | Real power flow of phase ABC in kVA for switch #3 | Float
1387 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVAA | Real power flow of phase A in kVA for switch #3 | Float
1388 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVAB | Real power flow of phase B in kVA for switch #3 | Float
1389 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVAC | Real power flow of phase C in kVA for switch #3 | Float
1390 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVAR3PH | Real power flow of phase ABC in kVAR for switch #3 | Float
1391 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVARA | Real power flow of phase A in kVAR for switch #3 | Float
1392 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVARB | Real power flow of phase B in kVAR for switch #3 | Float
1393 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KVARC | Real power flow of phase C in kVAR for switch #3 | Float
1394 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KW3PH | Real power flow of phase ABC in kW for switch #3 | Float
1395 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KWA | Real power flow of phase A in kW for switch #3 | Float
1396 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KWB | Real power flow of phase B in kW for switch #3 | Float
1397 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3KWC | Real power flow of phase C in kW for switch #3 | Float
1398 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM1 | Level 1 limit value for switch #3 | Float
1399 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM1NAME | Level 1 limit name for switch #3 | String
1400 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM1SEASON | Level 1 limit season for switch #3 | String
1401 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM2 | Level 2 limit value for switch #3 | Float
1402 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM2NAME | Level 2 limit name for switch #3 | String
1403 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM2SEASON | Level 2 limit season for switch #3 | String
1404 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM3 | Level 3 limit value for switch #3 | Float
1405 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM3NAME | Level 3 limit name for switch #3 | String
1406 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM3SEASON | Level 3 limit season for switch #3 | String
1407 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM4 | Level 4 limit value for switch #3 | Float
1408 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM4NAME | Level 4 limit name for switch #3 | String
1409 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM4SEASON | Level 4 limit season for switch #3 | String
1410 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM5 | Level 5 limit value for switch #3 | Float
1411 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM5NAME | Level 5 limit name for switch #3 | String
1412 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LIM5SEASON | Level 5 limit season for switch #3 | String
1413 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3LOOPED | Switch #3 phases currently in a loop. | String
1414 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3NORMALLYDEENERGIZED | Is switch #3 normally de-energized? | Boolean
1415 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3NORMALLYLOOPED | Is the switch #3 normally looped? | Boolean
1416 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3OPENPHASES | Switch #3 open phases | String
1417 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3OPERATINGKV | Switch #3 nominal voltage | Float
1418 | DNOM Component | Composite Switch | COMPSW | output | COMPSW3PFA | Switch #3 phase A power factor | Float
1419 | DNOM Component | Composite Switch | COMPSW | output | COMPSW3PFABC | Switch #3 phase ABC power factor | Float
1420 | DNOM Component | Composite Switch | COMPSW | output | COMPSW3PFB | Switch #3 phase B power factor | Float
1421 | DNOM Component | Composite Switch | COMPSW | output | COMPSW3PFC | Switch #3 phase C power factor | Float
1422 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHAAMPS | Phase A current flow for switch #3 | Float
1423 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHALOADING | Phase A percent loading for switch #3 | Float
1424 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHASEAANGLEDIFF | The voltage angle difference of phase A between two nodes for switch #3 | Float
1425 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHASEBANGLEDIFF | The voltage angle difference of phase B between two nodes for switch #3 | Float
1426 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHASECANGLEDIFF | The voltage angle difference of phase C between two nodes for switch #3 | Float
1427 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHBAMPS | Phase B current flow for switch #3 | Float
1428 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHBLOADING | Phase B percent loading for switch #3 | Float
1429 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHCAMPS | Phase C current flow for switch #3 | Float
1430 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3PHCLOADING | Phase C percent loading for switch #3 | Float
1431 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3REMTOP | Switch #3 phases that are removed from topology due to multiple source energization | String
1432 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3SIZE | Switch #3 size | Float
1433 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3STATIONNAME | Switch #3 nominal station name | String
1434 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3TYPE | Switch #3 type | String
1435 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANA | Phase A side 1 voltage for switch #3 | Float
1436 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANALG | Phase A side 1 LG voltage for switch #3 | Float
1437 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANALL | Phase A side 1 LL voltage for switch #3 | Float
1438 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANATO | Phase A side 2 voltage for switch #3 | Float
1439 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANATOLG | Phase A side 2 LG voltage for switch #3 | Float
1440 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANATOLL | Phase A side 2 LL voltage for switch #3 | Float
1441 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANB | Phase B side 1 voltage for switch #3 | Float
1442 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANBLG | Phase B side 1 LG voltage for switch #3 | Float
1443 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANBLL | Phase B side 1 LL voltage for switch #3 | Float
1444 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANBTO | Phase B side 2 voltage for switch #3 | Float
1445 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANBTOLG | Phase B side 2 LG voltage for switch #3 | Float
1446 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANBTOLL | Phase B side 2 LL voltage for switch #3 | Float
1447 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANC | Phase C side 1 voltage for switch #3 | Float
1448 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANCLG | Phase C side 1 LG voltage for switch #3 | Float
1449 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANCLL | Phase C side 1 LL voltage for switch #3 | Float
1450 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANCTO | Phase C side 2 voltage for switch #3 | Float
1451 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANCTOLG | Phase C side 2 LG voltage for switch #3 | Float
1452 | DNOM Component | Composite Switch | COMPSW | input | COMPSW3VOLTANCTOLL | Phase C side 2 LL voltage for switch #3 | Float
1453 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4ABNORMAL | Switch #4 phases Abnormally Energized | String
1454 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4CLOSEDPHASES | Switch #4 closed phases | String
1455 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4DEENERGIZED | Switch #4 phases deenergized | String
1456 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4DYNFEEDERNAME | Switch #4 dynamic feeder name | String
1457 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4DYNFEEDERNAME2 | Switch #4 dynamic feeder 2 name | String
1458 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4DYNSTATIONNAME | Switch #4 dynamic station name | String
1459 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4DYNSTATIONNAME2 | Switch #4 dynamic station 2 name | String
1460 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4ENERGIZED | Switch #4 phases energized | String
1461 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4FEEDERNAME | Switch #4 nominal feeder name | String
1462 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVA3PH | Real power flow of phase ABC in kVA for switch #4 | Float
1463 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVAA | Real power flow of phase A in kVA for switch #4 | Float
1464 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVAB | Real power flow of phase B in kVA for switch #4 | Float
1465 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVAC | Real power flow of phase C in kVA for switch #4 | Float
1466 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVAR3PH | Real power flow of phase ABC in kVAR for switch #4 | Float
1467 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVARA | Real power flow of phase A in kVAR for switch #4 | Float
1468 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVARB | Real power flow of phase B in kVAR for switch #4 | Float
1469 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KVARC | Real power flow of phase C in kVAR for switch #4 | Float
1470 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KW3PH | Real power flow of phase ABC in kW for switch #4 | Float
1471 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KWA | Real power flow of phase A in kW for switch #4 | Float
1472 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KWB | Real power flow of phase B in kW for switch #4 | Float
1473 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4KWC | Real power flow of phase C in kW for switch #4 | Float
1474 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM1 | Level 1 limit value for switch #4 | Float
1475 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM1NAME | Level 1 limit name for switch #4 | String
1476 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM1SEASON | Level 1 limit season for switch #4 | String
1477 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM2 | Level 2 limit value for switch #4 | Float
1478 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM2NAME | Level 2 limit name for switch #4 | String
1479 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM2SEASON | Level 2 limit season for switch #4 | String
1480 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM3 | Level 3 limit value for switch #4 | Float
1481 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM3NAME | Level 3 limit name for switch #4 | String
1482 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM3SEASON | Level 3 limit season for switch #4 | String
1483 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM4 | Level 4 limit value for switch #4 | Float
1484 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM4NAME | Level 4 limit name for switch #4 | String
1485 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM4SEASON | Level 4 limit season for switch #4 | String
1486 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM5 | Level 5 limit value for switch #4 | Float
1487 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM5NAME | Level 5 limit name for switch #4 | String
1488 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LIM5SEASON | Level 5 limit season for switch #4 | String
1489 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4LOOPED | Switch #4 phases currently in a loop. | String
1490 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4NORMALLYDEENERGIZED | Is switch #4 normally de-energized? | Boolean
1491 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4NORMALLYLOOPED | Is the switch #4 normally looped? | Boolean
1492 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4OPENPHASES | Switch #4 open phases | String
1493 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4OPERATINGKV | Switch #4 nominal voltage | Float
1494 | DNOM Component | Composite Switch | COMPSW | output | COMPSW4PFA | Switch #4 phase A power factor | Float
1495 | DNOM Component | Composite Switch | COMPSW | output | COMPSW4PFABC | Switch #4 phase ABC power factor | Float
1496 | DNOM Component | Composite Switch | COMPSW | output | COMPSW4PFB | Switch #4 phase B power factor | Float
1497 | DNOM Component | Composite Switch | COMPSW | output | COMPSW4PFC | Switch #4 phase C power factor | Float
1498 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHAAMPS | Phase A current flow for switch #4 | Float
1499 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHALOADING | Phase A percent loading for switch #4 | Float
1500 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHASEAANGLEDIFF | The voltage angle difference of phase A between two nodes for switch #4 | Float
1501 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHASEBANGLEDIFF | The voltage angle difference of phase B between two nodes for switch #4 | Float
1502 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHASECANGLEDIFF | The voltage angle difference of phase C between two nodes for switch #4 | Float
1503 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHBAMPS | Phase B current flow for switch #4 | Float
1504 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHBLOADING | Phase B percent loading for switch #4 | Float
1505 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHCAMPS | Phase C current flow for switch #4 | Float
1506 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4PHCLOADING | Phase C percent loading for switch #4 | Float
1507 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4REMTOP | Switch #4 phases that are removed from topology due to multiple source energization | String
1508 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4SIZE | Switch #4 size | Float
1509 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4STATIONNAME | Switch #4 nominal station name | String
1510 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4TYPE | Switch #4 type | String
1511 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANA | Phase A side 1 voltage for switch #4 | Float
1512 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANALG | Phase A side 1 LG voltage for switch #4 | Float
1513 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANALL | Phase A side 1 LL voltage for switch #4 | Float
1514 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANATO | Phase A side 2 voltage for switch #4 | Float
1515 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANATOLG | Phase A side 2 LG voltage for switch #4 | Float
1516 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANATOLL | Phase A side 2 LL voltage for switch #4 | Float
1517 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANB | Phase B side 1 voltage for switch #4 | Float
1518 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANBLG | Phase B side 1 LG voltage for switch #4 | Float
1519 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANBLL | Phase B side 1 LL voltage for switch #4 | Float
1520 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANBTO | Phase B side 2 voltage for switch #4 | Float
1521 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANBTOLG | Phase B side 2 LG voltage for switch #4 | Float
1522 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANBTOLL | Phase B side 2 LL voltage for switch #4 | Float
1523 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANC | Phase C side 1 voltage for switch #4 | Float
1524 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANCLG | Phase C side 1 LG voltage for switch #4 | Float
1525 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANCLL | Phase C side 1 LL voltage for switch #4 | Float
1526 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANCTO | Phase C side 2 voltage for switch #4 | Float
1527 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANCTOLG | Phase C side 2 LG voltage for switch #4 | Float
1528 | DNOM Component | Composite Switch | COMPSW | input | COMPSW4VOLTANCTOLL | Phase C side 2 LL voltage for switch #4 | Float
1529 | DNOM Component | Composite Switch | COMPSW | input | COMPSWALTERNATE | For throwover switches, the alternate state name. | String
1530 | DNOM Component | Composite Switch | COMPSW | input | COMPSWALTSUBNAMEDYN | The second switch link dynamic station name. | String
1531 | DNOM Component | Composite Switch | COMPSW | input | COMPSWALTSUBNAMENOM | The second switch link nominal station name. | String
1532 | DNOM Component | Composite Switch | COMPSW | input | COMPSWAREANAME | Associated area name. | String
1533 | DNOM Component | Composite Switch | COMPSW | input | COMPSWAUTOMANUALSTATUS | Current throwover operation status (for throwover devices). Returns "Manual" or "Automatic". | String
1534 | DNOM Component | Composite Switch | COMPSW | input | COMPSWSTATE1AUTOMANUALSTATUS | Composite switch state 1 operation status. Returns "Manual" or "Automatic". | String
1535 | DNOM Component | Composite Switch | COMPSW | input | COMPSWSTATE2AUTOMANUALSTATUS | Composite switch state 2 operation status. Returns "Manual" or "Automatic". | String
1536 | DNOM Component | Composite Switch | COMPSW | input | COMPSWSTATE3AUTOMANUALSTATUS | Composite switch state 3 operation status. Returns "Manual" or "Automatic". | String
1537 | DNOM Component | Composite Switch | COMPSW | input | COMPSWSTATE4AUTOMANUALSTATUS | Composite switch state 4 operation status. Returns "Manual" or "Automatic". | String
1538 | DNOM Component | Composite Switch | COMPSW | input | COMPSWCONSTRUCTPHASES | Constructed phases | String
1539 | DNOM Component | Composite Switch | COMPSW | input | COMPSWCURRENT | Current state name. | String
1540 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDDBCOORD | DDB coordinate. | String
1541 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDMSDYNAMICSTATNAME | Dynamic substation of first switch link. | String
1542 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDMSSTATNAME | Nominal DMS substation name. | String
1543 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDPFSTATUS | Power flow status | String
1544 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDYNAMICFEED1 | The first switch link dynamic feeder name. | String
1545 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDYNAMICFEED2 | The second switch link dynamic feeder name. | String
1546 | DNOM Component | Composite Switch | COMPSW | input | COMPSWDYNFEEDERNAME | Composite switch dynamic feeder name | String
1547 | DNOM Component | Composite Switch | COMPSW | input | COMPSWEMSSTATNAME | Nominal EMS substation name. | String
1548 | DNOM Component | Composite Switch | COMPSW | input | COMPSWFUTUREPHASES | Future phases | String
1549 | DNOM Component | Composite Switch | COMPSW | input | COMPSWISAUTOTHROWOVER | Flag indicating whether the composite switch is an automatic throwover device. | Boolean
1550 | DNOM Component | Composite Switch | COMPSW | input | COMPSWMASTER | ID of master switch for throwover switches. | String
1551 | DNOM Component | Composite Switch | COMPSW | input | COMPSWMASTERADDRESS | Address of master switch for throwover switches. | String
1552 | DNOM Component | Composite Switch | COMPSW | input | COMPSWNOMINALFEED1 | The first switch link nominal feeder name. | String
1553 | DNOM Component | Composite Switch | COMPSW | input | COMPSWNOMINALFEED2 | The second switch link nominal feeder name. | String
1554 | DNOM Component | Composite Switch | COMPSW | input | COMPSWNORMAL | Nominal state name. | String
1555 | DNOM Component | Composite Switch | COMPSW | input | COMPSWOPERATINGKV | Operating voltage (kV line to line). | Float
1556 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPERMMANOP | Flag indicating device is only manually operated (for throwover devices only). If the device is only manually operated, return “Manual Only”, otherwise, return “Auto Or Manual”. | String
1557 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPFCOMPTIME | Completion time of power flow calculation | String
1558 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHAAMPS | Phase A current flow for closed switch link (Amps). | Complex | DPF | Amps | Amps
1559 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHALOADING | Phase A percent loading for closed switch link. | Float | DPF | percent | percent
1560 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHALT | Non-neutral phases measured on the alternate side of throwover switches. | String
1561 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHASEA | The flag indicating whether the switch has phase A. | Boolean
1562 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHASEB | The flag indicating whether the switch has phase B. | Boolean
1563 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHASEC | The flag indicating whether the switch has phase C. | Boolean
1564 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHASEN | The flag indicating whether the switch has phase N. | Boolean
1565 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHBAMPS | Phase B current flow for closed switch link (Amps). | Complex | DPF | Amps | Amps
1566 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHBLOADING | Phase B percent loading for closed switch link. | Float | DPF | percent | percent
1567 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHCAMPS | Phase C current flow for closed switch link (Amps). | Complex | DPF | Amps | Amps
1568 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHCLOADING | Phase C percent loading for closed switch link. | Float | DPF | percent | percent
1569 | DNOM Component | Composite Switch | COMPSW | output | COMPSWPHNAMPS | Phase N current flow for closed switch link (Amps). | Complex | DPF | Amps | Amps
1570 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPHPREF | Non-neutral phases measured on the preferred side of throwover switches. | String
1571 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPREFERRED | For throwover switches, the preferred state name. | String
1572 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPREFSUBNAMEDYN | The first switch link dynamic station name. | String
1573 | DNOM Component | Composite Switch | COMPSW | input | COMPSWPREFSUBNAMENOM | The first switch link nominal station name. | String
1574 | DNOM Component | Composite Switch | COMPSW | input | COMPSWSIZE | Size of individual switch links. | Float
1575 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTALARMSTATUS | Composite switch alarm status. Measured value | String
1576 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTAUTORECLSTATUS | Composite switch autoreclosing status. Measured value | String
1577 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTCURPOSSTATUS | Composite switch open/closed status. Measured value | String
1578 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTCURPOSSTATUSMEASID | Composite switch open/closed measurement ID | String
1579 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTHOTLINETAGSTATUS | Composite switch hot line status. Measured value | String
1580 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTHROWFEED | Current energizing feeder. | String
1581 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTHROWSTATION | Current energizing station. | String
1582 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTLOCKOUTSTATUS | Composite switch lockout status. Measured value | String
1583 | DNOM Component | Composite Switch | COMPSW | output | COMPSWTOTALKVAR | Total three-phase reactive power for closed switch link (in kVAR). | Float | DPF | kVAR | kVAR
1584 | DNOM Component | Composite Switch | COMPSW | output | COMPSWTOTALKW | Total three-phase real power for closed switch link (in kW). | Float | DPF | kW | kW
1585 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTRECLOSEROPMODESTATUS | Composite switch recloser operation mode status. Measured value | String
1586 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTREMOTECONTROLSTATUS | Composite switch Local/Remote status. Measured value | String
1587 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTSUPERVISORYCUTOUTSTATUS | Composite switch supervisory cutout status. Measured value | String
1588 | DNOM Component | Composite Switch | COMPSW | input | COMPSWTYPE | Composite switch model type (Throwover, ESCO Throwover, RAL, GRAL, Regulator Bypass, UG Multi Switch, Grounding Switch, RAG, or RAC) | String
1589 | DNOM Component | Composite Switch | COMPSW | input | COMPSWUSERTYPE | Composite switch type defined by user | String
1590 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTANA | Phase A side 1 voltage for closed switch link (in configurable voltage base with angle in degrees). | Float | DPF | Volt | Volt
1591 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTANB | Phase B side 1 voltage for closed switch link (in configurable voltage base with angle in degrees). | Float | DPF | Volt | Volt
1592 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTANC | Phase C side 1 voltage for closed switch link (in configurable voltage base with angle in degrees). | Float | DPF | Volt | Volt
1593 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTOPA | Phase A side 1 voltage for closed switch link (in configurable voltage base with no angle). | Float | DPF | Volt | Volt
1594 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTOPB | Phase B side 1 voltage for closed switch link (in configurable voltage base with no angle). | Float | DPF | Volt | Volt
1595 | DNOM Component | Composite Switch | COMPSW | output | COMPSWVOLTOPC | Phase C side 1 voltage for closed switch link (in configurable voltage base with no angle). | Float | DPF | Volt | Volt
1596 | DNOM Component | Composite Switch | COMPSW | input | CTRLPNTCNT | The number of control points | Integer
1597 | DNOM Component | Composite Switch | COMPSW | input | DEVICEDSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String
1598 | DNOM Component | Composite Switch | COMPSW | input | DISPLAYCOMPSTATE1 | Composite switch state name 1. | String
1599 | DNOM Component | Composite Switch | COMPSW | input | DISPLAYCOMPSTATE2 | Composite switch state name 2. | String
1600 | DNOM Component | Composite Switch | COMPSW | input | DISPLAYCOMPSTATE3 | Composite switch state name 3. | String
1601 | DNOM Component | Composite Switch | COMPSW | input | DISPLAYCOMPSTATE4 | Composite switch state name 4. | String
1602 | DNOM Component | Composite Switch | COMPSW | input | DNOMRECORDNAME | The DNOM record name of the composite switch. | String |  |  |  | DNMOBJ
1603 | DNOM Component | Composite Switch | COMPSW | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1604 | DNOM Component | Composite Switch | COMPSW | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1605 | DNOM Component | Composite Switch | COMPSW |  | DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration
1606 | DNOM Component | Composite Switch | COMPSW | input | EQUIPFROMEMS | Flag indicating whether the composite switch is station internal device. | Boolean
1607 | DNOM Component | Composite Switch | COMPSW | input | FROMFEEDER | Nominal feeder of from node of the first switch link. | String
1608 | DNOM Component | Composite Switch | COMPSW | input | HASCOMPSTATE1 | Indicates whether the switch has composite switch state 1 | Boolean
1609 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
1610 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.ID | ID of the internal geometry | String |  |  |  | DNMOBJ
1611 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
1612 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1613 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1614 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1615 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1616 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1617 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1618 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1619 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1620 | DNOM Component | Composite Switch | COMPSW | input | HASCOMPSTATE2 | Indicates whether the switch has composite switch state 2 | Boolean
1621 | DNOM Component | Composite Switch | COMPSW | input | HASCOMPSTATE3 | Indicates whether the switch has composite switch state 3 | Boolean
1622 | DNOM Component | Composite Switch | COMPSW | input | HASCOMPSTATE4 | Indicates whether the switch has composite switch state 4 | Boolean
1623 | DNOM Component | Composite Switch | COMPSW | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1624 | DNOM Component | Composite Switch | COMPSW | input | INTGEOM | Array of internal world geometry pointers | String
1625 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSW1AVAILABLE | Does composite switch contain switch #1 | Boolean
1626 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSW2AVAILABLE | Does composite switch contain switch #2 | Boolean
1627 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSW3AVAILABLE | Does composite switch contain switch #3 | Boolean
1628 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | Float |  |  |  | JUNCCONT
1629 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | Float |  |  |  | JUNCCONT
1630 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | JUNCCONT
1631 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | Float |  |  |  | JUNCCONT
1632 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | Float |  |  |  | JUNCCONT
1633 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT.TYPEMASK | Type | Integer |  |  |  | JUNCCONT
1634 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSW4AVAILABLE | Does composite switch contain switch #4 | Boolean
1635 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWAUTOSTATUS | Indicates whether the composite switch status is auto | Boolean
1636 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWSTATE1AUTOSTATUS | Indicates whether the composite switch state 1 status is Auto | Boolean
1637 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWSTATE2AUTOSTATUS | Indicates whether the composite switch state 2 status is Auto | Boolean
1638 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWSTATE3AUTOSTATUS | Indicates whether the composite switch state 3 status is Auto | Boolean
1639 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWSTATE4AUTOSTATUS | Indicates whether the composite switch state 4 status is Auto | Boolean
1640 | DNOM Component | Composite Switch | COMPSW | input | ISCOMPSWMANUALSTATUS | Indicates whether the composite switch status is manual | Boolean
1641 | DNOM Component | Composite Switch | COMPSW | input | JUNCCONT | Pointer to the junction container | String
1642 | DNOM Component | Composite Switch | COMPSW | input | MASTER.CMPSWBMK | Combined state variable which packages up the current state, auto/manual status, and preferred switch state into a single integer value | Integer |  |  |  | COMPSW
1643 | DNOM Component | Composite Switch | COMPSW | input | MASTER.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | COMPSW
1644 | DNOM Component | Composite Switch | COMPSW | input | MASTER.MANOP | Flag indicating device is only manually operated | Boolean |  |  |  | COMPSW
1645 | DNOM Component | Composite Switch | COMPSW | input | MASTER.NOMSTATE | The nominal state of the composite switch | Integer |  |  |  | COMPSW
1646 | DNOM Component | Composite Switch | COMPSW | input | MASTER.NUMGEOM | The number of internal world geometries | Integer |  |  |  | COMPSW
1647 | DNOM Component | Composite Switch | COMPSW | input | MASTER.NUMSWIT | The number of individual switch links | Integer |  |  |  | COMPSW
1648 | DNOM Component | Composite Switch | COMPSW | input | MASTER.PHALT | Non-neutral phases measured on the throwover switch alternate side | Integer |  |  |  | COMPSW
1649 | DNOM Component | Composite Switch | COMPSW | input | MASTER.PHPREF | Non-neutral phases measured on the throwover switch preferred side | Integer |  |  |  | COMPSW
1650 | DNOM Component | Composite Switch | COMPSW | input | MASTER.TMDELAY | Time delay (in seconds) | Float |  |  |  | COMPSW
1651 | DNOM Component | Composite Switch | COMPSW | input | MASTER.TYPE | Device type description | String |  |  |  | COMPSW
1652 | DNOM Component | Composite Switch | COMPSW | input | LIMITCOMPTYPE | Type name, returns "Multi-State Switch". | String
1653 | DNOM Component | Composite Switch | COMPSW | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
1654 | DNOM Component | Composite Switch | COMPSW | input | MANOP | Flag indicating device is only manually operated. True = only manually operated. | Boolean
1655 | DNOM Component | Composite Switch | COMPSW | input | MASTER | Pointer to a master switch (such as master/slave) | String
1656 | DNOM Component | Composite Switch | COMPSW | input | MCSTHROWOVERSTATUS | Flag indicating whether automatic throwover device is currently being automatically operated. Return “On” if automatically operated, otherwise return “Off”. | String
1657 | DNOM Component | Composite Switch | COMPSW | input | NAME | Object name | String |  |  |  | DNMOBJ
1658 | DNOM Component | Composite Switch | COMPSW | input | NOMSTATE | The nominal state of the composite switch. | Integer
1659 | DNOM Component | Composite Switch | COMPSW | input | NUMGEOM | The number of internal world geometries | Integer
1660 | DNOM Component | Composite Switch | COMPSW | input | NUMSWIT | The number of individual switch links. | Integer
1661 | DNOM Component | Composite Switch | COMPSW |  | OSMFEEDERFILTER | If the input feeder matches either the from or to feeder, the string stays the same. Otherwise, it's blanked out. | String
1662 | DNOM Component | Composite Switch | COMPSW | input | OVERLOADCOMPTYPE | Type name, returns "Multi-State Switch". | String
1663 | DNOM Component | Composite Switch | COMPSW | input | OVERLOADCOMPTYPEINDEX | Overload composite switch type index | Integer
1664 | DNOM Component | Composite Switch | COMPSW | input | PENDPERMCOMPSWSET |  | Boolean
1665 | DNOM Component | Composite Switch | COMPSW | input | PENDPERMCOMPSWSTATENAME | New pending permanent state name. | String
1666 | DNOM Component | Composite Switch | COMPSW | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
1667 | DNOM Component | Composite Switch | COMPSW | output | PFCOMPTIME | Latest power flow solution time. | String | DPF | #N/A | #N/A
1668 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.AX | Dynamic array of X coordinates | String |  |  |  | CMBPLS
1669 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.AY | Dynamic array of Y coordinates | String |  |  |  | CMBPLS
1670 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
1671 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
1672 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
1673 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
1674 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1675 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1676 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1677 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1678 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
1679 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
1680 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
1681 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
1682 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.NUMVERT | Number of vertices (line or polygon) | String |  |  |  | CMBPLS
1683 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.ROTATION | Rotation anagle of the placement | String |  | degrees | degrees | CMBPLS
1684 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.SIZE | Size of the object | String |  |  |  | CMBPLS
1685 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.X | X coordinate of the placement | String |  |  |  | CMBPLS
1686 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT.Y | Y coordinate of the placement | String |  |  |  | CMBPLS
1687 | DNOM Component | Composite Switch | COMPSW |  | PFCOMPTIME_TICKS | Latest power flow solution time | String
1688 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
1689 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
1690 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
1691 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
1692 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
1693 | DNOM Component | Composite Switch | COMPSW | input | PHALT | Non-neutral phases measured on the throwover switch alternate side. | Integer
1694 | DNOM Component | Composite Switch | COMPSW | input | PHPREF | Non-neutral phases measured on the throwover switch preferred side. | Integer
1695 | DNOM Component | Composite Switch | COMPSW | input | PLACEMNT | Pointer to the composite switch placement | String
1696 | DNOM Component | Composite Switch | COMPSW | input | SERVCNTR | Pointer to the associated service center | String
1697 | DNOM Component | Composite Switch | COMPSW |  | STATIONNAME | Name of the station the composite switch belongs to | String
1698 | DNOM Component | Composite Switch | COMPSW | input | SWTID | ID of the first switch link. | String
1699 | DNOM Component | Composite Switch | COMPSW | input | SWTNAME | Name of the first switch link. | String
1700 | DNOM Component | Composite Switch | COMPSW | input | TMDELAY | Time delay (in seconds). | Float
1701 | DNOM Component | Composite Switch | COMPSW | input | TOFEEDER | Nominal feeder of to node of the first switch link. | String
1702 | DNOM Component | Composite Switch | COMPSW | input | TOPOEMSSUBNAME | Nominal EMS substation name | String
1703 | DNOM Component | Composite Switch | COMPSW | input | TOPOSUBNAME | Nominal DMS substation name . | String
1704 | DNOM Component | Composite Switch | COMPSW | input | TYPE | Device type description. | String
1705 | DNOM Component | Composite Switch | COMPSW | input | VALIDRETURNAUTOMODE | Flag indicating whether it is valid to return to the automatic operation mode for ESCO throwover switch. True = valid. | Boolean
1706 | DNOM Component | Composite Switch | COMPSW | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
1707 | DNOM Component | Composite Switch | COMPSW | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
1708 | Virtual Object | Composite Switch | COMPSW | input | ISTHIRDPARTY | Flag indicating that the switch is owned by a third-party company | Boolean
1709 | DNOM Component | Composite Switch | COMPSW | output | NORMOPEN | Specifies whether the current switch specific open state classification is Normal Open (normally deenergized). | Boolean
1710 | DNOM Component | Composite Switch | COMPSW | output | TEMPOPEN | Specifies whether the current switch specific open state classification is Temporary Open (temporary deenergized). | Boolean
1711 | DNOM Component | Composite Switch | COMPSW | output | BADOPEN | Specifies whether the current switch specific open state classification is Bad Open (must not be closed at normal conditions). | Boolean
1712 | DNOM Component | Composite Switch | COMPSW | output | SWSPECIFICOPENSTATUS | The switch classification (--. Temporary Open, Bad Open, or Normal Open) | String
1713 | DNOM Component | Composite Switch | COMPSW | input | SWSTATUS | The switch status (for example, A, AB, Preferred, Side 1, On, or Open) | String
1714 | DNOM Component | Composite Switch | COMPSW |  | OPENSTATUS | The switch open status (true for Open) | Boolean
1715 | DNOM Component | Composite Switch | COMPSW |  | COMPSWSTATUS | The switch open status (Open or Closed) | String
1716 | Virtual Object | Container Object | CONTAINER |  | CONTAINERSTATE | Container state (Open, Closed, Partially Open, Open Abnormal, Closed Abnormal, or Partially Open Abnormal) | String
1717 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1718 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.CMPSWBMK | Combined state variable which packages up the current state, auto/manual status, and preferred switch state into a single integer value.. | Integer |  |  |  | COMPSW
1719 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1720 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1721 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | COMPSW
1722 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
1723 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.MANOP | Flag indicating device is only manually operated. True = only manually operated. | Boolean |  |  |  | COMPSW
1724 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.NAME | Name of the object | String |  |  |  | DNMOBJ
1725 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.NOMSTATE | The nominal state of the composite switch. | Integer |  |  |  | COMPSW
1726 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.NUMGEOM | The number of internal world geometries | Integer |  |  |  | COMPSW
1727 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.NUMSWIT | The number of individual switch links. | Integer |  |  |  | COMPSW
1728 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.PHALT | Non-neutral phases measured on the throwover switch alternate side. | Integer |  |  |  | COMPSW
1729 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.PHPREF | Non-neutral phases measured on the throwover switch preferred side. | Integer |  |  |  | COMPSW
1730 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.TMDELAY | Time delay (in seconds). | Float |  |  |  | COMPSW
1731 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW.TYPE | Device type description. | String |  |  |  | COMPSW
1732 | Virtual Object | Control Device | CONTROLDEV |  | CONTROLFAILEDTEXT | Returns description of control failure reason. | String
1733 | Virtual Object | Control Device | CONTROLDEV |  | CONTROLFAILEDTIME | Returns time when device experienced control failure. | String
1734 | Virtual Object | Control Device | CONTROLDEV |  | CONTROLINDIRECTCHECKEDMEASNAME | The name of the measurement that was used for indirect confirmation. Applies to control failure devices only. | String
1735 | Virtual Object | Control Device | CONTROLDEV |  | CTRLTYPE | The type of control the device failed with (Status Control or Analog Setpoint Control). Applies to control failure devices only. | String
1736 | Virtual Object | Control Device | CONTROLDEV |  | ISCONTROLFAILED | Flag indicating if device has experienced control failure. | Boolean
1737 | Virtual Object | Control Device | CONTROLDEV |  | ISCONTROLPROCESSED | Indicates whether the device's control has been processed. Used for the LVM Device Exclusion List display. | Boolean
1738 | Virtual Object | Control Device | CONTROLDEV |  | ISLVMCONTROLDEV | Returns true or false dependent on if the device type is used in LVM | Boolean
1739 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL | input | COMPSW | Pointer to the associated composite switch | String
1740 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL |  | ROTTWO | Rotation angle of the associated composite switch point placement | Integer |  | degrees | degrees
1741 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL |  | SIZETWO | Size of the associated composite switch point object | Integer
1742 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL |  | XTWO | X coordinate of the associated composite switch point placement | Float
1743 | DNOM Component Placement | Composite Switch Label Placement | CSLBPL |  | YTWO | Y coordinate of the associated composite switch point placement | Float
1744 | Global Object | Construction Model | CSTMOD |  | bOverhead | Flag indicating overhead vs. underground construction (True = overhead). | Boolean
1745 | Global Object | Construction Model | CSTMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1746 | Global Object | Construction Model | CSTMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
1747 | Global Object | Construction Model | CSTMOD |  | rVoltage | Associated voltage level or class (15 kV, 25 kV, other). | Float
1748 | Global Object | Construction Model | CSTMOD |  | rXPhaseA | X coordinate for conductor on position 1 in feet/meters. The X coordinates are referenced to the pole (left/right). Usually, position 1 is the leftmost position, which means its X coordinate is smallest among all positions. | Float
1749 | Global Object | Construction Model | CSTMOD |  | rXPhaseB | X coordinate for conductor on position 2 in feet/meters. | Float
1750 | Global Object | Construction Model | CSTMOD |  | rXPhaseC | X coordinate for conductor on position 3 in feet/meters. Usually, position3 is the rightmost position, which means its X coordinate is the biggest among all positions. | Float
1751 | Global Object | Construction Model | CSTMOD |  | rXPhaseN | X coordinate for conductor on position N in feet/meters. Usually, this position N is for neutral conductor. | Float
1752 | Global Object | Construction Model | CSTMOD |  | rYPhaseA | Y coordinate for conductor on position 1 in feet/meters. The Y coordinates are referenced to height above ground. | Float
1753 | Global Object | Construction Model | CSTMOD |  | rYPhaseB | Y coordinate for conductor on position 2 in feet/meters. Usually, position2 is the highest position, which means its Y coordinate is biggest among all positions. | Float
1754 | Global Object | Construction Model | CSTMOD |  | rYPhaseC | Y coordinate for conductor on position 3 in feet/meters. | Float
1755 | Global Object | Construction Model | CSTMOD |  | rYPhaseN | Y coordinate for conductor on position N in feet/meters. | Float
1756 | Global Object | Composite Switch Model | CSWMOD |  | ICSWTYPE | Switch type | String
1757 | Global Object | Composite Switch Model | CSWMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1758 | Global Object | Composite Switch Model | CSWMOD |  | INITMODE | Initial operating mode (true = automatic, false = manual). | Boolean
1759 | Global Object | Composite Switch Model | CSWMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
1760 | Global Object | Composite Switch Model | CSWMOD |  | NUMLINK | Number of switch links. | Integer
1761 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1762 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.CMPSWBMK | Combined state variable which packages up the current state, auto/manual status, and preferred switch state into a single integer value.. | Integer |  |  |  | COMPSW
1763 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1764 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1765 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | COMPSW
1766 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
1767 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.MANOP | Flag indicating device is only manually operated. True = only manually operated. | Boolean |  |  |  | COMPSW
1768 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.NAME | Name of the object | String |  |  |  | DNMOBJ
1769 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.NOMSTATE | The nominal state of the composite switch. | Integer |  |  |  | COMPSW
1770 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.NUMGEOM | The number of internal world geometries | Integer |  |  |  | COMPSW
1771 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.NUMSWIT | The number of individual switch links. | Integer |  |  |  | COMPSW
1772 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.PHALT | Non-neutral phases measured on the throwover switch alternate side. | Integer |  |  |  | COMPSW
1773 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.PHPREF | Non-neutral phases measured on the throwover switch preferred side. | Integer |  |  |  | COMPSW
1774 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.TMDELAY | Time delay (in seconds). | Float |  |  |  | COMPSW
1775 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW.TYPE | Device type description. | String |  |  |  | COMPSW
1776 | Global Object | Composite Switch Model | CSWMOD |  | NUMSTATE | The number of different state the switch can be. | Integer
1777 | Global Object | Composite Switch Model | CSWMOD |  | RECONFIG | Reconfigurable flag for geoschematics (true = reconfigurable). | Boolean
1778 | Global Object | Composite Switch Model | CSWMOD |  | STNAME | Array of state names | String
1779 | Global Object | Composite Switch Model | CSWMOD |  | STSCADAVAL | Array of SCADA state values associated with the switch states | String
1780 | Global Object | Composite Switch Model | CSWMOD |  | STVALUE | Array of valid switch states | String
1781 | Global Object | Composite Switch Model | CSWMOD |  | SWTYPE | Enumerated composite switch model type, 1 = Throwover, 2 = ESCO Throwover, 3 = RAL, 4 = GRAL, 5 = Regulator Bypass, 6 = UG Multi Switch, 7 = Grounding Switch, 8 = RAG, 9 = RAC | Integer
1782 | Global Object | Composite Switch Model | CSWMOD |  |  | Name of the bitmap scheme (default is blank). | String
1783 | DNOM Component Placement | Composite Switch Placement | CSWPLE | input | COMPSW | Pointer to the associated composite switch | String
1784 | DNOM Component | Cut | CUT | input | ABNDATETIME | Date and time when cut is placed or time of last status change. | String
1785 | DNOM Component | Cut | CUT |  | ABNDATETIME_TICKS | The device's last update time | String
1786 | DNOM Component | Cut | CUT | output | ABNDATETIMEUPDATE | Time of update | Struct TM
1787 | DNOM Component | Cut | CUT | output | ABNDATETIMEUPDATE_TICKS | The cut's last update time | Struct TM
1788 | DNOM Component | Cut | CUT | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
1789 | DNOM Component | Cut | CUT | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1790 | DNOM Component | Cut | CUT | input | CUTSTAT | Current open status, the value is “True” or “False”. True = open, False = closed. | Boolean
1791 | DNOM Component | Cut | CUT | input | CUTSTATSTR | Current open status, the value is Open" or "Closed"" | String
1792 | DNOM Component | Cut | CUT | input | CUTTYPE | Cut type (terminal, closed line, open line) | String
1793 | DNOM Component | Cut | CUT | input | CUTTYPENAME | The type of the cut. | String
1794 | DNOM Component | Cut | CUT | input | CUTISCONTROLLABLE | Specefies whether the cut status can be changed by the user (for example, False for a Loss of Voltage cut). | Boolean
1795 | DNOM Component | Cut | CUT | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
1796 | DNOM Component | Cut | CUT | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1797 | DNOM Component | Cut | CUT | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1798 | DNOM Component | Cut | CUT | input | FRLENGTH | Percentage of distance from cut to the from node of the branch where the cut is placed to the length of the branch. | Float
1799 | DNOM Component | Cut | CUT | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
1800 | DNOM Component | Cut | CUT | input | GEOMETRY | Geometry for the cut | String
1801 | DNOM Component | Cut | CUT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1802 | DNOM Component | Cut | CUT | output | IFROMA | Phase A current flow (Amps). | Float | DPF | Amps | Amps
1803 | DNOM Component | Cut | CUT | output | IFROMB | Phase B current flow (Amps). | Float | DPF | Amps | Amps
1804 | DNOM Component | Cut | CUT | output | IFROMC | Phase C current flow (Amps). | Float | DPF | Amps | Amps
1805 | DNOM Component | Cut | CUT | output | IFROMN | Phase N current flow (Amps). | Float | DPF | Amps | Amps
1806 | DNOM Component | Cut | CUT | input | ISORPHAN | Flag indicating that the cut is an orphan | Boolean
1807 | DNOM Component | Cut | CUT |  | LBLPOSITION | Label position | String
1808 | DNOM Component | Cut | CUT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
1809 | DNOM Component | Cut | CUT | input | LOCATIONSNAPPED | Flag indicating that the cut location was "snapped" to the target branch | Boolean
1810 | DNOM Component | Cut | CUT | input | NAME | Object name | String |  |  |  | DNMOBJ
1811 | DNOM Component | Cut | CUT | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1812 | DNOM Component | Cut | CUT | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1813 | DNOM Component | Cut | CUT | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
1814 | DNOM Component | Cut | CUT | input | OPCOMMNT | Operator inserted comment. | String
1815 | DNOM Component | Cut | CUT | input | ORGCMPID | ID of original component where the cut is placed. | String
1816 | DNOM Component | Cut | CUT | input | ORGCPTYID | Type of original component where the cut is placed. | Integer
1817 | DNOM Component | Cut | CUT |  | POSITIONTXT | Position specific comments | String
1818 | DNOM Component | Cut | CUT | output | PQFROMA | Phase A power flow (kVA). | Float | DPF | kVA | kVA
1819 | DNOM Component | Cut | CUT | output | PQFROMB | Phase B power flow (kVA). | Float | DPF | kVA | kVA
1820 | DNOM Component | Cut | CUT | output | PQFROMC | Phase C power flow (kVA). | Float | DPF | kVA | kVA
1821 | DNOM Component | Cut | CUT | output | PQFROMN | Phase N power flow (kVA). | Float | DPF | kVA | kVA
1822 | DNOM Component | Cut | CUT | input | REALCUT | Flag indicating the cut is real (on the UI, not needed for topology reasons) | Boolean
1823 | DNOM Component | Cut | CUT | input | REMCMPID | Removed component ID | String
1824 | DNOM Component | Cut | CUT | output | SWIDPREDICTCUT | Switch ID for the predicted cut (Loss of Voltage cut) | String
1825 | DNOM Component | Cut | CUT | input | TEMPMODDESCRIPT | Operator inserted comment. | String
1826 | DNOM Component | Cut | CUT | input | TEMPMODPERMITAREA | Associated permission area name. | String
1827 | DNOM Component | Cut | CUT |  | WASSNAPPED | A flag indicating that the cut position was updated | Boolean
1828 | DNOM Component | Cut | CUT | input | XCOORD | Cut x coordinate | Float
1829 | DNOM Component | Cut | CUT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
1830 | DNOM Component | Cut | CUT | input | YCOORD | Cut y coordinate | Float
1831 | DNOM Component | Cut | CUT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
1832 | DNOM Component | Cut Output | CUTOUT |  | IFROMA | Phase A current flow | Float |  | Amps | Amps
1833 | DNOM Component | Cut Output | CUTOUT |  | IFROMB | Phase B current flow | Float |  | Amps | Amps
1834 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1835 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
1836 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1837 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1838 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.FRLENGTH | Percentage of distance from cut to the from node of the branch where the cut is placed to the length of the branch. | Float |  |  |  | CUT
1839 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
1840 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.GEOMETRY | Geometry for the cut | String |  |  |  | CUT
1841 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
1842 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.ISORPHAN | Flag indicating that the cut is an orphan | Boolean |  |  |  | CUT
1843 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.LOCATIONSNAPPED | Flag indicating that the cut location was "snapped" to the target branch | Boolean |  |  |  | CUT
1844 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.NAME | Name of the object | String |  |  |  | DNMOBJ
1845 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1846 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1847 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
1848 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.OPCOMMNT | Operator inserted comment | String |  |  |  | CUT
1849 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.ORGCMPID | ID of original component where the cut is placed. | String |  |  |  | CUT
1850 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.POSITIONTXT | Position specific comments | String |  |  |  | CUT
1851 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.REALCUT | Flag indicating the cut is real (on the UI, not needed for topology reasons) | Boolean |  |  |  | CUT
1852 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.REMCMPID | Removed component ID | String |  |  |  | CUT
1853 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.XCOORD | Cut x coordinate | Float |  |  |  | CUT
1854 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut.YCOORD | Cut y coordinate | Float |  |  |  | CUT
1855 | DNOM Component | Cut Output | CUTOUT |  | IFROMC | Phase C current flow | Float |  | Amps | Amps
1856 | DNOM Component | Cut Output | CUTOUT |  | IFROMN | Phase N current flow | Float |  | Amps | Amps
1857 | DNOM Component | Cut Output | CUTOUT |  | PQFROMA | Phase A power flow (kVA). | Float
1858 | DNOM Component | Cut Output | CUTOUT |  | PQFROMB | Phase B power flow (kVA). | Float
1859 | DNOM Component | Cut Output | CUTOUT |  | PQFROMC | Phase C power flow (kVA). | Float
1860 | DNOM Component | Cut Output | CUTOUT |  | PQFROMN | Phase N power flow (kVA). | Float
1861 | DNOM Component Placement | Cut Placement | CUTPLE | input | pCut | Pointer to the associated cut | String
1862 | DNOM Component | Duct Bank | DBANK | input | ADDRESS.NOAPPSTRING | Address. | String
1863 | Global Object | Day Type | DAYTYP |  | ACALDATE | Abnormal days (month/day/year format). | String
1864 | Global Object | Day Type | DAYTYP |  | AWEEKDAY | Days of the week: (0 = Sunday, 1 = Monday, 2 = Tuesday, 3 = Wednesday, 4 = Thursday, 5 = Friday, and 6 = Saturday). | Integer
1865 | Global Object | Day Type | DAYTYP |  | DESCRIPT | Description of day type. | String
1866 | Global Object | Day Type | DAYTYP | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1867 | Global Object | Day Type | DAYTYP | input | NAME | Object name | String |  |  |  | DNMOBJ
1868 | Global Object | Day Type | DAYTYP |  | NUMCALD | The number of abnormal load days. | Integer
1869 | Global Object | Day Type | DAYTYP |  | NUMWEEKD | The number of days of the week. | Integer
1870 | DNOM Component | Duct Bank | DBANK | input | ALTERNATENAME | Alternate Name. | String
1871 | DNOM Component | Duct Bank | DBANK | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
1872 | DNOM Component | Duct Bank | DBANK | input | AREAIND | Integer index into station permission area list | Integer |  |  |  | DNMOBJ
1873 | DNOM Component | Duct Bank | DBANK | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
1874 | DNOM Component | Duct Bank | DBANK | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
1875 | DNOM Component | Duct Bank | DBANK | input | DNOMTABNAME | The DNOM table name. | String
1876 | DNOM Component | Duct Bank | DBANK | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1877 | DNOM Component | Duct Bank | DBANK | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1878 | DNOM Component | Duct Bank | DBANK | input | ENUMTYPE | Duct bank type enumeration. 0 = standard, 1 = others. | Integer
1879 | DNOM Component | Duct Bank | DBANK | input | ID | Object unique ID | String |  |  |  | DNMOBJ
1880 | DNOM Component | Duct Bank | DBANK | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
1881 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
1882 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1883 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
1884 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1885 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1886 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.ENUMTYPE | Duct bank type enumeration. 0 = standard, 1 = others. | Integer |  |  |  | DBANK
1887 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
1888 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.ID | ID of the object | String |  |  |  | DNMOBJ
1889 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.NAME | Object name | String |  |  |  | DNMOBJ
1890 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1891 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK.NUMLINE | The number of lines contained in the duct bank.. | Integer |  |  |  | DBANK
1892 | DNOM Component | Duct Bank | DBANK | input | NAME | Object name | String |  |  |  | DNMOBJ
1893 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
1894 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1895 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
1896 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1897 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1898 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.ENUMTYPE | Duct bank type enumeration. 0 = standard, 1 = others. | Integer |  |  |  | DBANK
1899 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
1900 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.ID | ID of the object | String |  |  |  | DNMOBJ
1901 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.NAME | Object name | String |  |  |  | DNMOBJ
1902 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1903 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK.NUMLINE | The number of lines contained in the duct bank.. | Integer |  |  |  | DBANK
1904 | DNOM Component | Duct Bank | DBANK | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
1905 | DNOM Component | Duct Bank | DBANK | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
1906 | DNOM Component | Duct Bank | DBANK | input | NUMLINE | The number of lines contained in the duct bank.. | Integer
1907 | DNOM Component | Distribution Transformer | DISTTF | input | ADDRESS.NOAPPSTR | Transformer address. | String
1908 | DNOM Component | Duct Bank | DBANK | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
1909 | DNOM Component | Duct Bank | DBANK | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
1910 | DNOM Component Placement | Duct Bank Label Placement | DBLBPL | input | DUCTBANK | Pointer to the associated duct bank | String
1911 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1912 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1913 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1914 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
1915 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.NAME | Name of the object | String |  |  |  | DNMOBJ
1916 | DNOM Component | Distribution Transformer | DISTTF | input | BANK.NUMTF | The number of single-phase transformers in the bank. | Integer |  |  |  | TFBNK
1917 | DNOM Component Placement | Duct Bank Placement | DBPLE | input | DUCTBANK | Pointer to the associated duct bank | String
1918 | Virtual Object | De-Energized | DEENRG | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
1919 | Virtual Object | De-Energized | DEENRG | input | TNDEENERGIZED | If the device is de-energized. | Boolean
1920 | DNOM Component | DER Measurement | DERMEAS |  | DATASOURCE | Measurement data source (1 = SCADA and 2 = 2030.5 Gateway) | Integer
1921 | DNOM Component | DER Measurement | DERMEAS |  | DERDEVICETYPE | Energy resource device type. | String
1922 | DNOM Component | DER Measurement | DERMEAS |  | DERPROGRAMENROLL | Enrolled Programs of the energy resource. | String
1923 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASDATASOURCE | Measurement data source (SCADA or 2030.5 Gateway). | String
1924 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASLASTUPDATETIME | Measurement last update time. | DateTime
1925 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASPHASE | Measurement phasing. | String
1926 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASQUALITY | Measurement quality. The supported measurement quality bits are: Valid = 1 ManuallyEdited = 2 EstimatedWithReferenceDay = 4 EstimatedWithLinearInterpolation = 8 Questionable = 16 Derived = 32 Projected = 64 The measurement quality value is set to Suspect if the Questinable bit is set. | Integer
1927 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASREADINGTIME | Measurement reading time. | DateTime
1928 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASTYPE | Measurement type (for example, kW). | String
1929 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASVALUE | DER analog measurement value | Float
1930 | DNOM Component | DER Measurement | DERMEAS |  | DERMEASVALUE | Measurement value. | String
1931 | DNOM Component | DER Measurement | DERMEAS |  | ENERGYRES | Pointer to the associated energy resource | String
1932 | DNOM Component | DER Measurement | DERMEAS |  | MEASQUALITY | Measurement quality | Integer
1933 | DNOM Component | DER Measurement | DERMEAS |  | MEASTYPE | Enumeration of the measurement type (for example, 50 = MeasVolts, 501 = kW) Where, measurements 1-300 are from DMS and SCADA, and measurements 501-508 are from 2030.5 Gateway: 501 = KW 502 = KVAR 503 = KV 504 = FREQ 505 = OPSTATE 506 = CS 507 = AS 508 = SOC | Integer
1934 | DNOM Component | DER Measurement | DERMEAS |  | MEASUREMENT | Pointer to the associated measurement | String
1935 | DNOM Component | DER Measurement | DERMEAS |  | PHASING | Measurement phases | String
1936 | DNOM Component | Distribution System | DISTRIBUTIONSYSTEM |  | _KEY | The unique identifier to represent a device | String
1937 | DNOM Component | Distribution Transformer | DISTTF | input | ALTID | Returns the ADDRESS | String
1938 | DNOM Component | Distribution Transformer | DISTTF | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1939 | DNOM Component | Distribution Transformer | DISTTF | input | BANK | Pointer to the associated tansformer bank | String
1940 | DNOM Component | Distribution Transformer | DISTTF | input | BOUNDARY | The boundary flag | Boolean
1941 | DNOM Component | Distribution Transformer | DISTTF | input | COMPCONFIRMCLOSED | Flag indicating if the transformer is confirmed close (used in OMS) | Boolean
1942 | DNOM Component | Distribution Transformer | DISTTF | input | COMPPREDICTEDOUT | Flag indicating if the transformer is predicted outage (used in OMS) | Boolean
1943 | DNOM Component | Distribution Transformer | DISTTF | input | CREWDISPATCHED | Indicates whether a crew is dispatched | Boolean
1944 | DNOM Component | Distribution Transformer | DISTTF | input | CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean
1945 | DNOM Component | Distribution Transformer | DISTTF | input | CUSTMERA | The number of phase A only connected customers | Integer
1946 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
1947 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
1948 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
1949 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.CURROPEN | Current open status | Boolean |  |  |  | SWT
1950 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
1951 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
1952 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
1953 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
1954 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
1955 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
1956 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.NAME | Name of the object | String |  |  |  | DNMOBJ
1957 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1958 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
1959 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.NOPEN | Normally Open | Boolean |  |  |  | SWT
1960 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
1961 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.REMOTE | Remote | Boolean |  |  |  | SWT
1962 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
1963 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
1964 | DNOM Component | Distribution Transformer | DISTTF | input | CUSTMERB | The number of phase B only connected customers | Integer
1965 | DNOM Component | Distribution Transformer | DISTTF | input | CUSTMERC | The number of phase C only connected customers | Integer
1966 | DNOM Component | Distribution Transformer | DISTTF | input | CUSTOMER | The number of connected customers | Integer
1967 | DNOM Component | Distribution Transformer | DISTTF | input | DISTTFCRITICAL | Flag indicating if the transformer connected to critical customer | Boolean
1968 | DNOM Component | Distribution Transformer | DISTTF | input | DISTTFISOVERHEAD | Flag indicating if the distribution transformer is overhead transformer | Boolean
1969 | DNOM Component | Distribution Transformer | DISTTF |  | DISTTFNUMCRITLOADS | Number of critical loads associated with the transformer | Integer
1970 | DNOM Component | Distribution Transformer | DISTTF | input | DISTTFROTATION | Placement rotation | Float
1971 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.BANKCODE | Transformer bank code | String |  |  |  | TFMOD
1972 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.CNSTTYPE | Configuration type (overhead, underground, padmount, others) | Integer |  |  |  | TFMOD
1973 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.CYCREACT | CYC matrix elements - reactive portion | Integer |  |  |  | TFMOD
1974 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.CYCREAL | CYC matrix elements - real portion | Integer |  |  |  | TFMOD
1975 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.DMSTYPE | Enumerated transformer type. The following values are used: 1 = Secondary transformer, 2 = Voltage regulator, 3 = Power transformer, 4 = Auto-transformer, 5 = Step Up/Down transformer, 6 = Zigzag transformer. | Integer |  |  |  | TFMOD
1976 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.EXCITEPF | Magnetization power factor (optional if percent excitation current is provided) | Float |  |  |  | TFMOD
1977 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.EXCTEAMP | Average percent excitation current (optional if the magnetizing power factor is provided) | Float |  |  |  | TFMOD
1978 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.ID | Object unique ID | String |  |  |  | DNMOBJ
1979 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | TFMOD
1980 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMITEVENTSEC | A flag indicating secondary operational limit event | Boolean |  |  |  | TFMOD
1981 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMITEVENTTER | A flag indicating tertiary operational limit event | Boolean |  |  |  | TFMOD
1982 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | TFMOD
1983 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMNAMES | The limits name in secondary winding | String |  |  |  | TFMOD
1984 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMNAMET | The limits name in tertiary winding | String |  |  |  | TFMOD
1985 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMSEASSEC | Season of the operational limit in secondary winding | String |  |  |  | TFMOD
1986 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMUNIT | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | Integer |  |  |  | TFMOD
1987 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMUNITS | The limits unit in secondary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer |  |  |  | TFMOD
1988 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMUNITT | The limits unit in tertiary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer |  |  |  | TFMOD
1989 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMVALS | The limits value in secondary winding | Float |  |  |  | TFMOD
1990 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMVALT | The limits value in tertiary winding | Float |  |  |  | TFMOD
1991 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.LIMVALUE | Value of the operational limit | Float |  | Amps, kVA, or MVA | Amps, kVA, or MVA | TFMOD
1992 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.MAGLOSS | Transformer nominal core loss | Float |  |  |  | TFMOD
1993 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.MAGYZERO | Zero sequence magnetization susceptance (optional) | Complex |  |  |  | TFMOD
1994 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NAME | Associated transformer model name. | String
1995 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMCYCEL | Number of elements | Integer |  |  |  | TFMOD
1996 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMCYCRW | Number of rows | Integer |  |  |  | TFMOD
1997 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMLIMIT | The number of operation limits | Integer |  |  |  | TFMOD
1998 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMLIMSS | The number of the operation limits in secondary winding | Integer |  |  |  | TFMOD
1999 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMLIMST | The number of the limits in tertiary winding | Integer |  |  |  | TFMOD
2000 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.NUMRGLIM | The number of regulator step limits | Integer |  |  |  | TFMOD
2001 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.PRIMGRDZ | Primary grounding impedance | Float |  |  |  | TFMOD
2002 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.PRIMZ | Primary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
2003 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.REGLIMIT | Regulator step limit | Float |  | Amps | Amps | TFMOD
2004 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.REGLIMITEVENT | A flag indicating regulation limit event | Boolean |  |  |  | TFMOD
2005 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.REGRTGIV | Flag indicating whether the provided rating is the regulating VA | Boolean |  |  |  | TFMOD
2006 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.REGUNITS | Enumerated flag indicating the voltage units that should be used for transformers with voltage regulation capability. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer |  |  |  | TFMOD
2007 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.RGLIMSTP | The regulation step in percent voltage such as 5.0% or 10.0% | Float |  |  |  | TFMOD
2008 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.SECGRDZ | Secondary grounding impedance | Float |  |  |  | TFMOD
2009 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.SECZ | Secondary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
2010 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.SRATING | Transformer rating | Float |  | kVA or MVA | kVA or MVA | TFMOD
2011 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.SRATINGTER | Tertiary winding Rated capacity in kVA or MVA depending on the units flag | Float |  | kVA or MVA | kVA or MVA | TFMOD
2012 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.SUNITS | A flag indicating units used for displaying transformer rating (true - kVA, false - MVA) | Boolean |  |  |  | TFMOD
2013 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.TERTGRDZ | Tertiary grounding impedance | Float |  |  |  | TFMOD
2014 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.TERTZ | Tertiary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
2015 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.TFTYPE | Enumerated transformer type for linking the transformer model to a transformer type that is needed by the power flow function | Integer |  |  |  | TFMOD
2016 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL.TFTYPEINDEX | Transformer type index, used for validation purposes | Integer |  |  |  | TFMOD
2017 | DNOM Component | Distribution Transformer | DISTTF | output | DISTTFVOLTDROPEXCEEDED | Flag if the voltage drop of the distribution transformer exceed limit | Integer
2018 | DNOM Component | Distribution Transformer | DISTTF | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
2019 | DNOM Component | Distribution Transformer | DISTTF | input | DNOMTABNAME | DNOM table name | String
2020 | DNOM Component | Distribution Transformer | DISTTF | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2021 | DNOM Component | Distribution Transformer | DISTTF | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2022 | DNOM Component | Distribution Transformer | DISTTF | input | DSECGRND | Grounded phase winding for a transformer | Integer
2023 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAIN | Flag indicating if the transformer is on feeder main. | Boolean
2024 | DNOM Component | Distribution Transformer | DISTTF | input | FEEDERMAINSWTDEVICE | Pointer to the upstream feeder main switching device | String
2025 | DNOM Component | Distribution Transformer | DISTTF | input | FROMEMS | A flag indicating that the distribution transformer is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
2026 | DNOM Component | Distribution Transformer | DISTTF | input | GROUNDPR | Primary grounded flag | Boolean
2027 | DNOM Component | Distribution Transformer | DISTTF | input | GROUNDSC | Secondary grounded flag | Boolean
2028 | DNOM Component | Distribution Transformer | DISTTF | input | ID | Object unique ID | String |  |  |  | DNMOBJ
2029 | DNOM Component | Distribution Transformer | DISTTF |  | LIMFLAGS | Number of limit violations | Integer
2030 | DNOM Component | Distribution Transformer | DISTTF | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
2031 | DNOM Component | Distribution Transformer | DISTTF | input | MODEL | Pointer to the associated transformer model | String
2032 | DNOM Component | Distribution Transformer | DISTTF | input | NAME | Object name | String |  |  |  | DNMOBJ
2033 | DNOM Component | Distribution Transformer | DISTTF | input | SERVCNTR.NAME | Service center. | String
2034 | DNOM Component | Distribution Transformer | DISTTF | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2035 | DNOM Component | Distribution Transformer | DISTTF | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2036 | DNOM Component | Distribution Transformer | DISTTF | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2037 | DNOM Component | Distribution Transformer | DISTTF | output | PREDICTEDPHASES | Predicted phases | String
2038 | DNOM Component | Distribution Transformer | DISTTF | output | PREDICTIONBLOCKED | Indicates if the prediction is blocked | Boolean
2039 | DNOM Component | Distribution Transformer | DISTTF | output | PREDICTIONBLOCKEDPHASES | Indicates the phases for which the prediction is blocked | String
2040 | DNOM Component | Distribution Transformer | DISTTF | output | PREDICTIONBLOCKINGPERPHASE | Indicates if the prediction is blocked for phases | Boolean
2041 | DNOM Component | Distribution Transformer | DISTTF | input | PRIMGNDR | Primary grounding branch resistance | Float
2042 | DNOM Component | Distribution Transformer | DISTTF | input | PRIMGNDX | Primary grounding branch reactance | Float
2043 | DNOM Component | Distribution Transformer | DISTTF |  | PRIMOPERVOLT | Primary operating voltage (in kV l-g) | Integer
2044 | DNOM Component | Distribution Transformer | DISTTF | input | PRIMWIND | Primary winding connection type | Integer
2045 | DNOM Component | Distribution Transformer | DISTTF |  | ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer
2046 | DNOM Component | Distribution Transformer | DISTTF | input | SEC1GNDR | Secondary grounding branch resistance | Float
2047 | DNOM Component | Distribution Transformer | DISTTF | input | SEC1GNDX | Secondary grounding branch reactance | Float
2048 | DNOM Component | Distribution Transformer | DISTTF | input | SECWIND | Secondary winding connection type | Integer
2049 | DNOM Component | Distribution Transformer | DISTTF |  | SERVICEPOINTID | ID of the transformer's service point | String
2050 | DNOM Component | Distribution Transformer | DISTTF | input | TFBANKID | Transformer bank ID | String
2051 | DNOM Component | Distribution Transformer | DISTTF | input | TFLOADED | Connected load flag | Boolean
2052 | DNOM Component | Distribution Transformer | DISTTF | input | TFMASK | All booleans will be combined into a single mask | Integer
2053 | DNOM Component | Distribution Transformer | DISTTF | input | VOLTPR | Primary Rated voltage (kV line to ground). | Float |  | kV | kV
2054 | DNOM Component | Distribution Transformer | DISTTF | input | VOLTSC | Secondary Rated voltage (kV line to ground). | Float |  | kV | kV
2055 | DNOM Component | Distribution Transformer | DISTTF | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
2056 | DNOM Component | Distribution Transformer | DISTTF | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
2057 | DNOM Component | Distribution Transformer | DISTTF | input | DISTTFHASDERCONNECTED | Specifies whether the distribution transformer has an energy resource connected to the secondary side. | Boolean
2058 | DNOM Component | Distribution Transformer | DISTTF | input | DISTTFENERGYRES | Names of energy resources that are connected to the secondary side of the transformer. | String
2059 | Virtual Object | DMS Branch Component | DMSBRANCH | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
2060 | Virtual Object | DMS Branch Component | DMSBRANCH | output | AVGKVAR3PH | Average three-phase power (kVAR) for nodes 1 and 2. A negative value indicates flow is towards the source. | Float
2061 | Virtual Object | DMS Branch Component | DMSBRANCH | output | AVGKW3PH | Average three-phase power (kW) for nodes 1 and 2. | Float
2062 | Virtual Object | DMS Branch Component | DMSBRANCH | output | AVGVOLTA | Average phase A voltage (configurable voltage base) for nodes 1 and 2. | Float
2063 | Virtual Object | DMS Branch Component | DMSBRANCH | output | AVGVOLTB | Average phase B voltage (configurable voltage base) for nodes 1 and 2. | Float
2064 | Virtual Object | DMS Branch Component | DMSBRANCH | output | AVGVOLTC | Average phase C voltage (configurable voltage base) for nodes 1 and 2. | Float
2065 | Virtual Object | DMS Branch Component | DMSBRANCH | output | BRANCHDEENERGIZED | All deenergized phases of specified branch and associated external branches | String
2066 | Virtual Object | DMS Branch Component | DMSBRANCH | input | BRANCHENERGIZED | Phases currently energized. | String
2067 | Virtual Object | DMS Branch Component | DMSBRANCH | input | BRANCHOPERKV | Voltage level (line to neutral).Not used anymore. | Float
2068 | Virtual Object | DMS Branch Component | DMSBRANCH | output | BRANCHPHASEAENERGIZED | Is phase A of specified branch energized or not. | Boolean
2069 | Virtual Object | DMS Branch Component | DMSBRANCH | output | BRANCHPHASEBENERGIZED | Is phase B of specified branch energized or not. | Boolean
2070 | Virtual Object | DMS Branch Component | DMSBRANCH | output | BRANCHPHASECENERGIZED | Is phase C of specified branch energized or not. | Boolean
2071 | Virtual Object | DMS Branch Component | DMSBRANCH | input | BRANCHREMTOP | Phases that are removed from topology due to multiple source energization. | String
2072 | Virtual Object | DMS Branch Component | DMSBRANCH | input | LIMITCOMPTYPE | Type name of the component. Returns one of the following: Not Identified, Bus, Multi-State Switch, Line, Load, Switch, Fuse, Recloser, Breaker, Sectionalizer, Jumper, NetworkProtector, Switch, Capacitor, Transformer, Reactor, Cut, Jumper, Generator, Energy Resource, Regulator, LTC, Auto Transformer, Transformer, Temp. Fault, Temp. Ground, Temp. Plan Out, Temp. Energized. | String
2073 | Virtual Object | DMS Branch Component | DMSBRANCH | output | LOSSKVAR | Loss imaginary part in KVAR | Float
2074 | Virtual Object | DMS Branch Component | DMSBRANCH | output | LOSSKW | Loss real part in KW | Float
2075 | Virtual Object | DMS Branch Component | DMSBRANCH | output | LOSSVAR | Loss imaginary part in VAR | Float
2076 | Virtual Object | DMS Branch Component | DMSBRANCH | output | LOSSW | Loss real part in W | Float
2077 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTAVGLOADA | Phase A percent loading against level 1 limit. | Float
2078 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTAVGLOADB | Phase B percent loading against level 1 limit. | Float
2079 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTAVGLOADC | Phase C percent loading against level 1 limit. | Float
2080 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTLOADA | Phase A percent loading against level 1 limit. | Float
2081 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTLOADB | Phase B percent loading against level 1 limit. | Float
2082 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PERCENTLOADC | Phase C percent loading against level 1 limit. | Float
2083 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PHASEAANGLEDIFF | The voltage angle difference of phase A between a switch or a jumper (Degree). | Float
2084 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PHASEBANGLEDIFF | The voltage angle difference of phase B between a switch or a jumper (Degree). | Float
2085 | Virtual Object | DMS Branch Component | DMSBRANCH | output | PHASECANGLEDIFF | The voltage angle difference of phase C between a switch or a jumper (Degree). | Float
2086 | Virtual Object | DMS Branch Component | DMSBRANCH | input | STRUCTUREID | ID of a structure (e.g., pole) that is associated with the device | String
2087 | Virtual Object | DMS Branch Component | DMSBRANCH | input | TFPHASING | Source side phasing. | String
2088 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEAMPA | Side 2 phase A amp flow (amps magnitude and angle). | Float
2089 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEAMPB | Side 2 phase B amp flow (amps magnitude and angle). | Float
2090 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEAMPC | Side 2 phase C amp flow (amps magnitude and angle). | Float
2091 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEAMPN | Side 2 phase N amp flow (amps magnitude and angle). | Float
2092 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEAMPNEUT | Vector Summation of the Side 2 phase A,B,C current flows (magnitude and angle) | Float
2093 | Virtual Object | DMS Branch Component | DMSBRANCH |  | TONODEKVA3PH | Side 2 total apparent power flow (kVA) | Float |  | kVA | kVA
2094 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEKVAR3PH | Side 2 total reactive power flow (kVAR). | Float |  | kVAR | kVAR
2095 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEKW3PH | Side 2 total real power flow (kW). | Float |  | kW | kW
2096 | Virtual Object | DMS Branch Component | DMSBRANCH | output | TONODEPF3PH | Side 2 power factor. | Float
2097 | Virtual Object | DMS Branch Component | DMSBRANCH |  | TOPODEENERGIZED | Phases deenergized | String
2098 | Virtual Object | DMS Branch Component | DMSBRANCH | input | TOPODELETED | Flag indicating whether the component has been removed | Boolean
2099 | Virtual Object | DMS Branch Component | DMSBRANCH |  | UPSTREAMINFO | Upstream info (binary number) | String
2100 | Virtual Object | DMS Branch Component | DMSBRANCH |  | UPSTREAMNODE | ID of the upstream node | String
2101 | Virtual Object | DMS Branch Component | DMSBRANCH |  | UPSTREAMNODEA | ID of the upstream node of phase A | String
2102 | Virtual Object | DMS Branch Component | DMSBRANCH |  | UPSTREAMNODEB | ID of the upstream node of phase B | String
2103 | Virtual Object | DMS Branch Component | DMSBRANCH |  | UPSTREAMNODEC | ID of the upstream node of phase C | String
2104 | DNOM Component | DMS Component | DMSCOMP | output | CURROPEN | Specifies whether the current component's state is Open, Disconnected, or Off (deenergized) | Boolean
2105 | DNOM Component | DMS Component | DMSCOMP | output | COMPPARENTTF | The name of the energizing power transformer for a component. | String | LVM | #N/A | #N/A
2106 | DNOM Component | DMS Component | DMSCOMP | input | HOLDFAULTINDACTIVE | Specifies whether the fault indication is currently held for the breaker | Boolean
2107 | DNOM Component | DMS Component | DMSCOMP | input | HOLDFAULTINDCAPABLE | Specifies whether the breaker is capable of holding fault indication | Boolean
2108 | DNOM Component | DMS Component | DMSCOMP | output | VVCSTATGROUP | The name of substation group. | String | LVM | #N/A | #N/A
2109 | Global Object | DMS Component | DMSCOMP | input | DEVICESCHEDULETYPE | Device schedule type, static or dynamic | String
2110 | Global Object | DMS Component | DMSCOMP | input | DEVICESCHEDULEVALUE | Scheduled load value. | String
2111 | Global Object | DMS Component | DMSCOMP | input | FDRHASTEMPDEVICE | Specifies whether the feeder has a temporary device (for example, cut or jumper) | Boolean
2112 | Virtual Object | DMS Component | DMSCOMP | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
2113 | Virtual Object | DMS Component | DMSCOMP |  | BRANCHFLOWOVERLIMITPERCENT | Percent of flow over the corresponding limit level | Float
2114 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWACTVALUE | Flow value | String
2115 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWCAPAMARGINPERCENT | The percentage of the flow to the level 1 limit value. | Float
2116 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWCAPAVALUE | The level 1 limit value | String
2117 | Virtual Object | DMS Component | DMSCOMP | input | COMPFLOWDERATEDLIMITVALUE | Component flow derated limit value | String
2118 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWLIMITNAME | The highest violated flow limit name. | String
2119 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWLIMITPERCENT | The percentage of the largest flow to the highest violated limit value. | Float
2120 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWLIMITVALUE | The highest violated flow limit value. | String
2121 | Virtual Object | DMS Component | DMSCOMP |  | COMPFLOWLIMITVALUEAMPS | Flow limit value in Amps | Float |  | Amps
2122 | Virtual Object | DMS Component | DMSCOMP | output | COMPFLOWVALUE | Flow value. | String
2123 | Virtual Object | DMS Component | DMSCOMP |  | COMPFLOWVALUEAMPS | Flow value in Amps | Float |  | Amps
2124 | Virtual Object | DMS Component | DMSCOMP | output | COMPHASCAPAMARGINVIOLATION | Flag indicating whether the component has capacity margin violation. | Boolean
2125 | Virtual Object | DMS Component | DMSCOMP | output | COMPHASFLOWVIOLATION | Flag indicating whether the component has flow violation. Return TRUE or FALSE. | Boolean
2126 | Virtual Object | DMS Component | DMSCOMP | input | COMPHASMULTTAG | Flag indicating whether the component has multiple tags. | Boolean
2127 | Virtual Object | DMS Component | DMSCOMP | output | COMPHASRESCAPIMPACT | Returns true if component has non-zero derating value. | Boolean
2128 | Virtual Object | DMS Component | DMSCOMP | input | COMPHASTAG | Component tag field. | Integer
2129 | Virtual Object | DMS Component | DMSCOMP | input | COMPISINSIDESTATION | Flag indicating whether the component is inside station. | Boolean
2130 | Virtual Object | DMS Component | DMSCOMP | input | COMPPHASEA | Flag indicating whether phase A exists in the component. Return True or False. | Boolean
2131 | Virtual Object | DMS Component | DMSCOMP | input | COMPPHASEB | Flag indicating whether phase B exists in the component. Return True or False. | Boolean
2132 | Virtual Object | DMS Component | DMSCOMP | input | COMPPHASEC | Flag indicating whether phase C exists in the component. Return True or False. | Boolean
2133 | Virtual Object | DMS Component | DMSCOMP | input | COMPPHASEN | Flag indicating whether phase N exists in the component. Return True or False. | Boolean
2134 | Virtual Object | DMS Component | DMSCOMP | output | COMPTYPESTRING | Returns the component type string of the component | String
2135 | Virtual Object | DMS Component | DMSCOMP | input | DEENERGIZEDATETIME | The time when load is deenergized. It is for loads and distribution transformers. | String
2136 | Virtual Object | DMS Component | DMSCOMP | output | DEENERGIZEDATETIME_TICKS | The time of the load is de-energized | String
2137 | Virtual Object | DMS Component | DMSCOMP | input | DNOMDEVICEID | The DNOM record ID of the device. | String
2138 | Virtual Object | DMS Component | DMSCOMP | input | DYNFEEDERNAME | Dynamic feeder name. | String
2139 | Virtual Object | DMS Component | DMSCOMP | input | DYNFEEDERSUBNAME | Station name of the component’s dynamic feeder. | String
2140 | Virtual Object | DMS Component | DMSCOMP | input | DYNTFNAME | Energizing (dynamic)power transformer of the component. | String
2141 | Virtual Object | DMS Component | DMSCOMP |  | DYNSTATIONID | Dynamic station ID | String
2142 | Virtual Object | DMS Component | DMSCOMP | input | DYNSTATIONNAME | Dynamic station name. | String
2143 | Virtual Object | DMS Component | DMSCOMP |  | ENABLELVM | Indicates if the device is LVM eligible | Boolean
2144 | Virtual Object | DMS Component | DMSCOMP | output | FLOWVIOLATIONLEVEL | The highest violated flow limit level. | Integer
2145 | Virtual Object | DMS Component | DMSCOMP | input | FROMFEEDER | Nominal feeder name of the “from node” of the component if the component is a branch, or the nominal feeder name of the component if the component is a shunt. | String
2146 | Virtual Object | DMS Component | DMSCOMP |  | INTERNALLYENERGIZEDPHASEA | A flag indicating that phase A is internally energized (true/false) | Boolean
2147 | Virtual Object | DMS Component | DMSCOMP |  | INTERNALLYENERGIZEDPHASEB | A flag indicating that phase B is internally energized (true/false) | Boolean
2148 | Virtual Object | DMS Component | DMSCOMP |  | INTERNALLYENERGIZEDPHASEC | A flag indicating that phase C is internally energized (true/false) | Boolean
2149 | Virtual Object | DMS Component | DMSCOMP | input | ISOPTDEVICE | Flag indicating whether the component is optimization function capable. It is for transformers and capacitors. | Boolean
2150 | Virtual Object | DMS Component | DMSCOMP | input | NORMALLYDEENERGIZED | Is the device normally de-energized? | Boolean
2151 | Virtual Object | DMS Component | DMSCOMP | input | NORMALLYLOOPED | Is the device normally looped? | Boolean
2152 | Virtual Object | DMS Component | DMSCOMP |  | NORMALLYNETWORKLOOPED | Indicates the normally network looped component | Boolean
2153 | Virtual Object | DMS Component | DMSCOMP |  | NORMALLYPARALLELLOOPED | Indicates the normally parallel looped component | Boolean
2154 | Virtual Object | DMS Component | DMSCOMP | input | OSMFEEDERFILTER | If the input Feeder matches either the from or to feeder, the string stays the same. Otherwise, it's blanked out. | String
2155 | Virtual Object | DMS Component | DMSCOMP | input | OVERLOADCOMPTYPE | Type name of the component. Return “Overhead Line:, “Underground Line”, “Switch”, “Elbow”, “Fuse”, “Recloser”, “Breaker”,”Sectionalizer”, “Distribution Transformer”, “Regulator”, “Power Transformer”, “Auto Transformer”, “Jumper”, “Series Reactor”, or “Not Identified”. | String
2156 | Virtual Object | DMS Component | DMSCOMP | input | OVERLOADCOMPTYPEINDEX | the index of overloaded component type for sorting 1: underground line 2: overhead line 3: switch 4: auto tx 5: power tx 6: regulator 7: series reactor 8: dist tx | Integer
2157 | Virtual Object | DMS Component | DMSCOMP | output | PFCOMPTIME | Latest power flow solution time. | String
2158 | Virtual Object | DMS Component | DMSCOMP | output | PFCOMPTIME_TICKS | The latest solution time | String
2159 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYADJUSTEDAVAILCAP | The available capacity without including the RC impact. | String
2160 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYADJUSTEDLOADING | The % loading of the component with the flow value including the RC impact. | String
2161 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYDERATEDAVAILCAP | The available capacity with including the RC impact. | String
2162 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYDERATEDLIMIT | The value of the maximum derated violation limit level (or level 1 if no violation). | String
2163 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYDERATEDLOADING | The % loading of the component with the derated limit value. | String
2164 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYNOMINALLIMIT | The value of the maximum violated limit level (or level 1 if no violation). | String
2165 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYUNADJUSTEDFLOW | The DPF calculated flow value. | String
2166 | Virtual Object | DMS Component | DMSCOMP | output | RESERVEDCAPACITYVALUE | The Reserved Capacity derating value. | String
2167 | Virtual Object | DMS Component | DMSCOMP | input | RTCLIENT | Flag indicating the component is in real time context. True = real time. | Boolean
2168 | Virtual Object | DMS Component | DMSCOMP | input | SSCUST | The customer count of the switchable section the component is in. | Integer
2169 | Virtual Object | DMS Component | DMSCOMP | input | SSHIVLT | Highest voltage load for switchable section the component is in (in measurement voltage base). | Float
2170 | Virtual Object | DMS Component | DMSCOMP | output | SSLDLSKVAR | The total reactive load of the switchable section the line is in. | Float
2171 | Virtual Object | DMS Component | DMSCOMP | output | SSLDLSKW | The total real load of the switchable section the line is in. | Float
2172 | Virtual Object | DMS Component | DMSCOMP | input | SSLOVLT | Lowest voltage load for switchable section the component is in (in measurement voltage base). | Float
2173 | Virtual Object | DMS Component | DMSCOMP | input | TFIDFROMSWITCH | The ID of the transformer that is connected to the switch. | String
2174 | Virtual Object | DMS Component | DMSCOMP | input | TOFEEDER | Nominal feeder name of the “to node” of the component if the component is a branch, or the nominal feeder name of the component if the component is a shunt. | String
2175 | Virtual Object | DMS Component | DMSCOMP | input | UNDERGROUND | Is the device underground? | Boolean
2176 | Virtual Object | DMS Component | DMSCOMP | input | VOLTLEVEL | Nominal Voltage level voltage in kV (line to neutral voltage for single phase component and line to line voltage for three phase component) | String
2177 | Virtual Object | DMS Component | DMSCOMP | input | VOLTSECLEVEL | Nominal Voltage level voltage in kV (line to line) | String
2178 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | LIMITCOMPTYPE | Type name of the component. Returns “LOAD”, “CAPACITOR”, “TEMP. FAULT”, “TEMP. GROUND”, “TEMP. PLAN OUT”, “TEMP ENERGIZED”, or “NOT IDENTIFIED”. | String
2179 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | NODEID | Shunt node ID. | String
2180 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | NODENUM | Node name | String
2181 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | SHUNTCONNECTION | Connection type (Delta, Grounded Wye, or Ungrounded Wye) | String
2182 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | SHUNTPHASING | Shunt phases. | String
2183 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | STRUCTUREID | ID of a structure (e.g., pole) that is associated with the device | String
2184 | Virtual Object | DMS Shunt Component | DMSSHUNT | input | TOPODELETED | Flag indicating whether the component has been removed. | Boolean
2185 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPDIAGDETAIL | The detailed diagnostic message of the application. | String |  | #N/A | #N/A
2186 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPDIAGMSG | The general diagnostic message of the application. | String |  | #N/A | #N/A
2187 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPEXETIME | The execution time of related application. | String |  | #N/A | #N/A
2188 | DNAF Object | DNAF Information | DNAFDIAGNOSTIC | output | APPEXETIME_TICKS | The last execution time of the related application in clock ticks | String
2189 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPNAME | The DNAF application name related to this diagnostic info object. | String |  | #N/A | #N/A
2190 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPSOLUPLANNUM | The number of plans for the currently generated application solution. | String |  | #N/A | #N/A
2191 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | APPSOLUTIONID | The related DNAF application's solution ID. | String |  | #N/A | #N/A
2192 | DNAF Object | DNAF Information | DNAFDIAGNOSTIC |  | DIAGNOSTICDETAILS | Diagnostic details | String
2193 | DNAF Object | Dnaf Diagnostic Info | DNAFDIAGNOSTIC | output | SUBNAME | The substation name related to this object. | String |  | #N/A | #N/A
2194 | DNOM Component | Dnom Object | DNMOBJ | input | CUSTOMFIELD | Custom field | String
2195 | DNOM Group Object | DNOM Object | DNMOBJ | input | AREAIND | Integer (index) into station permission area list | Integer
2196 | DNOM Group Object | DNOM Object | DNMOBJ | input | DNOMRECORDNAME | Object name in the DNOM | String
2197 | DNOM Group Object | DNOM Object | DNMOBJ | input | DNOMX | X coordinate | Float
2198 | DNOM Group Object | DNOM Object | DNMOBJ | input | DNOMY | Y coordinate | Float
2199 | DNOM Group Object | DNOM Object | DNMOBJ | input | EXTCOMPANY | The name of the extenal company (for components that are owned by an external company) | Integer
2200 | DNOM Group Object | DNOM Object | DNMOBJ | input | LOCATIONDESCRIPTION | Pointer to the string with information about the device location (for example, pole number or street number) | Pointer
2201 | DNOM Group Object | DNOM Object | DNMOBJ | input | STATE | Pointer to the string with the name of the associated state | Pointer
2202 | DNOM Group Object | DNOM Object | DNMOBJ | input | COUNTY | Pointer to the string with the name of the associated county | Pointer
2203 | DNOM Group Object | DNOM Object | DNMOBJ | input | MUNICIPALITY | Pointer to the string with the name of the associated municipality | Pointer
2204 | DNOM Group Object | DNOM Object | DNMOBJ | input | ID | Object unique ID | String
2205 | DNOM Group Object | DNOM Object | DNMOBJ | input | NAME | Object name | String
2206 | DNOM Group Object | DNOM Object | DNMOBJ | input | NEWATMSK0 | Additional attributes bitmask flag | Integer
2207 | DNOM Group Object | DNOM Object | DNMOBJ | input | XCOORDINATE | Similar to DNOMX | String
2208 | DNOM Group Object | DNOM Object | DNMOBJ | input | YCOORDINATE | Similar to DNOMY | String
2209 | Virtual Object | DNOM Component | DNOMCOMP |  | N/A | Supports query fields of DNOM objects | String
2210 | DNOM Group Object | DNOM Object | DNOMOBJ | input | COMPANYNAME | Name of a company that owns the device | String
2211 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD1NAME | Name of the custom field 1 of the associated component | String
2212 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD1VALUE | Value of the custom field 1 of the associated component | String
2213 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD2NAME | Name of the custom field 2 of the associated component | String
2214 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD2VALUE | Value of the custom field 2 of the associated component | String
2215 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD3NAME | Name of the custom field 3 of the associated component | String
2216 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD3VALUE | Value of the custom field 3 of the associated component | String
2217 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD4NAME | Name of the custom field 4 of the associated component | String
2218 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD4VALUE | Value of the custom field 4 of the associated component | String
2219 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD5NAME | Name of the custom field 5 of the associated component | String
2220 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD5VALUE | Value of the custom field 5 of the associated component | String
2221 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD6NAME | Name of the custom field 6 of the associated component | String
2222 | DNOM Group Object | DNOM Object | DNOMOBJ | input | CUSTOMFIELD6VALUE | Value of the custom field 6 of the associated component | String
2223 | DNOM Group Object | DNOM Object | DNOMOBJ | input | ISTHIRDPARTY | Flag indicating that the component is owned by a third-party company | Boolean
2224 | DNOM Group Object | DNOM Object | DNOMOBJ | input | LOCATION | The X coordinate and Y coordinate of the dnom object. | String |  | #N/A | #N/A
2225 | DNOM Group Object | DNOM Object | DNOMOBJ | input | LOCATIONDESCRIPTION | Information about the device location (for example, pole number or street number) | String
2226 | DNOM Group Object | DNOM Object | DNOMOBJ | input | STATE | The name of the associated state | String
2227 | DNOM Group Object | DNOM Object | DNOMOBJ | input | COUNTY | The name of the associated county | String
2228 | DNOM Group Object | DNOM Object | DNOMOBJ | input | MUNICIPALITY | The name of the associated municipality | String
2229 | DNAF Object | DSO Substation Group | DSOGRP |  | AFRCLOSEDLOOP | AFR Closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
2230 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONACTIVEDEMAND | Total DPF calculated real power demand at the load side (secondary) | String | DPF | MW | MW
2231 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONACTIVEDEMANDHIGHLOW | Total DPF calculated real power demand at the source side (primary) and at the load side (secondary) | String | DPF | MW | MW
2232 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONACTIVELOSS | Calculated real power losses | String | DPF | MW | MW
2233 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONACTIVELOSS | Calculated real power loss in MW | Float | DPF | MW | MW
2234 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONCAPACITORMVAROFFLINE | The calculated offline capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. As opposed to the calculation for online capacitor reactive power, the offline calculation only includes disconnected remote capacitors. | String | MVAR | MVAR | MVAR
2235 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONCAPACITORMVARONLINE | The calculated online capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. This includes connected fixed and remote capacitors as well as all local capacitors. | String | MVAR | MVAR | MVAR
2236 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.ID | ID of the object function schedule array | String |  |  |  | DNMOBJ
2237 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2238 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.Name | Name of the object function schedule array | String |  |  |  | DNMOBJ
2239 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2240 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2241 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2242 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2243 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2244 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2245 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2246 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2247 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2248 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2249 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2250 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONCAPACITORMVARTOTAL | The total capacitor reactive power, which is the sum of the online and offline capacitor reactive power for each aggregation object. | String | MVAR | MVAR | MVAR
2251 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONDERACTIVEDEMAND | Calculated DER/DG real power injection in MW | Float | DPF | MW | MW
2252 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONDERREACTIVEDEMAND | Calculated DER/DG reactive power injection in MVAR | Float | DPF | MVAR | MVAR
2253 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONNATIVEACTIVEDEMAND | Calculated native real power demand in MW | Float | DPF | MW | MW
2254 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONNATIVEREACTIVEDEMAND | Calculated native reactive power demand in MVAR | Float | DPF | MVAR | MVAR
2255 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONPOWERFACTOR | Calculated power factor at the load side | String | DPF
2256 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONPOWERFACTORHIGHLOW | Calculated power factor at the source side (primary) and at the load side (secondary) | String | DPF
2257 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONREACTIVEDEMAND | Total DPF calculated reactive power demand at the load side (secondary) | String | DPF | MVAR | MVAR
2258 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONREACTIVEDEMANDHIGHLOW | Total DPF calculated reactive power demand at the source side (primary) and at the load side (secondary) | String | DPF | MVAR | MVAR
2259 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONREACTIVELOSS | Calculated reactive power losses | String | DPF | MVAR | MVAR
2260 | DNAF Object | DSO Substation Group | DSOGRP | output | AGGREGATIONREACTIVELOSS | Calculated reactive power loss in MVAR | Float | DPF | MVAR | MVAR
2261 | DNAF Object | DSO Group | DSOGRP | input | AOBJFUNCSCHARRAY | Pointer to the object function schedule array | String
2262 | DNAF Object | DSO Substation Group | DSOGRP |  | FISRCLOSEDLOOP | FISR closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
2263 | DNAF Object | DSO Substation Group | DSOGRP | output | HASMAN_DSOGRP_REACTIVE_THROTTLING_DOWN | Specifies whether manually entered value for reactive power throttling for decreases exists | Boolean
2264 | DNAF Object | DSO Substation Group | DSOGRP | output | HASMAN_DSOGRP_REACTIVE_THROTTLING_UP | Specifies whether manually entered value for reactive power throttling for increases exists | Boolean
2265 | DNAF Object | DSO Substation Group | DSOGRP | output | HASMAN_DSOGRP_REAL_THROTTLING_DOWN | Specifies whether manually entered value for real power throttling for decreases exists | Boolean
2266 | DNAF Object | DSO Substation Group | DSOGRP | output | HASMAN_DSOGRP_REAL_THROTTLING_UP | Specifies whether manually entered value for real power throttling for increases exists | Boolean
2267 | DNAF Object | DSO Group | DSOGRP | input | ID | Object unique ID | String |  |  |  | DNMOBJ
2268 | DNAF Object | DSO Substation Group | DSOGRP |  | LVMCLOSEDLOOP | LVM closed loop/advisory flag (true = closed loop, false = advisory) | Boolean
2269 | DNAF Object | DSO Group | DSOGRP |  | LVMHEURISTIC | A flag indicating that heuristic LVM solution is used | Boolean
2270 | DNAF Object | DSO Substation Group | DSOGRP | input | MAN_DSOGRP_REACTIVE_THROTTLING_DOWN | Manually entered rate at which reactive power decrease is throttled during an LVM plan execution. | Float |  | MVAR/minute | MVAR/minute
2271 | DNAF Object | DSO Substation Group | DSOGRP | input | MAN_DSOGRP_REACTIVE_THROTTLING_UP | Manually entered rate at which reactive power increase is throttled during an LVM plan execution. | Float |  | MVAR/minute | MVAR/minute
2272 | DNAF Object | DSO Substation Group | DSOGRP | input | MAN_DSOGRP_REAL_THROTTLING_DOWN | Manually entered rate at which real power decrease is throttled during an LVM plan execution. | Float |  | MW/minute | MW/minute
2273 | DNAF Object | DSO Substation Group | DSOGRP | input | MAN_DSOGRP_REAL_THROTTLING_UP | Manually entered rate at which real power increase is throttled during an LVM plan execution. | Float |  | MW/minute | MW/minute
2274 | DNAF Object | DSO Group | DSOGRP | input | NAME | Object name | String |  |  |  | DNMOBJ
2275 | DNAF Object | DSO Group | DSOGRP |  | NUMOBJFUNCSCH | Number of objective function schedules | Integer
2276 | DNAF Object | DSO Substation Group | DSOGRP | input | REACTIVEPOWERTHROTTLINGDOWN | Rate at which reactive power decrease is throttled during an LVM plan execution. | Float |  | MVAR/minute | MVAR/minute
2277 | DNAF Object | DSO Substation Group | DSOGRP | input | REACTIVEPOWERTHROTTLINGUP | Rate at which reactive power increase is throttled during an LVM plan execution. | Float |  | MVAR/minute | MVAR/minute
2278 | DNAF Object | DSO Substation Group | DSOGRP | input | REALPOWERTHROTTLINGDOWN | Rate at which real power decrease is throttled during an LVM plan execution. | Float |  | MW/minute | MW/minute
2279 | DNAF Object | DSO Substation Group | DSOGRP | input | REALPOWERTHROTTLINGUP | Rate at which real power increase is throttled during an LVM plan execution. | Float |  | MW/minute | MW/minute
2280 | DNOM Component | Distribution Transformer Output | DTFOUT |  | COPPLOSS | Total transformer core loss | Float |  | P + jQ | P + jQ
2281 | DNOM Component | Distribution Transformer Output | DTFOUT |  | CORELOSS | Total transformer copper loss | Float |  | P + jQ | P + jQ
2282 | DNOM Component | Distribution Transformer Output | DTFOUT |  | IPRIMA | Phase A current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
2283 | DNOM Component | Distribution Transformer Output | DTFOUT |  | IPRIMB | Phase B current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
2284 | DNOM Component | Distribution Transformer Output | DTFOUT |  | IPRIMC | Phase C current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
2285 | DNOM Component | Distribution Transformer Output | DTFOUT |  | IPRIMN | Phase N current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
2286 | DNOM Component | Distribution Transformer Output | DTFOUT |  | ISEC1A | Phase A current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
2287 | DNOM Component | Distribution Transformer Output | DTFOUT |  | ISEC1B | Phase B current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
2288 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2289 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
2290 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | DISTTF
2291 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.CUSTMERA | The number of phase A only connected customers | Integer |  |  |  | DISTTF
2292 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.CUSTMERB | The number of phase B only connected customers | Integer |  |  |  | DISTTF
2293 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.CUSTMERC | The number of phase C only connected customers | Integer |  |  |  | DISTTF
2294 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.CUSTOMER | The number of connected customers | Integer |  |  |  | DISTTF
2295 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2296 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2297 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | DISTTF
2298 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
2299 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | DISTTF
2300 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | DISTTF
2301 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
2302 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.NAME | Name of the object | String |  |  |  | DNMOBJ
2303 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2304 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2305 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2306 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.PRIMGNDR | Primary grounding branch resistance | Float |  |  |  | DISTTF
2307 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.PRIMGNDX | Primary grounding branch reactance | Float |  |  |  | DISTTF
2308 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.PRIMOPERVOLT | Primary operating voltage (in kV l-g) | Integer |  |  |  | DISTTF
2309 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.PRIMWIND | Primary winding connection type | Integer |  |  |  | DISTTF
2310 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | DISTTF
2311 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.SEC1GNDR | Secondary grounding branch resistance | Float |  |  |  | DISTTF
2312 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.SEC1GNDX | Secondary grounding branch reactance | Float |  |  |  | DISTTF
2313 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.SECWIND | Secondary winding connection type | Integer |  |  |  | DISTTF
2314 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.TFLOADED | Connected load flag | Boolean |  |  |  | DISTTF
2315 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | DISTTF
2316 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.VOLTPR | Primary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
2317 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF.VOLTSC | Secondary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
2318 | DNOM Component | Distribution Transformer Output | DTFOUT |  | ISEC1C | Phase C current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
2319 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2320 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
2321 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | DISTTF
2322 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.CUSTMERA | The number of phase A only connected customers | Integer |  |  |  | DISTTF
2323 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.CUSTMERB | The number of phase B only connected customers | Integer |  |  |  | DISTTF
2324 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.CUSTMERC | The number of phase C only connected customers | Integer |  |  |  | DISTTF
2325 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.CUSTOMER | The number of connected customers | Integer |  |  |  | DISTTF
2326 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2327 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2328 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | DISTTF
2329 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
2330 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | DISTTF
2331 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | DISTTF
2332 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
2333 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.NAME | Name of the object | String |  |  |  | DNMOBJ
2334 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2335 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2336 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2337 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.PRIMGNDR | Primary grounding branch resistance | Float |  |  |  | DISTTF
2338 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.PRIMGNDX | Primary grounding branch reactance | Float |  |  |  | DISTTF
2339 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.PRIMOPERVOLT | Primary operating voltage (in kV l-g) | Integer |  |  |  | DISTTF
2340 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.PRIMWIND | Primary winding connection type | Integer |  |  |  | DISTTF
2341 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | DISTTF
2342 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.SEC1GNDR | Secondary grounding branch resistance | Float |  |  |  | DISTTF
2343 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.SEC1GNDX | Secondary grounding branch reactance | Float |  |  |  | DISTTF
2344 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.SECWIND | Secondary winding connection type | Integer |  |  |  | DISTTF
2345 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.TFLOADED | Connected load flag | Boolean |  |  |  | DISTTF
2346 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | DISTTF
2347 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.VOLTPR | Primary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
2348 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF.VOLTSC | Secondary Rated voltage (kV line to ground). | Float |  |  |  | DISTTF
2349 | DNOM Component | Distribution Transformer Output | DTFOUT |  | ISEC1N | Phase N current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
2350 | DNOM Component | Distribution Transformer Output | DTFOUT |  | LIMFLAGS | Limit violation flags | Integer
2351 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQPRIMA | Phase A power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
2352 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQPRIMB | Phase B power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
2353 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQPRIMC | Phase C power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
2354 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQPRIMN | Phase N power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
2355 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQSEC1A | Phase A power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
2356 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQSEC1B | Phase B power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
2357 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQSEC1C | Phase C power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
2358 | DNOM Component | Distribution Transformer Output | DTFOUT |  | PQSEC1N | Phase N power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
2359 | DNOM Component Placement | Distribution Transformer Bank Placement | DTFPLE | input | TF | Pointer to the associated distribution transformer | String
2360 | DNOM Component Placement | Distribution Transformer Bank Label Placement | DTLBPL | input | TF | Pointer to the associated distribution transformer | String
2361 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ALTNAME | Alternate name of the energy resource | String |  |  |  | ENERGYRES
2362 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2363 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.CONTYPE | Connection type (1 - Not Set, 1 - Induction, 2 - DFIG - Doubly Fed Induction Generator, 3 - Inverter Coupled) | Enumeration |  |  |  | ENERGYRES
2364 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.DEVTYPE | Device type (0 - Not Set, 1 - Wind, 2 - Solar,3 - Micro_Turbine, 4 - Fuel_Cell, 5 - Battery_Storage, 6 - Gas, 7 - Biomass, 8 - Others) | Enumeration |  |  |  | ENERGYRES
2365 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2366 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2367 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ENERGYRESBITMSK | Energy resource bitmask | Integer |  |  |  | ENERGYRES
2368 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ENERGYRESHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set | Boolean |  |  |  | ENERGYRES
2369 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ENERGYRESHASQTARGETOVERRIDE | Indicates whether the energy resource has a manual Q target | Boolean |  |  |  | ENERGYRES
2370 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ENERGYRESHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set. | Boolean |  |  |  | ENERGYRES
2371 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ENERGYRESNOMVOLT | Nominal voltage of the energy resource | String |  |  |  | ENERGYRES
2372 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.EXITEMODE | Energy resource excitation mode (0 - NotSet, 1 - ConstantV, 2 - ConstantQ, 3 - ConstantPF) | Enumeration |  |  |  | ENERGYRES
2373 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
2374 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.GENTYPE | The type of the generator (PV or PQ) | Integer |  |  |  | ENERGYRES
2375 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
2376 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
2377 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.MANPTARGET | Manually entered real power target value | Float |  | kW | kW | ENERGYRES
2378 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.MANQTARGET | The manual reactive power target of the energy resource | Float |  |  |  | ENERGYRES
2379 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.MANVTARGET | Manually entered voltage target value | Float |  | p.u. | p.u. | ENERGYRES
2380 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.NAME | Name of the object | String |  |  |  | DNMOBJ
2381 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2382 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2383 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.NORMDEENER | Flag indicating that the energy resource is normally de-energized | Boolean |  |  |  | ENERGYRES
2384 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2385 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.PHSENSE | Phases measured | Integer |  |  |  | ENERGYRES
2386 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.RGROUND | Grounding resistance | Float |  | Ohms | Ohms | ENERGYRES
2387 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.SLACKBUS | Flag indicating whether the energy resource is a slack bus | Boolean |  |  |  | ENERGYRES
2388 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.VMAXSEP | Maximum voltage before separation from the network (per unit). | Float |  |  |  | ENERGYRES
2389 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.VMINSEP | Minimum voltage before separation from the network (per unit). | Float |  |  |  | ENERGYRES
2390 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.VREGLL | Indicates whether the line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation) | Boolean |  |  |  | ENERGYRES
2391 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
2392 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES.XGROUND | Grounding reactance | Float |  | Ohms | Ohms | ENERGYRES
2393 | DNOM Component | Dynamic Schedule | DYNSCHED | input | DEVICEID | Device ID | String
2394 | DNOM Component | Dynamic Schedule | DYNSCHED | input | GROUPID | Station name | String
2395 | DNOM Component | Dynamic Schedule | DYNSCHED | input | SCHEDULETYPE | Enumeration of the schedule type (e.g., 2 = Load-to-Voltage Dependency) | Integer
2396 | DNOM Component | Dynamic Schedule | DYNSCHED | input | XUNIT | Unit of the schedule’s X axis | String
2397 | DNOM Component | Dynamic Schedule | DYNSCHED | input | XVALUE | Value of the schedule’s X axis | String
2398 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YUNIT | Unit of the schedule’s Y axis | String
2399 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YUNIT2 | Unit of the schedule’s Y2 axis | String
2400 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YUNIT3 | Unit of the schedule’s Y3 axis | String
2401 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YVALUE | Value of the schedule’s Y axis | Float
2402 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YVALUE2 | Value of the schedule’s Y2 axis | Float
2403 | DNOM Component | Dynamic Schedule | DYNSCHED | input | YVALUE3 | Value of the schedule’s Y3 axis | Float
2404 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
2405 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2406 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2407 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2408 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2409 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2410 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2411 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2412 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2413 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2414 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2415 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2416 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2417 | DNOM Component Placement | Energy Resource Placement | ENERGYPLE | input | ENERGYRES | Pointer to the associated energy resource | String
2418 | DNOM Component | Energy Resource | ENERGYRES |  | DERMEASDATASOURCE | Measurement data source (--, SCADA, or GATEWAY) | String
2419 | DNOM Component | Energy Resource | ENERGYRES | input | ADDRESS | Energy resource address | String |  |  |  | NDPFST
2420 | DNOM Component | Energy Resource | ENERGYRES | input | ALTNAME | Alternate Name. | String
2421 | DNOM Component | Energy Resource | ENERGYRES | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2422 | DNOM Component | Energy Resource | ENERGYRES | input | CONNECTIONCONTROLFLAG | Flag indicating that the connection (connect/disconnect) status can be controlled | Boolean
2423 | DNOM Component | Energy Resource | ENERGYRES | input | CONTROLCAP | Energy Resource Control type. 0 = No Control 1 = On/off Control 2 = P control with on/off control 3 = P control without on/off control 4 = Q control with on/off control 5 = Q control without on/off control 6 = PQ control with on/off control 7 = PQ control without on/off control | Integer
2424 | DNOM Component | Energy Resource | ENERGYRES | input | CONTYPE | Connection type | Integer
2425 | DNOM Component | Energy Resource | ENERGYRES | input | CSCHED | Pointer to the charging schedule | String
2426 | DNOM Component | Energy Resource | ENERGYRES | input | DERAGGREGATOR | DER aggregator | String
2427 | DNOM Component | Energy Resource | ENERGYRES | output | DERCONNECTCTRLSTATUS | DER connection control status via 2030.5 Gateway ("" = None, "S" = Sent, "A" = Acknowledged, "R" = Rejected) | String
2428 | DNOM Component | Energy Resource | ENERGYRES | input | DERCONNECTSTATUS | Connection status of the DER. 0 = Disconnected 1 = Connected 2 = Unknown | Enumeration
2429 | DNOM Component | Energy Resource | ENERGYRES | output | DERCTRLCONNECT | DER connection control value for the 2030.5 Gateway | String
2430 | DNOM Component | Energy Resource | ENERGYRES | output | DERCTRLCURVE | DER curve control value for the 2030.5 Gateway | String
2431 | DNOM Component | Energy Resource | ENERGYRES | input | DERCTRLCURVES | DER control curves | String
2432 | DNOM Component | Energy Resource | ENERGYRES | output | DERCTRLKVAR3PHASE | DER reactive power output control value for the 2030.5 Gateway | String
2433 | DNOM Component | Energy Resource | ENERGYRES | output | DERCTRLKW3PHASE | DER real power output control value for the 2030.5 Gateway | String
2434 | DNOM Component | Energy Resource | ENERGYRES | output | DERCTRLPF | DER power factor control value for the 2030.5 Gateway | String
2435 | DNOM Component | Energy Resource | ENERGYRES | input | DERCURVE | DER curve | String
2436 | DNOM Component | Energy Resource | ENERGYRES | output | DERCURVECTRLSTATUS | DER curve control status via 2030.5 Gateway ("" = None, "S" = Sent, "A" = Acknowledged, "R" = Rejected) | String
2437 | DNOM Component | Energy Resource | ENERGYRES | input | DERKVAR3PHASE | Reactive power output by the DER | String |  | kVAR | kVAR
2438 | DNOM Component | Energy Resource | ENERGYRES | output | DERKVARCTRLSTATUS | DER reactive power output control status via 2030.5 Gateway ("" = None, "S" = Sent, "A" = Acknowledged, "R" = Rejected) | String
2439 | DNOM Component | Energy Resource | ENERGYRES | input | DERKW3PHASE | Real power output by the DER | String |  | kW | kW
2440 | DNOM Component | Energy Resource | ENERGYRES | output | DERKWATTCTRLSTATUS | DER real power output control status via 2030.5 Gateway ("" = None, "S" = Sent, "A" = Acknowledged, "R" = Rejected) | String
2441 | DNOM Component | Energy Resource | ENERGYRES | input | DERPF | DER power factor | String
2442 | DNOM Component | Energy Resource | ENERGYRES | output | DERPFCTRLSTATUS | DER power factor control status via 2030.5 Gateway ("" = None, "S" = Sent, "A" = Acknowledged, "R" = Rejected) | String
2443 | DNOM Component | Energy Resource | ENERGYRES | input | DERPGENMAX | Maximum real power generation by the DER | String |  | kW | kW
2444 | DNOM Component | Energy Resource | ENERGYRES | input | DERPGENMIN | Minimum real power generation by the DER | String |  | kW | kW
2445 | DNOM Component | Energy Resource | ENERGYRES | input | DERQGENMAX | The maximum reactive power output by the DER. | Float |  | kVAR | kVAR
2446 | DNOM Component | Energy Resource | ENERGYRES | input | DERQGENMIN | The minimum reactive power output by the DER. | Float |  | kVAR | kVAR
2447 | DNOM Component | Energy Resource | ENERGYRES | input | DERPHASE | The energy resource phasing. | String
2448 | DNOM Component | Energy Resource | ENERGYRES | input | DERTFID | ID of the power transformer that is assiciated with the DER | String
2449 | DNOM Component | Energy Resource | ENERGYRES |  | DEVICEDSOOVER | Flag from the model to override whether to use in the Distribution System Optimization | Boolean
2450 | DNOM Component | Energy Resource | ENERGYRES | input | DEVTYPE | Energy Resource Device Type. 1 = wind 2 = solar 3 = micro turbine 4 = fuel cell 5 = battery storage 6 = gas 7 = biomass 8 = others 9 = cogeneration 10 = hydro 11 = EV charging station | Integer
2451 | DNOM Component | Energy Resource | ENERGYRES | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
2452 | DNOM Component | Energy Resource | ENERGYRES | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2453 | DNOM Component | Energy Resource | ENERGYRES | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2454 | DNOM Component | Energy Resource | ENERGYRES | input | DSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String
2455 | DNOM Component | Energy Resource | ENERGYRES |  | DYNFREQ | Dynamic DER three-phase frequency value from a measurement | Float
2456 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVA | Dynamic DER phase A apparent power value from a measurement | Float |  | kVA | kVA
2457 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVAR | Dynamic DER three-phase reactive power value from a measurement | Float |  | kVAR | kVAR
2458 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVARA | Dynamic DER phase A reactive power value from a measurement | Float |  | kVAR | kVAR
2459 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVARB | Dynamic DER phase B reactive power value from a measurement | Float |  | kVAR | kVAR
2460 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVARC | Dynamic DER phase C reactive power value from a measurement | Float |  | kVAR | kVAR
2461 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVB | Dynamic DER phase B apparent power value from a measurement | Float |  | kVA | kVA
2462 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVC | Dynamic DER phase C apparent power value from a measurement | Float |  | kVA | kVA
2463 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKVR | Dynamic DER apparent power value from a measurement | Float |  | kVA | kVA
2464 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKW | Dynamic DERthree-phase real power value from a measurement | Float |  | kW | kW
2465 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKWA | Dynamic DER phase A real power value from a measurement | Float |  | kW | kW
2466 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKWB | Dynamic DER phase B real power value from a measurement | Float |  | kW | kW
2467 | DNOM Component | Energy Resource | ENERGYRES |  | DYNKWC | Dynamic DER phase C real power value from a measurement | Float |  | kW | kW
2468 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXCHARGERATEW | DER dynamic limit - maximum charge rate | Float
2469 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXDISCHARGERATEW | DER dynamic limit - maximum discharge rate | Float
2470 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXKVA | DER dynamic limit - maximum apparent power | Float |  | kVA | kVA
2471 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXKVAR | DER dynamic limit - maximum reactive power | Float |  | kVAR | kVAR
2472 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXKVARNEG | DER dynamic limit - maximum negative reactive power | Float |  | kVAR | kVAR
2473 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMAXKW | DER dynamic limit - maximum real power | Float |  | kW | kW
2474 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMINPFOVEREXCITED | DER dynamic limit - minimum power factor when overeexcited | Float
2475 | DNOM Component | Energy Resource | ENERGYRES |  | DYNLIMITMINPFUNDEREXCITED | DER dynamic limit - minimum power factor when underexcited | Float
2476 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.CONFAULTCURR | A flag indicating that energy resource will contribute to fault current during SSC or PRV (used instead of ALLOWLVRT) | Boolean |  |  |  | ENERGYRESMOD
2477 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.ID | ID of the energy resource mode | String |  |  |  | DNMOBJ
2478 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.KVA | Generator rating | Float |  | kVA | kVA | ENERGYRESMOD
2479 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.NUMOPSCHEDS | Number of operation schedules | String |  |  |  | ENERGYRESMOD
2480 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.PGENMAX | Maximum real power output | Float |  | kW | kW | ENERGYRESMOD
2481 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.PGENMIN | Minimum real power output | Float |  | kW | kW | ENERGYRESMOD
2482 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.POUTCAPCURVESCHED | Real power output capability curve schedule | String |  |  |  | ENERGYRESMOD
2483 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.QGENMAX | The maximum reactive power output | Float |  | kVAR | kVAR | ENERGYRESMOD
2484 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.QGENMIN | The minimum reactive power output | Float |  | kVAR | kVAR | ENERGYRESMOD
2485 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.QOUTCAPCURVESCHED | Reactive power output capability curve schedule | String |  |  |  | ENERGYRESMOD
2486 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.R2 | Second sequence resistance | Float |  | p.u. | p.u. | ENERGYRESMOD
2487 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.RSC | Short circuit resistance | Float |  | p.u. | p.u. | ENERGYRESMOD
2488 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.RZERO | Zero sequence resistance | Float |  | p.u. | p.u. | ENERGYRESMOD
2489 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.SWCOST | The operational cost of switching on/off a generator | Float |  |  |  | ENERGYRESMOD
2490 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.VHIGHLIMIT | High voltage limit | Float |  |  |  | ENERGYRESMOD
2491 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.VLOWLIMIT | Low voltage limit | Float |  |  |  | ENERGYRESMOD
2492 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.VOLTAGEBASE | Voltage base value | Float |  | Volt | Volt | ENERGYRESMOD
2493 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.VOLTUNIT | Enumerated flag indicating the voltage units that should be used. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer |  |  |  | ENERGYRESMOD
2494 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.X2 | Second sequence reactance | Float |  | p.u. | p.u. | ENERGYRESMOD
2495 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.XSC | Short circuit reactance | Float |  | p.u. | p.u. | ENERGYRESMOD
2496 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL.XZERO | Zero sequence reactance | Float |  | p.u. | p.u. | ENERGYRESMOD
2497 | DNOM Component | Energy Resource | ENERGYRES | input | DYNSOC | The current state of charge (or current capacity), which is the amount of charge that is stored in the device, in % of the energy rating. This value is provided via the Supervisory Control and Data Acquisition (SCADA) system or the 2030.5 Gateway. | Float |  | % | %
2498 | DNOM Component | Energy Resource | ENERGYRES | input | DYNSOCKWH | The current state of charge (or current capacity), which is the amount of charge that is stored in the device, in kWh. Calculated as 'Energy Rating' / 100 * 'State Of Charge (%)') This value is provided via the Supervisory Control and Data Acquisition (SCADA) system or the 2030.5 Gateway. | Float |  | kWh | kWh
2499 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRATING | The useable capacity of the storage device | Float |  | kWh | kWh
2500 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESBITMSK | Bitmask - for booleans. | Integer
2501 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESGATEWAY | Pointer to the DER Gateway attributes | String
2502 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set. | Boolean
2503 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESHASQTARGETOVERRIDE | Indicates whether the energy resource has a manual Q target. | Boolean
2504 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set. | Boolean
2505 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESMODEL | Associated energy resource model name. | String
2506 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESNOMVOLT | Nominal voltage of the energy resource | Float
2507 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESSTG | Pointer to the corresponding storage device | String
2508 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESCONNECTTYPE | Connection type | String
2509 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESCONTRIBUTESTOFAULTCURRENT | Flag indicating that energy resource will contribute to fault current during SSC or PRV (used instead of ENGYRESLVRT) | Boolean
2510 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESENERGYRESPROGRAM | Enrolled Programs of the energy resource. | String
2511 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESDEVTYPE | Energy Resource Device Type. 1 = wind 2 = solar 3 = micro turbine 4 = fuel cell 5 = battery storage 6 = gas 7 = biomass 8 = others 9 = cogeneration 10 = hydro 11 = EV charging station | Integer
2512 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESEXCITMODE | Excitation mode | String
2513 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESLVRT | Flag indicating low voltage ride through (deprecated, use ENGYRESCONTRIBUTESTOFAULTCURRENT instead) | Boolean
2514 | DNOM Component | Energy Resource | ENERGYRES |  | ENGYRESOWNERSHIP | Energy resource ownership Unspecified = 0, // Should not be set to this CustomerOwnedMaintained = 1, // Customer Owned, Customer Maintained CustomerOwner_UtilityMaintained = 2, // Customer Owned, Utility Maintained UtilityOwnedMaintained = 3 // Utility Owned, Utility Maintained | Enumeration
2515 | DNOM Component | Energy Resource | ENERGYRES | input | ERCONNECTMEASID | ID of the connection status SCADA measurement | String
2516 | DNOM Component | Energy Resource | ENERGYRES | input | EXITEMODE | Excitation mode | Integer
2517 | DNOM Component | Energy Resource | ENERGYRES | input | FEEDERMAIN | Flag indicating if it is on feeder main. | Boolean
2518 | DNOM Component | Energy Resource | ENERGYRES | input | FREQUENCYMAXSEP | Maximum frequency before separation from the network (Hz). By default, 63 Hz. | Double |  | Hz | Hz
2519 | DNOM Component | Energy Resource | ENERGYRES | input | FREQUENCYMINSEP | Minimum frequency before separation from the network (Hz). By default, 56 Hz. | Double |  | Hz | Hz
2520 | DNOM Component | Energy Resource | ENERGYRES | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
2521 | DNOM Component | Energy Resource | ENERGYRES | input | GENTYPE | The type of the energy resource (PV or PQ). | Integer
2522 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.ADDRESS.NOAPPSTR | Load address | String |  |  |  | NOAPPSTR
2523 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String |  |  |  | OSMQUERYDEVICE
2524 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.AMPANDANGLEA | Phase A current (magnitude and angle in degrees) | Float |  | Amps | Amps | BRNCHSHUNT
2525 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.AMPANDANGLEB | Phase B current (magnitude and angle in degrees) | Float |  | Amps | Amps | BRNCHSHUNT
2526 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.AMPANDANGLEC | Phase current (magnitude and angle in degrees) | Float |  | Amps | Amps | BRNCHSHUNT
2527 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2528 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.BLAFLAGS | BLA flags | Integer |  |  |  | LOAD
2529 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.COLDLOADMULT | Load cold start multiplier | Float
2530 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.CONSTRUCTPHASES | Constructed Phases | String |  |  |  | FUTUREOP
2531 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.CRITICALCUSTNUM | Number of critical customers | Integer |  |  |  | LOAD
2532 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.CUSTOMERCOUNT | Customer count | Integer |  | count | count
2533 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.CUSTOMERDRRATIO | Ration of customers with DER | String
2534 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.CUSTOMERGENRATING | Customer generation rating | String
2535 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.CUSTOMERGENTYPE | Customer generation type | String
2536 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.CUSTOMERLOADTYPE | Customer load type | String
2537 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DISTTFTABNAME | The DNOM table name of the distribution transformer of the load | String
2538 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DNOMRECORDNAME | The DNOM record name of the generator | String |  |  |  | DNMOBJ
2539 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DNOMTABNAME | The DNOM table name of the load | String
2540 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2541 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2542 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DRRATIO | Demand response component of the load (in percent) | Integer |  |  |  | LOAD
2543 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.DYNFEEDERNAME | Dynamic (currently energizing) feeder name | String |  |  |  | DMSCOMP
2544 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.FEEDERNAME | Nominal feeder name | String |  |  |  | TOPOCOMP
2545 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
2546 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.GENRATING | Nameplate kVA rating of the generation component of the load | Integer |  |  |  | LOAD
2547 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.GENTYPE | User defined enumeration type for generation component | Integer |  |  |  | LOAD
2548 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
2549 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.HASMANUALENTRY | If one or some fields of load has(have) value override | Boolean
2550 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.ID | Object unique ID | String |  |  |  | DNMOBJ
2551 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.IFLOWA | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
2552 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.IFLOWB | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
2553 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.IFLOWC | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
2554 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.ISDYNFEEDERLOOPED | Flag indicating if Dynamic Feeder is Looped | Boolean |  |  |  | TOPOCOMP
2555 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.KVAR3PH | Total reactive power flow (kVAR) | Float |  | kVAR | kVAR | BRNCHSHUNT
2556 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVAR3PHDER | Associated DER apparent power phase ABC | String
2557 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVAR3PHNATIVE | Native load reactive power phase ABC | String
2558 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARADER | Associated DER apparent power phase A | String
2559 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARANATIVE | Native load reactive power phase A | String
2560 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARBDER | Associated DER apparent power phase B | String
2561 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARBNATIVE | Native load reactive power phase B | String
2562 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARCDER | Associated DER apparent power phase C | String
2563 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KVARCNATIVE | Native load reactive power phase C | String
2564 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.KW3PH | Total real power flow (kW) | Float |  | kW | kW | BRNCHSHUNT
2565 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KW3PHDER | Associated DER active power phase ABC | String
2566 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KW3PHNATIVE | Native load real power phase ABC | String
2567 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWADER | Associated DER active power phase A | String
2568 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWANATIVE | Native load real power phase A | String
2569 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWBDER | Associated DER active power phase B | String
2570 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWBNATIVE | Native load real power phase B | String
2571 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWCDER | Associated DER active power phase C | String
2572 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.KWCNATIVE | Native load real power phase C | String
2573 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LDSCHEDDISTTFLOADPERCENT | Associated distribution transformer loading (using manually overrided capacity) | Float |  | % | %
2574 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LDSCHEDDISTTFLOADRATINGPERCENT | Associated distribution transformer loading (using transformer rating capacity) | Float |  | % | %
2575 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LDSCHEDSECVOLTDROP | Associated distribution transformer secondary voltage drop | Float |  | % | %
2576 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LDSCHEDSECVOLTNAME | Secondary voltage drop load schedule name | Float
2577 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADCAT.NAME | Name of associated load category | String
2578 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADHASGEN | Indicates whether the load is with generation | Boolean
2579 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADHASMAN | Manual entry enable flag | Boolean
2580 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADHASVHIGHLMTMANENABLE | Whether the load has high voltage limit | Boolean
2581 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADHASVLOWLMTMANENABLE | Whether the load has low voltage limit | Boolean
2582 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADIMBALVOLTVALUE | Voltage Imbalance | String |  |  |  | LDBUS
2583 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKVARA | Phase A reactive power flow (kVAR) | Float |  | kVAR | kVAR
2584 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKVARB | Phase B reactive power flow (kVAR) | Float |  | kVAR | kVAR
2585 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKVARC | Phase C reactive power flow (kVAR) | Float |  | kVAR | kVAR
2586 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKWA | Phase A real power flow (kW) | Float |  | kW | kW
2587 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKWB | Phase B real power flow (kW) | Float |  | kW | kW
2588 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADKWC | Phase C real power flow (kW) | Float |  | kW | kW
2589 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADMANPA | Phase A or AB (if delta connected) nominal load (kW) | Float
2590 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADMANPB | Phase B or BC (if delta connected) nominal load (kW) | Float
2591 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADMANPC | Phase C or CA (if delta connected) nominal load (kW) | Float
2592 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADMANQA | Phase A or AB (if delta connected) nominal load (kVAR) | Float
2593 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADMANQB | Phase B or BC (if delta connected) nominal load (kVAR) | Float
2594 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADMANQC | Phase C or CA (if delta connected) nominal load (kVAR) | Float
2595 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADMANVOLTMEASVALUE | The SCADA voltage measurement value, if available | Float |  | Volt | Volt
2596 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADNUMBERDRCUSTOMERS | Number of customers with DER | String
2597 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADNUMBERGENCUSTOMERS | Number of customers with generation | String
2598 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADOPTVLIMHIGHEMERG | Optimization Emergency high voltage limit | Float
2599 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADOPTVLIMHIGHNORM | Optimization Normal high voltage limit | Float
2600 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADOPTVLIMLOWEMERG | Optimization Emergency low voltage limit | Float
2601 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADOPTVLIMLOWNORM | Optimization Normal low voltage limit | Float
2602 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADORBUSHASVOLTIMBALVIOLATION | Whether the load has voltage imbalance violation | Boolean
2603 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADOUTAGELENGTH | Load last outage length | String
2604 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADOUTAGETIME | Last recorded outage time (for cold load pick-up calculations) | String
2605 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADPF | Power Factor | Float
2606 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADPFNOM | Total nominal power factor of the load | Float
2607 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADPFNOMA | Phase A or AB (if delta connected) nominal power factor of the load | Float
2608 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADPFNOMB | Phase B or BC (if delta connected) nominal power factor of the load | Float
2609 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADPFNOMC | Phase C or CA (if delta connected) nominal power factor of the load | Float
2610 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADPNORM | Total nominal power of the load | Float
2611 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADPNORMA | Phase A or AB (if delta connected) nominal power of the load | Float
2612 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADPNORMB | Phase B or BC (if delta connected) nominal power of the load | Float
2613 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADPNORMC | Phase C or CA (if delta connected) nominal power of the load | Float
2614 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADPQIHIGH | PQI high voltage index | Float
2615 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADPQIIMBALANCE | PQI imbalance voltage index for three-phase loads | Float
2616 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADPQILOW | PQI low voltage index | Float
2617 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADQNORM | Total nominal reactive power of the load | Float
2618 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADQNORMA | Phase A or AB (if delta connected) nominal reactive power of the load | Float
2619 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADQNORMB | Phase B or BC (if delta connected) nominal reactive power of the load | Float
2620 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADQNORMC | Phase C or CA (if delta connected) nominal reactive power of the load | Float
2621 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADRESTORETIME | Last recorded restoration time (for cold load pick-up calculations) | String
2622 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN1 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2623 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN2 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2624 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN3 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2625 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN4 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2626 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN5 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2627 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADSTUDYBIN6 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period) | Float
2628 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADTFNAME | Connected transformer ID | String
2629 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADTFNAME2 | Second connected transformer ID (Special version to account for multiple transformers in a bank) | String
2630 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADTFNAMEFIRST | First connected transformer ID (Special version to account for multiple transformers in a bank) | Float
2631 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADTFVOLTA | Phase A Voltage magnitude of connected distribution transformer | Float |  | Volt | Volt
2632 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADTFVOLTB | Phase B Voltage magnitude of connected distribution transformer | Float |  | Volt | Volt
2633 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.LOADTFVOLTC | Phase C Voltage magnitude of connected distribution transformer | Float |  | Volt | Volt
2634 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLIMHIGHEMERG | High emergency voltage limit (configurable voltage base) | Float
2635 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLIMHIGHNORM | High normal voltage limit (configurable voltage base) | Float
2636 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADVLIMHIGHSTAB | Stability voltage high limit | Float
2637 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLIMLOWEMERG | Low normal voltage limit (configurable voltage base) | Float
2638 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLIMLOWNORM | Low emergency voltage limit (configurable voltage base) | Float
2639 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.LOADVLIMLOWSTAB | Stability voltage low limit | Float
2640 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLMTMANHIGH | High voltage limit override | Float
2641 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.LOADVLMTMANLOW | Low voltage limit override | Float
2642 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.MANENTRYLOAD | Whether the load has manual entry | Boolean
2643 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NAME | Object name | String |  |  |  | DNMOBJ
2644 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2645 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2646 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.NONCONFORMINGLOAD | Flag indicating a non-conforming load | String
2647 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2648 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NUMCUST | Customer count. | Integer |  |  |  | LOAD
2649 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NUMDRCUSTOMER | The number of customers participating in demand response program | Integer |  |  |  | LOAD
2650 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NUMGENCUSTOMER | The number of customers that have generation | Integer |  |  |  | LOAD
2651 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NUMREGDT | The number of regular day types | Integer |  |  |  | LOAD
2652 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.NUMSTBIN | The total number of historical data bins for study mode. | Integer |  |  |  | LOAD
2653 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.PFCOMPTIME | Latest power flow solution time | String |  |  |  | DMSCOMP
2654 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PNOMA | Nominal phase A real power demand | Float |  | kW | kW | LOAD
2655 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PNOMB | Nominal phase B real power demand | Float |  | kW | kW | LOAD
2656 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PNOMC | Nominal phase C real power demand | Float |  | kW | kW | LOAD
2657 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.PQFLOWA | Phase A output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
2658 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.PQFLOWB | Phase B output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
2659 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.PQFLOWC | Phase C output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
2660 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PRIMCONN | Composite flag (mask) | Integer |  |  |  | LOAD
2661 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PRIMMETLOAD | Flag indicating load is a primary meter load (true = primary) | Boolean
2662 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.PRMETERLOADAMPA | Phase A current | Float |  | Amps | Amps
2663 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.PRMETERLOADAMPB | Phase B current | Float |  | Amps | Amps
2664 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.PRMETERLOADAMPC | Phase C current | Float |  | Amps | Amps
2665 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.PRMETERLOADKVA | Total connected load value (kVA) | Float
2666 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.QNOMA | Nominal phase A reactive power demand | Float |  | kW | kW | LOAD
2667 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.QNOMB | Nominal phase B reactive power demand | Float |  | kW | kW | LOAD
2668 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.QNOMC | Nominal phase C reactive power demand | Float |  | kW | kW | LOAD
2669 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.SERVCNTR.NAME | Service center name | String
2670 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEANA | From end phase A voltage (magnitude on configurable voltage base and angle) for analyst pop-up. | Float
2671 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEANB | From end phase B voltage (magnitude on configurable voltage base and angle) for analyst pop-up. | Float
2672 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEANC | From end phase C voltage (magnitude on configurable voltage base and angle) for analyst pop-up. | Float
2673 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEOPA | From end phase A voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
2674 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEOPB | From end phase B voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
2675 | DNOM Component | Energy Resource | ENERGYRES |  | LOAD.SERVICEVOLTANDANGLEOPC | From end phase C voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
2676 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.SHUNTCONNECTION | Connection type (Delta, Grounded Wye, or Ungrounded Wye) | String |  |  |  | DMSSHUNT
2677 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.SHUNTPHASING | Load phasing information | String |  |  |  | DMSSHUNT
2678 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.STATIONNAME | Nominal station name | String |  |  |  | TOPOCOMP
2679 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.STDELTAC | The load delta iteration counter | Integer |  |  |  | LOAD
2680 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.STDELTAP | The values of the schedule correction factors for power. | String |  |  |  | LOAD
2681 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.STDELTAQ | The values of the schedule correction factors for reactive power. | String |  |  |  | LOAD
2682 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.SUPPLIER | Energy supplier | Integer |  |  |  | LOAD
2683 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.SUSPECTLDA | Phase A voltage information if the load DPF result is suspect | Float
2684 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.SUSPECTLDB | Phase B voltage information if the load DPF result is suspect | Float
2685 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.SUSPECTLDC | Phase C voltage information if the load DPF result is suspect | Float
2686 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.SUSPECTLOAD | Whether the load is suspect | Boolean
2687 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.TYPE | Type of the load | Integer |  |  |  | LOAD
2688 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEANA | Load phase A voltage (magnitude on configurable voltage base and angle in degrees) | Float |  | Volt | Volt | BRNCHSHUNT
2689 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEANB | Load phase B voltage (magnitude on configurable voltage base and angle in degrees) | Float |  | Volt | Volt | BRNCHSHUNT
2690 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEANC | Load phase C voltage (magnitude on configurable voltage base and angle in degrees) | Float |  | Volt | Volt | BRNCHSHUNT
2691 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEOPA | Phase A voltage (magnitude on configurable voltage base and no angle) | Float |  | Volt | Volt | BRNCHSHUNT
2692 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEOPB | Phase B voltage (magnitude on configurable voltage base and no angle) | Float |  | Volt | Volt | BRNCHSHUNT
2693 | DNOM Component | Energy Resource | ENERGYRES | output | LOAD.VOLTANDANGLEOPC | Phase C voltage (magnitude on configurable voltage base and no angle) | Float |  | Volt | Volt | BRNCHSHUNT
2694 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD.WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
2695 | DNOM Component | Energy Resource | ENERGYRES | input | GROUNDED | Flag indicating if the energy resource is grounded. | Boolean
2696 | DNOM Component | Energy Resource | ENERGYRES | input | HASENERGYRESSTG | Specifies whether the battery energy resource has a storage object modeled | Boolean
2697 | DNOM Component | Energy Resource | ENERGYRES | input | HASSCADASOC | Specifies whether the battery energy resource has a SCADA state of charge (SOC) measurement | Boolean
2698 | DNOM Component | Energy Resource | ENERGYRES | input | ID | Object unique ID | String |  |  |  | DNMOBJ
2699 | DNOM Component | Energy Resource | ENERGYRES | input | INVERTERID | The ID of the associated inverter | String
2700 | DNOM Component | Energy Resource | ENERGYRES | input | ISDERGATEWAYCONTROLLED | Specifies whether the DER is controlled by the 2030.5 Gateway | Boolean
2701 | DNOM Component | Energy Resource | ENERGYRES | input | KVA | Energy resource rating. | Float |  | kVA | kVA
2702 | DNOM Component | Energy Resource | ENERGYRES | input | LASTDISCREASONTEXT | The reason for the last disconnection: - "--" (for currently connected energy resources) - High Voltage Out of Range - Low Voltage Out of Range - High Frequency Out of Range - Low Frequency Out of Range - Manual Operation - SCADA Operation | String
2703 | DNOM Component | Energy Resource | ENERGYRES | input | LASTDISCRSN | The reason for the last disconnection: 0 = Unknown (connected now) 1 = High Voltage Out of Range 2 = High Frequency Out of Range 3= Manual Operation 4 = SCADA Operation 5 = Low Voltage Out of Range 6 = Low Frequency Out of Range | String
2704 | DNOM Component | Energy Resource | ENERGYRES | input | LASTDISCTIME | The time when the last disconnection occurred | String
2705 | DNOM Component | Energy Resource | ENERGYRES | input | LOAD | Associated energy resource load | String
2706 | DNOM Component | Energy Resource | ENERGYRES | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
2707 | DNOM Component | Energy Resource | ENERGYRES |  | LVMCONTROLTYPE | LVM control type (0 = VoltageControl = 0, 1 = VarControl, 2 = PowerFactorControl) | Integer
2708 | DNOM Component | Energy Resource | ENERGYRES | input | MANPTARGET | Manually entered real power target value (kW). | Float
2709 | DNOM Component | Energy Resource | ENERGYRES | input | MANQTARGET | The manual reactive power target of the energy resource. | Float
2710 | DNOM Component | Energy Resource | ENERGYRES | output | MANUALEXCLUSIONFLAG | Flag indicating that the device is manually excluded for LVM | Boolean
2711 | DNOM Component | Energy Resource | ENERGYRES | input | MANVTARGET | Manually entered voltage target value (per unit). | Float
2712 | DNOM Component | Energy Resource | ENERGYRES | input | MAXSOC | The maximum state of charge (or nominal capacity), which is the maximum amount of charge that can be stored in the device | Float |  | kWh | kWh
2713 | DNOM Component | Energy Resource | ENERGYRES | input | MINSOC | Charge level below which the device should never be drawn | Float |  | kWh | kWh
2714 | DNOM Component | Energy Resource | ENERGYRES | input | MODELKVA | Size of the energy resource in kVA | Boolean |  | kVA | kVA
2715 | DNOM Component | Energy Resource | ENERGYRES | input | NAME | Display name. | String |  |  |  | DNMOBJ
2716 | DNOM Component | Energy Resource | ENERGYRES | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2717 | DNOM Component | Energy Resource | ENERGYRES | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2718 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
2719 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2720 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2721 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2722 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2723 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2724 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2725 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2726 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2727 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2728 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2729 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2730 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2731 | DNOM Component | Energy Resource | ENERGYRES | input | NOMFEED | The nominal feeder of the energy resource | String
2732 | DNOM Component | Energy Resource | ENERGYRES | input | NORMDEENER | Normally denergized | Boolean
2733 | DNOM Component | Energy Resource | ENERGYRES | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2734 | DNOM Component | Energy Resource | ENERGYRES | input | OWNERSHIP | Energy Resource Ownership. 0 = Unknown 1 = Customer Owned, Customer Maintained 2 = Customer Owned, Utility Maintained 3 = Utility Owned, Utility Maintained | Integer
2735 | DNOM Component | Energy Resource | ENERGYRES | input | PGENMAX | Maximum real power output. | Float |  | kW | kW
2736 | DNOM Component | Energy Resource | ENERGYRES | input | PGENMIN | Minimum real power output. | Float |  | kW | kW
2737 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
2738 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2739 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2740 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2741 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2742 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2743 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2744 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2745 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2746 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2747 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2748 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2749 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2750 | DNOM Component | Energy Resource | ENERGYRES | input | PHSENSE | Phases Measured. | Integer
2751 | DNOM Component | Energy Resource | ENERGYRES | input | PLANNEDRESTORATIONTIME | Planned restoration time after re-energization of the feeder (seconds). | Integer |  | seconds
2752 | DNOM Component | Energy Resource | ENERGYRES | input | POUTPUTMAX | Maximum real power output. | Float |  | KW | KW
2753 | DNOM Component | Energy Resource | ENERGYRES | input | POUTPUTMIN | Minimum real power output. | Float |  | KW | KW
2754 | DNOM Component | Energy Resource | ENERGYRES | input | PSCHED | Real power schedule name | String
2755 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
2756 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
2757 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
2758 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
2759 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
2760 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2761 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2762 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2763 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
2764 | DNOM Component | Energy Resource | ENERGYRES | input | PTARGET | Nominal real power target for an energy resource | Float |  | kW | kW
2765 | DNOM Component | Energy Resource | ENERGYRES | input | QGENMAX | The maximum reactive power output. | Float |  | kVAR | kVAR
2766 | DNOM Component | Energy Resource | ENERGYRES | input | QGENMIN | The minimum reactive power output. | Float |  | kVAR | kVAR
2767 | DNOM Component | Energy Resource | ENERGYRES | input | QOUTPUTMAX | Maximum reactive power output. | Float |  | KVAR | KVAR
2768 | DNOM Component | Energy Resource | ENERGYRES | input | QOUTPUTMIN | Minimum reactive power output. | Float |  | KVAR | KVAR
2769 | DNOM Component | Energy Resource | ENERGYRES | input | QSCHED | Reactive power schedule name | String
2770 | DNOM Component | Energy Resource | ENERGYRES | input | QTARGET | Nominal reactive power target for an energy resource | Float |  | kVAR | kVAR
2771 | DNOM Component | Energy Resource | ENERGYRES | input | REACTIVEPOWERCONTROLFLAG | Flag indicating that the reactive power output can be controlled. | Boolean
2772 | DNOM Component | Energy Resource | ENERGYRES | input | REALPOWERCONTROLFLAG | Flag indicating that the real power output can be controlled. | Boolean
2773 | DNOM Component | Energy Resource | ENERGYRES | input | REGNODE | Regulation node. | String
2774 | DNOM Component | Energy Resource | ENERGYRES | input | RGROUND | Grounding resistance (ohms). | Float
2775 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
2776 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2777 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2778 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2779 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2780 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2781 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2782 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2783 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2784 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2785 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2786 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2787 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2788 | DNOM Component | Energy Resource | ENERGYRES | input | SCHEDULES | DER schedules | String
2789 | DNOM Component | Energy Resource | ENERGYRES | input | SERVCNTR | Service center. | String
2790 | DNOM Component | Energy Resource | ENERGYRES | input | SLACKBUS | Flag indicating whether the generator is a slack bus. | Boolean
2791 | DNOM Component | Energy Resource | ENERGYRES | input | VARSUPPORTFLAG | Flag indicating that the device can provide VAR support. | Boolean
2792 | DNOM Component | Energy Resource | ENERGYRES | input | VMAXSEP | Maximum voltage before separation from the network (per unit). | Float
2793 | DNOM Component | Energy Resource | ENERGYRES | input | VMINSEP | Minimum voltage before separation from the network (per unit). | Float
2794 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ALTNAME | Alternate name of the energy resource | String |  |  |  | ENERGYRES
2795 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2796 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.CONTYPE | Connection type (1 - Not Set, 1 - Induction, 2 - DFIG - Doubly Fed Induction Generator, 3 - Inverter Coupled) | Enumeration |  |  |  | ENERGYRES
2797 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.DEVTYPE | Device type (0 - Not Set, 1 - Wind, 2 - Solar,3 - Micro_Turbine, 4 - Fuel_Cell, 5 - Battery_Storage, 6 - Gas, 7 - Biomass, 8 - Others) | Enumeration |  |  |  | ENERGYRES
2798 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2799 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2800 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ENERGYRESBITMSK | Energy resource bitmask | Integer |  |  |  | ENERGYRES
2801 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ENERGYRESHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set | Boolean |  |  |  | ENERGYRES
2802 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ENERGYRESHASQTARGETOVERRIDE | Indicates whether the energy resource has a manual Q target | Boolean |  |  |  | ENERGYRES
2803 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ENERGYRESHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set. | Boolean |  |  |  | ENERGYRES
2804 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ENERGYRESNOMVOLT | Nominal voltage of the energy resource | String |  |  |  | ENERGYRES
2805 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.EXITEMODE | Energy resource excitation mode (0 - NotSet, 1 - ConstantV, 2 - ConstantQ, 3 - ConstantPF) | Enumeration |  |  |  | ENERGYRES
2806 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
2807 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.GENTYPE | The type of the generator (PV or PQ) | Integer |  |  |  | ENERGYRES
2808 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
2809 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
2810 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.MANPTARGET | Manually entered real power target value | Float |  | kW | kW | ENERGYRES
2811 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.MANQTARGET | The manual reactive power target of the energy resource | Float |  |  |  | ENERGYRES
2812 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.MANVTARGET | Manually entered voltage target value | Float |  | p.u. | p.u. | ENERGYRES
2813 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.NAME | Name of the object | String |  |  |  | DNMOBJ
2814 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2815 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
2816 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.NORMDEENER | Flag indicating that the energy resource is normally de-energized | Boolean |  |  |  | ENERGYRES
2817 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
2818 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.PHSENSE | Phases measured | Integer |  |  |  | ENERGYRES
2819 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.RGROUND | Grounding resistance | Float |  | Ohms | Ohms | ENERGYRES
2820 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.SLACKBUS | Flag indicating whether the energy resource is a slack bus | Boolean |  |  |  | ENERGYRES
2821 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.VMAXSEP | Maximum voltage before separation from the network (per unit). | Float |  |  |  | ENERGYRES
2822 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.VMINSEP | Minimum voltage before separation from the network (per unit). | Float |  |  |  | ENERGYRES
2823 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.VREGLL | Indicates whether the line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation) | Boolean |  |  |  | ENERGYRES
2824 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
2825 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES.XGROUND | Grounding reactance | Float |  | Ohms | Ohms | ENERGYRES
2826 | DNOM Component | Energy Resource | ENERGYRES | input | VOLTAGEBASE | Voltage base value. | Float |  | V | V
2827 | DNOM Component | Energy Resource | ENERGYRES | input | VOLTUNIT | Specifies whether voltage units are defined in the station externals file. The following values are supported: -1 = Not defined (default in DNOM) 0 = False 1 = True | Integer |  | enumeration | enumeration
2828 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
2829 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2830 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2831 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2832 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2833 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2834 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2835 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2836 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2837 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2838 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2839 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2840 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2841 | DNOM Component | Energy Resource | ENERGYRES | input | VREGLL | Whether line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation). | Boolean
2842 | DNOM Component | Energy Resource | ENERGYRES | input | VSCHED | Associated voltage schedule | String
2843 | DNOM Component | Energy Resource | ENERGYRES | input | VTARGET | Nominal voltage target (percent) for an energy resource | Float |  | % | %
2844 | DNOM Component | Energy Resource | ENERGYRES | input | WYE | Flag indicating if the generator is wye connected. | Boolean
2845 | DNOM Component | Energy Resource | ENERGYRES | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
2846 | DNOM Component | Energy Resource | ENERGYRES | input | XGROUND | Grounding reactance (ohms). | Float
2847 | DNOM Component | Energy Resource | ENERGYRES | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
2848 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESPROGRAM | Pointer to the energy resource program | String
2849 | DNOM Component | Energy Resource | ENERGYRES | input | ENGYRESENERGYRESPROGRAM | Energy resource enrolled program. | String
2850 | DNOM Component | Energy Resource | ENERGYRES | input | PROGRAMENROLLMENT | Program enrollment mask. | Integer64 |  | #N/A | #N/A
2851 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERTARGETTYPE | The real power target type (name) | String
2852 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERTARGETTYPE | The reactive power target type (name) | String
2853 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERXVALUE | The real power target X value | Float |  | kW | kW
2854 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERXVALUE | The reactive power target X value | Float |  | kVAR | kVAR
2855 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERXUNIT | The real power target X value unit | String
2856 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERXUNIT | The reactive power target X value unit | String
2857 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERYVALUE | The real power target Y value | Float |  | kW | kW
2858 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERYVALUE | The reactive power target Y value | Float |  | kVAR | kVAR
2859 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERYUNIT | The real power target Y value unit | String
2860 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERYUNIT | The reactive power target Y value unit | String
2861 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERSCHEDULEPOINT1 | The real power schedule point 1 X/Y values. | Float |  | kW | kW
2862 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREALPOWERSCHEDULEPOINT2 | The real power schedule point 2 X/Y values. | Float |  | kW | kW
2863 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERSCHEDULEPOINT1 | The reactuve power schedule point 1 X/Y values. | Float |  | kVAR | kVAR
2864 | DNOM Component | Energy Resource | ENERGYRES | input | ENERGYRESREACTIVEPOWERSCHEDULEPOINT2 | The reactive power schedule point 2 X/Y values. | Float |  | kVAR | kVAR
2865 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.ID | ID of the schedule | String |  |  |  | DNMOBJ
2866 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
2867 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
2868 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
2869 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
2870 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
2871 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
2872 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
2873 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
2874 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
2875 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
2876 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.YUNITONE | Y1 axis units | String |  |  |  | SCHED
2877 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
2878 | DNOM Component | Energy Resource | ENERGYRES | input | PWRTFNAME | The name of the associated power transformer | String
2879 | DNOM Component | Energy Resource 2030.5 Gateway | ENERGYRESGATEWAY | input | AGGREGATIONGROUPNAME | Name of the associated aggregation group if the device is managed under an aggregation group. | String
2880 | DNOM Component | Energy Resource 2030.5 Gateway | ENERGYRESGATEWAY | input | AGGREGATIONMANAGEDFLAG | Flag indicating that the device is managed under an aggregation group (true = managed in aggregation group) | Boolean
2881 | DNOM Component | Energy Resource 2030.5 Gateway | ENERGYRESGATEWAY | input | COMMUNICATIONID | Communication ID | String
2882 | DNOM Component | Energy Resource 2030.5 Gateway | ENERGYRESGATEWAY | input | LIFECYCLESTATUS | Lifecycle status | Integer
2883 | DNOM Component Placement | Energy Resource Label Placement | ENERGYRESLBPL | input | ENERGYRES | Pointer to the associated energy resource | String
2884 | Global Object | Energy Resource Model | ENERGYRESMOD |  | ALLOWLVRT | A flag indicating that low voltage ride-through is enabled (deprecated, use CONFAULTCURR instead) | Boolean
2885 | Global Object | Energy Resource Model | ENERGYRESMOD | input | CAPCURVESCHED | Pointer to the capability curve schedule | String
2886 | Global Object | Energy Resource Model | ENERGYRESMOD |  | CONFAULTCURR | A flag indicating that energy resource will contribute to fault current during SSC or PRV (used instead of ALLOWLVRT) | Boolean
2887 | Global Object | Energy Resource Model | ENERGYRESMOD | input | HIGHVOLTRANGES | High voltage value (per unit V) | Float | DPF | p.u. | p.u.
2888 | Global Object | Energy Resource Model | ENERGYRESMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
2889 | Global Object | Energy Resource Model | ENERGYRESMOD | input | KVA | Generator rating | Float
2890 | Global Object | Energy Resource Model | ENERGYRESMOD | input | LOWVOLTRANGES | Low voltage value (per unit V) | Float | DPF | p.u. | p.u.
2891 | Global Object | Energy Resource Model | ENERGYRESMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
2892 | Global Object | Energy Resource Model | ENERGYRESMOD | input | NUMOPSCHEDS | Number of operation schedules | String
2893 | Global Object | Energy Resource Model | ENERGYRESMOD | input | NUMSCVOLTAGERANGES | The number of voltage ranges and their associated fault current level | Integer | DPF
2894 | Global Object | Energy Resource Model | ENERGYRESMOD | input | OPSCHEDS | Array of pointers to statically defined operating schedules | String
2895 | Global Object | Energy Resource Model | ENERGYRESMOD | input | PGENMAX | Maximum real power output | Float
2896 | Global Object | Energy Resource Model | ENERGYRESMOD | input | PGENMIN | Minimum real power output | Float
2897 | Global Object | Energy Resource Model | ENERGYRESMOD | input | PLANNEDRESTORATIONTIME | Planned restoration time after re-energization of the feeder (seconds). | Integer |  | seconds
2898 | Global Object | Energy Resource Model | ENERGYRESMOD | input | POUTCAPCURVESCHED | Real power output capability curve schedule | String
2899 | Global Object | Energy Resource Model | ENERGYRESMOD | input | QGENMAX | The maximum reactive power output | Float
2900 | Global Object | Energy Resource Model | ENERGYRESMOD | input | QGENMIN | The minimum reactive power output | Float
2901 | Global Object | Energy Resource Model | ENERGYRESMOD | input | QOUTCAPCURVESCHED | Reactive power output capability curve schedule | String
2902 | Global Object | Energy Resource Model | ENERGYRESMOD | input | R2 | Second sequence resistance | Float
2903 | Global Object | Energy Resource Model | ENERGYRESMOD | input | RSC | Short circuit resistance | Float
2904 | Global Object | Energy Resource Model | ENERGYRESMOD | input | RZERO | Zero sequence resistance | Float
2905 | Global Object | Energy Resource Model | ENERGYRESMOD | input | SCCURRENTLEVELS | Fault current as a rated multiplier of the rated output | Float | DPF
2906 | Global Object | Energy Resource Model | ENERGYRESMOD | input | SWCOST | The operational cost of switching on/off a generator | Float
2907 | Global Object | Energy Resource Model | ENERGYRESMOD | input | VHIGHLIMIT | High voltage limit | Float
2908 | Global Object | Energy Resource Model | ENERGYRESMOD | input | VLOWLIMIT | Low voltage limit | Float
2909 | Global Object | Energy Resource Model | ENERGYRESMOD | input | VOLTAGEBASE | Voltage base value | Float
2910 | Global Object | Energy Resource Model | ENERGYRESMOD | input | VOLTUNIT | Enumerated flag indicating the voltage units that should be used. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer
2911 | Global Object | Energy Resource Model | ENERGYRESMOD | input | X2 | Second sequence reactance | Float
2912 | Global Object | Energy Resource Model | ENERGYRESMOD | input | XSC | Short circuit reactance | Float
2913 | Global Object | Energy Resource Model | ENERGYRESMOD | input | XZERO | Zero sequence reactance | Float
2914 | DNOM Component | Energy Resource Program Definition | ENERGYRESPROGRAMDEF | input | PROGRAMNAME | Program name | String
2915 | DNOM Component | Energy Resource Program Definition | ENERGYRESPROGRAMDEF | input | ENROLLMENT | Integer used for associating one or more program enrollments (represented with a 64 bit integer). Each program enrollment is represented by an integer bit (0/1 - 63), to correspond to an Energy Resource Program object defined in the global.csv file. | Integer
2916 | DNOM Component | Energy Resource Program Definition | ENERGYRESPROGRAMDEF | input | PROGRAMTYPE | Program type | String
2917 | DNOM Component | Energy Resource Storage Device | ENERGYRESSTG | input | ENERGYRATING | The useable capacity of the storage device | Float |  | kWh | kWh
2918 | DNOM Component | Energy Resource Storage Device | ENERGYRESSTG | input | MAXSOC | The maximum state of charge (or nominal capacity), which is the maximum amount of charge that can be stored in the device. The maximum state of charge (SoC) of a DER storage device is specified as a fraction relative to the device's capacity in kWh (for example, 0.9 = 90%). | Float
2919 | DNOM Component | Energy Resource Storage Device | ENERGYRESSTG | input | MINSOC | Charge level below which the device should never be drawn, specified as a fraction relative to the total device capacity in kWh (for example, 0.4 = 40%). | Float
2920 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.ADDRESS | The feeder address | String |  |  |  | FDR
2921 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.ALTERNATENAME | Alternate name of the looped feeder | String |  |  |  | FDR
2922 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2923 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
2924 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.DEFCOLOR | Default color | Integer |  |  |  | FDR
2925 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
2926 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2927 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2928 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
2929 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
2930 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
2931 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
2932 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
2933 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.ID | Unique and persistent ID of the looped feeder | String |  |  |  | DNMOBJ
2934 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
2935 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
2936 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
2937 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
2938 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
2939 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
2940 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
2941 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
2942 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
2943 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
2944 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
2945 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NAME | Name of the looped feeder | String |  |  |  | DNMOBJ
2946 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
2947 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
2948 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
2949 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String |  |  |  | FDR
2950 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
2951 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
2952 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
2953 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
2954 | Virtual Object | Energizing Source | ENGZSOURCE | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
2955 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.ADDRESS | The feeder address | String |  |  |  | FDR
2956 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.ALTERNATENAME | Alternate name of the feeder | String |  |  |  | FDR
2957 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
2958 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
2959 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.DEFCOLOR | Default color | Integer |  |  |  | FDR
2960 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
2961 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
2962 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
2963 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
2964 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
2965 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
2966 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
2967 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
2968 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
2969 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
2970 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
2971 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
2972 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
2973 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
2974 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
2975 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
2976 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
2977 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
2978 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
2979 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
2980 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.NAME | Name of the object | String |  |  |  | DNMOBJ
2981 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
2982 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
2983 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
2984 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
2985 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
2986 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
2987 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
2988 | DNOM Component | Enumeration Table | ENUTAB |  | DESCRIPTION | Description string of the type value | String
2989 | DNOM Component | Enumeration Table | ENUTAB |  | DEVICE | Device type | String
2990 | DNOM Component | Enumeration Table | ENUTAB |  | ID | Device ID | String
2991 | DNOM Component | Enumeration Table | ENUTAB |  | NAME | Device name | String
2992 | DNOM Component | Enumeration Table | ENUTAB |  | TYPEVALUE | Type value. | Integer
2993 | DNOM Component | External Branch | EXTBRC |  | BRANCHID | ID of the branch | String
2994 | DNOM Component | External Branch | EXTBRC |  | COMBINEDFAULTPHASES | Fault phases identified by manual and telemetered fault indicators. Used for debugging the external branch fault halo issues. | String
2995 | DNOM Component | External Branch | EXTBRC |  | COMBINEDHALOINVALID | Indicates whether manual and telemetered fault indicator halos are invalid. Used for debugging the external branch fault halo issues. | Boolean
2996 | DNOM Component | External Branch | EXTBRC |  | EXTSBNME | External substation name | String
2997 | DNOM Component | External Branch | EXTBRC |  | FRTONODE | From and to nodes | String
2998 | DNOM Component | External Branch | EXTBRC | input | ID | Object unique ID | String |  |  |  | DNMOBJ
2999 | DNOM Component | External Branch | EXTBRC |  | MANUALFAULTPHASES | Fault phases identified by manual fault indicators. Used for debugging the external branch fault halo issues. | String
3000 | DNOM Component | External Branch | EXTBRC |  | MANUALHALOINVALID | Indicates whether manual fault indicator halos are invalid. Used for debugging the external branch fault halo issues. | Boolean
3001 | DNOM Component | External Branch | EXTBRC | input | NAME | Object name | String |  |  |  | DNMOBJ
3002 | DNOM Component | External Branch | EXTBRC |  | TELEMFAULTPHASES | Fault phases identified by telemetered fault indicators. Used for debugging the external branch fault halo issues. | String
3003 | DNOM Component | External Branch | EXTBRC |  | TELEMHALOINVALID | Indicates whether telemetered fault indicator halos are invalid. Used for debugging the external branch fault halo issues. | Boolean
3004 | DNOM Component Placement | Feeder Label Placement | FDLBPL | input | FEEDER | Pointer to the associated feeder | String
3005 | DNOM Component Placement | Feeder Polygon Placement | FDPOPL | input | FEEDER | Pointer to the associated feeder | String
3006 | DNOM Component | Feeder | FDR | input | _KEY | Field used for manual entry | String
3007 | DNOM Component | Feeder | FDR | output | ACTIVEDEMANDDIFF | Total real power demand difference between calculated and measured values | String |  | MW | MW
3008 | DNOM Component | Feeder | FDR | input | ADDRESS | The feeder address | String |  |  |  | NDPFST
3009 | DNOM Component | Feeder | FDR |  | AFRAUTOENABLEDTEXT | AFR auto enabled text | String
3010 | DNOM Component | Feeder | FDR | input | AFRPROFORMINDEX | The AFR problem formulation index | Integer
3011 | DNOM Component | Feeder | FDR | input | AFRPROFORMNAME | The AFR problem formulation name | Integer
3012 | DNOM Component | Feeder | FDR | output | AGGREGATIONACTIVEDEMAND | Total DPF calculated real power demand at the load side (secondary) | String | DPF | MW | MW
3013 | DNOM Component | Feeder | FDR | output | AGGREGATIONACTIVEDEMANDHIGHLOW | Total DPF calculated real power demand at the source side (primary) and at the load side (secondary) | String | DPF | MW | MW
3014 | DNOM Component | Feeder | FDR | output | AGGREGATIONACTIVELOSS | Total DPF calculated real power loss | String | DPF | MVAR | MVAR
3015 | DNOM Component | Feeder | FDR | output | AGGREGATIONCAPACITORMVAROFFLINE | The calculated offline capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. As opposed to the calculation for online capacitor reactive power, the offline calculation only includes disconnected remote capacitors. | String | MVAR | MVAR | MVAR
3016 | DNOM Component | Feeder | FDR | output | AGGREGATIONCAPACITORMVARONLINE | The calculated online capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. This includes connected fixed and remote capacitors as well as all local capacitors. | String | MVAR | MVAR | MVAR
3017 | DNOM Component | Feeder | FDR | output | AGGREGATIONCAPACITORMVARTOTAL | The total capacitor reactive power, which is the sum of the online and offline capacitor reactive power for each aggregation object. | String | MVAR | MVAR | MVAR
3018 | DNOM Component | Feeder | FDR | output | AGGREGATIONDERACTIVEDEMAND | Calculated DER/DG real power injection in MW | Float | DPF | MW | MW
3019 | DNOM Component | Feeder | FDR | output | AGGREGATIONDERREACTIVEDEMAND | Calculated DER/DG reactive power injection in MVAR | Float | DPF | MVAR | MVAR
3020 | DNOM Component | Feeder | FDR | output | AGGREGATIONNATIVEACTIVEDEMAND | Calculated native real power demand in MW | Float | DPF | MW | MW
3021 | DNOM Component | Feeder | FDR | output | AGGREGATIONNATIVEREACTIVEDEMAND | Calculated native reactive power demand in MVAR | Float | DPF | MVAR | MVAR
3022 | DNOM Component | Feeder | FDR | output | AGGREGATIONPOWERFACTOR | Calculated power factor at the load side | String | DPF
3023 | DNOM Component | Feeder | FDR | output | AGGREGATIONPOWERFACTORHIGHLOW | Calculated power factor at the source side (primary) and at the load side (secondary) | String | DPF
3024 | DNOM Component | Feeder | FDR | output | AGGREGATIONREACTIVEDEMAND | Total DPF calculated reactive power demand at the load side (secondary) | String | DPF | MVAR | MVAR
3025 | DNOM Component | Feeder | FDR | output | AGGREGATIONREACTIVEDEMANDHIGHLOW | Total DPF calculated reactive power demand at the source side (primary) and at the load side (secondary) | String | DPF | MVAR | MVAR
3026 | DNOM Component | Feeder | FDR | output | AGGREGATIONREACTIVELOSS | Total DPF calculated reactive power loss | String | DPF | MVAR | MVAR
3027 | DNOM Component | Feeder | FDR | input | ALTERNATENAME | Feeder Alternate Name | String
3028 | DNOM Component | Feeder | FDR | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
3029 | DNOM Component | Feeder | FDR | input | AREAIND | Integer index into station permission area list | Integer |  |  |  | DNMOBJ
3030 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGECALCAMPWEIGHTALLBUS | Weighted calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
3031 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGECALCAMPWEIGHTMVBUS | Weighted calculated average voltage in per unit. Only station MV buses are accounted. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
3032 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGECALCNOWEIGHTALLBUS | Calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. | Float | DPF | p.u. | p.u.
3033 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGECALCNOWEIGHTMVBUS | Calculated average voltage in per unit. Only station MV buses are accounted. | Float | DPF | p.u. | p.u.
3034 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
3035 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGEMEASAMPWEIGHTMVBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
3036 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGEMEASNOWEIGHTALLBUS | Weighted measured average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
3037 | DNOM Component | Feeder | FDR | output | AVRAGEVOLTAGEMEASNOWEIGHTMVBUS | Measured average voltage, station bus only, in per unit | Float | DPF | p.u. | p.u.
3038 | DNOM Component | Feeder | FDR |  | BACKFEED | Incicates if backfeed conditions exist | Boolean
3039 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCFLOWA | Last recorded Phase A flow at feeder head (amps). | Float | DPF | Amps | Amps
3040 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCFLOWB | Last recorded Phase B flow at feeder head (amps). | Float | DPF | Amps | Amps
3041 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCFLOWC | Last recorded Phase C flow at feeder head (amps). | Float | DPF | Amps | Amps
3042 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCPA | Calculated phase A real power (kW) at feeder head | Float | DPF | kW | kW
3043 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCPB | Calculated phase B real power (kW) at feeder head | Float | DPF | kW | kW
3044 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCPC | Calculated phase C real power (kW) at feeder head | Float | DPF | kW | kW
3045 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCQA | Calculated phase A reactive flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3046 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCQB | Calculated phase B reactive flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3047 | DNOM Component | Feeder | FDR | output | BLAFEEDCALCQC | Calculated phase C reactive flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3048 | DNOM Component | Feeder | FDR | output | BLAFEEDERERRORCOUNT | Counter for BLA measurement inconsistencies (count is reset to 0 after a model file is loaded) | Integer | BLA | count | count
3049 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASFLOWA | Last recorded measurement (or manual entry) phase A flow at feeder head (amps). | Float | DPF | Amps | Amps
3050 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASFLOWB | Last recorded measurement (or manual entry) phase B flow at feeder head (amps). | Float | DPF | Amps | Amps
3051 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASFLOWC | Last recorded measurement (or manual entry) phase C flow at feeder head (amps). | Float | DPF | Amps | Amps
3052 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSID | ID of the bus | String |  |  |  | NODE
3053 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSNAME | Name of the bus | String |  |  |  | NODE
3054 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVLIMHIGHEMERG | Emergency high voltage limit | Float |  |  |  | NODE
3055 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVLIMHIGHNORM | Normal high voltage limit | Float |  |  |  | NODE
3056 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVLIMLOWEMERG | Emergency low voltage limit | Float |  |  |  | NODE
3057 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVLIMLOWNORM | Normal low voltage limit | Float |  |  |  | NODE
3058 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVOPTEMRGHIGH | Emergency optimization high limit | Float |  |  |  | NODE
3059 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVOPTEMRGLOW | Emergency optimization low limit | Float |  |  |  | NODE
3060 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVOPTNORMHIGH | Normal optimization high limit | Float |  |  |  | NODE
3061 | DNOM Component | Feeder | FDR | input | BREAKERNODE.BUSVOPTNORMLOW | Normal optimization low limit | Float |  |  |  | NODE
3062 | DNOM Component | Feeder | FDR | input | BREAKERNODE.COMPPHASEA | Flag indicating whether phase A exists in the component | Boolean |  |  |  | NODE
3063 | DNOM Component | Feeder | FDR | input | BREAKERNODE.COMPPHASEB | Flag indicating whether phase B exists in the component | Boolean |  |  |  | NODE
3064 | DNOM Component | Feeder | FDR | input | BREAKERNODE.COMPPHASEC | Flag indicating whether phase C exists in the component | Boolean |  |  |  | NODE
3065 | DNOM Component | Feeder | FDR | input | BREAKERNODE.COMPPHASEN | Indicates whether neutral is connected | Boolean |  |  |  | NODE
3066 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VANGLEA | Voltage angle of phase A | Integer |  | Radians | Radians | NODE
3067 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VANGLEB | Voltage angle of phase B | Integer |  | Radians | Radians | NODE
3068 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VANGLEC | Voltage angle of phase B | Integer |  | Radians | Radians | NODE
3069 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VANGLEN | Voltage angle of neutral | Integer |  | Radians | Radians | NODE
3070 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMAGA | Voltage magnitude of phase A | Integer |  | p.u. | p.u. | NODE
3071 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMAGB | Voltage magnitude of phase B | Integer |  | p.u. | p.u. | NODE
3072 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMAGC | Voltage magnitude of phase B | Integer |  | p.u. | p.u. | NODE
3073 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMAGN | Voltage magnitude of neutral | Integer |  | p.u. | p.u. | NODE
3074 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASACTUALPHA | SCADA measured voltage of phase A | String |  |  |  | NODE
3075 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASACTUALPHB | SCADA measured voltage of phase B | String |  |  |  | NODE
3076 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASACTUALPHC | SCADA measured voltage of phase C | String |  |  |  | NODE
3077 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASPHA | Measured voltage of phase A | Float |  | kV | kV | NODE
3078 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASPHB | Measured voltage of phase B | Float |  | kV | kV | NODE
3079 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VMEASPHC | Measured voltage of phase C | Float |  | kV | kV | NODE
3080 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEANA | Connection node calculated voltage and angle of phase A (for Analyst pop-up) | Float |  | kV | kV | NODE
3081 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEANB | Connection node calculated voltage and angle of phase B (for Analyst pop-up) | Float |  | kV | kV | NODE
3082 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEANC | Connection node calculated voltage and angle of phase C (for Analyst pop-up) | Float |  | kV | kV | NODE
3083 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEOPA | Connection node calculated voltage and angle of phase A (for Operator pop-up) | Float |  | kV | kV | NODE
3084 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEOPB | Connection node calculated voltage and angle of phase B (for Operator pop-up) | Float |  | kV | kV | NODE
3085 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTANDANGLEOPC | Connection node calculated voltage and angle of phase C (for Operator pop-up) | Float |  | kV | kV | NODE
3086 | DNOM Component | Feeder | FDR | input | BREAKERNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
3087 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASPA | Measurement phase A flow (kW) at feeder head | Float | DPF | kW | kW
3088 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASPB | Measurement phase B flow (kW) at feeder head | Float | DPF | kW | kW
3089 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASPC | Measurement phase C flow (kW) at feeder head | Float | DPF | kW | kW
3090 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASQA | Measurement phase A flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3091 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASQB | Measurement phase B flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3092 | DNOM Component | Feeder | FDR | output | BLAFEEDMEASQC | Measurement phase C flow (kVAR) at feeder head | Float | DPF | kVAR | kVAR
3093 | DNOM Component | Feeder | FDR | output | BLAFEEDMISMATCHPERCENTA | Difference in measurement and calculated phase A flow at feeder head (percent). | Float | DPF | percent | percent
3094 | DNOM Component | Feeder | FDR | output | BLAFEEDMISMATCHPERCENTB | Difference in measurement and calculated phase B flow at feeder head (percent). | Float | DPF | percent | percent
3095 | DNOM Component | Feeder | FDR | output | BLAFEEDMISMATCHPERCENTC | Difference in measurement and calculated phase C flow at feeder head (percent). | Float | DPF | percent | percent
3096 | DNOM Component | Feeder | FDR | output | BLAFEEDPMISMATCHPERCENTA | Measurement & calculated phase A flow (Amps). | Float
3097 | DNOM Component | Feeder | FDR | output | BLAFEEDPMISMATCHPERCENTB | Measurement & calculated phase B flow (Amps). | Float
3098 | DNOM Component | Feeder | FDR | output | BLAFEEDPMISMATCHPERCENTC | Measurement & calculated phase C flow (Amps). | Float
3099 | DNOM Component | Feeder | FDR | output | BLAFEEDQMISMATCHPERCENTA | Mismatch between feeder head phase A reactive power measurements and calculated value (kVAR) | Float | DPF | kVAR | kVAR
3100 | DNOM Component | Feeder | FDR | output | BLAFEEDQMISMATCHPERCENTB | Mismatch between feeder head phase B reactive power measurements and calculated value (kVAR) | Float | DPF | kVAR | kVAR
3101 | DNOM Component | Feeder | FDR | output | BLAFEEDQMISMATCHPERCENTC | Mismatch between feeder head phase C reactive power measurements and calculated value (kVAR) | Float | DPF | kVAR | kVAR
3102 | DNOM Component | Feeder | FDR | output | BLASTATUSFEEDERP | Real power convergence status (BLA). | Boolean | DPF | #N/A | #N/A
3103 | DNOM Component | Feeder | FDR | output | BLASTATUSFEEDERQ | Reactive power convergence status (BLA). | Boolean | DPF | #N/A | #N/A
3104 | DNOM Component | Feeder | FDR | input | BREAKERNODE | Feeder breaker node. (Optional - if set at modeling side.) | String |  |  |  | NODE
3105 | DNOM Component | Feeder | FDR | input | BRHDFEND | Flow end for the feeder head branches | Integer
3106 | DNOM Component | Feeder | FDR | output | BUSVOLTMISMATCH | Specifies whether bus voltage mismatch exists | Boolean
3107 | DNOM Component | Feeder | FDR |  | DASTATUSMEAS | DA status measurement Id | String
3108 | DNOM Component | Feeder | FDR | input | DECREASABLE | Feeder DER output can be decreased by this number of kW | String |  | kW | kW
3109 | DNOM Component | Feeder | FDR | input | DEFCOLOR | Default color. | Integer
3110 | DNOM Component | Feeder | FDR | input | DERKVAR3PHASE | Reactive power output by the DER | String |  | kVAR | kVAR
3111 | DNOM Component | Feeder | FDR | input | DERKW3PHASE | Real power output by the DER | String |  | kW | kW
3112 | DNOM Component | Feeder | FDR | input | DERPF | DER power factor | String
3113 | DNOM Component | Feeder | FDR | input | EVALNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
3114 | DNOM Component | Feeder | FDR | input | EVALNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
3115 | DNOM Component | Feeder | FDR | input | EVALNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
3116 | DNOM Component | Feeder | FDR | input | EVALNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3117 | DNOM Component | Feeder | FDR | input | EVALNODE.ID | ID of the node | String |  |  |  | DNMOBJ
3118 | DNOM Component | Feeder | FDR | input | EVALNODE.NAME | Feeder Evaluation Head Node Name | String
3119 | DNOM Component | Feeder | FDR | input | EVALNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3120 | DNOM Component | Feeder | FDR | input | EVALNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3121 | DNOM Component | Feeder | FDR | input | EVALNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3122 | DNOM Component | Feeder | FDR | input | EVALNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
3123 | DNOM Component | Feeder | FDR | input | DERPGENMAX | Maximum real power generation by the DERs | String |  | kW | kW
3124 | DNOM Component | Feeder | FDR | input | DERQGENMAX | Maximum reactive power generation by DERs | String |  | KVAR | KVAR
3125 | DNOM Component | Feeder | FDR | input | DERQGENMIN | Minimum reactive power generation by DERs | String |  | KVAR | KVAR
3126 | DNOM Component | Feeder | FDR | output | DISTTFKVARLOSS | Total transformer reactive power loss (not including regulators) | Float | DPF | kVAR | kVAR
3127 | DNOM Component | Feeder | FDR | input | FDPOLYPL.AX | Dynamic array of X coordinates | String |  |  |  | CMBPLS
3128 | DNOM Component | Feeder | FDR | input | FDPOLYPL.AY | Dynamic array of Y coordinates | String |  |  |  | CMBPLS
3129 | DNOM Component | Feeder | FDR | input | FDPOLYPL.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
3130 | DNOM Component | Feeder | FDR | input | FDPOLYPL.NUMVERT | Number of vertices (line or polygon) | String |  |  |  | CMBPLS
3131 | DNOM Component | Feeder | FDR | output | DISTTFKWLOSS | Total transformer real power loss (not including regulators) | Float | DPF | kW | kW
3132 | DNOM Component | Feeder | FDR | input | DNAFAFRENABLED | If dnaf AFR application is enabled in this feeder. | Boolean
3133 | DNOM Component | Feeder | FDR |  | DNAFAUTOENABLEDAPPS | Auto enabling bitmask (all apps) | Integer
3134 | DNOM Component | Feeder | FDR | input | DNAFENABLEDAPPS | If the dnaf applications is enabled in feeder. | Boolean
3135 | DNOM Component | Feeder | FDR | output | DNAFENABLEDVVALARMS | Bitmaks that indicates if the LVM alarm is enabled | Integer
3136 | DNOM Component | Feeder | FDR | input | DNAFFISRENABLED | If dnaf FISR application is enabled in this feeder. | Boolean
3137 | DNOM Component | Feeder | FDR | input | DNAFLVMENABLED | If dnaf LVM application is enabled in this feeder. | Boolean
3138 | DNOM Component | Feeder | FDR | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
3139 | DNOM Component | Feeder | FDR | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3140 | DNOM Component | Feeder | FDR | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3141 | DNOM Component | Feeder | FDR | output | DPFFEEDERSTATUS | DPF solution quality description | Boolean | DPF | #N/A | #N/A
3142 | DNOM Component | Feeder | FDR | input | EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean
3143 | DNOM Component | Feeder | FDR | input | ENABLELVM | Flag of included in LVM optimization | Boolean |  | #NA | #NA
3144 | DNOM Component | Feeder | FDR | input | EVALNODE | Pointer to feeder head node - power flow applications | String
3145 | DNOM Component | Feeder | FDR | output | FAFEEDERSTATUS | PRV solution quality description | Integer | PRV | enumeration | enumeration
3146 | DNOM Component | Feeder | FDR | input | FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit. | Integer
3147 | DNOM Component | Feeder | FDR | input | FAILEDREGLIM | Maximum failed regulating device limit. | Integer
3148 | DNOM Component | Feeder | FDR | input | FDPOLYPL | Pointer to the feeder poly placement | String
3149 | DNOM Component | Feeder | FDR |  | FDRACTLSCALERUSED | Specifies whether the actual scale is used | Boolean
3150 | DNOM Component | Feeder | FDR | input | FDRAREA | The feeder's area name | String
3151 | DNOM Component | Feeder | FDR | input | FDRBREAKERID | Breaker ID | String
3152 | DNOM Component | Feeder | FDR | input | FDRBREAKERNAME | Breaker name | String
3153 | DNOM Component | Feeder | FDR |  | FDRHIGHVOLTID | ID of the device with highest voltage violation | String
3154 | DNOM Component | Feeder | FDR |  | FDRHIGHVOLTVIOL | Highest voltage violation for the feeder | Float
3155 | DNOM Component | Feeder | FDR | output | FDRKVARLOSS | Total instantaneous reactive power loss | Float | DPF | kVAR | kVAR
3156 | DNOM Component | Feeder | FDR | output | FDRKWLOSS | Total instantaneous real power loss | Float | DPF | kW | kW
3157 | DNOM Component | Feeder | FDR |  | FDRLOWVOLTID | ID of the device with lowest voltage violation | String
3158 | DNOM Component | Feeder | FDR |  | FDRLOWVOLTVIOL | Lowest voltage violation for the feeder | Float
3159 | DNOM Component | Feeder | FDR | input | FDRSUBNAME | Associated station name. | String
3160 | DNOM Component | Feeder | FDR | output | FEEDAMPA | Feeder head phase A current (amps). | Float | DPF | amps | amps
3161 | DNOM Component | Feeder | FDR | output | FEEDAMPB | Feeder head phase B current (amps). | Float | DPF | amps | amps
3162 | DNOM Component | Feeder | FDR | output | FEEDAMPC | Feeder head phase C current (amps). | Float | DPF | amps | amps
3163 | DNOM Component | Feeder | FDR | input | FEEDAMPN | Feeder head phase N current (amps). | Float |  | amps | amps
3164 | DNOM Component | Feeder | FDR | output | FEEDAMPPERCENTIMB | Feeder amp percentage imbalance. | Float
3165 | DNOM Component | Feeder | FDR | output | FEEDAVGPERCENTLOADING | Feeder average amp percent loading by three phases. | Float
3166 | DNOM Component | Feeder | FDR | output | FEEDCAPVARINSERVICE | Total capacitor kVAR in service | Float | DPF | kVAR | kVAR
3167 | DNOM Component | Feeder | FDR | output | FEEDCAPVAROUTOFSERVICE | Total capacitor kVAR not in service(nominal) | Float | DPF | kVAR | kVAR
3168 | DNOM Component | Feeder | FDR | output | FEEDCAPVARUNAVAILABLE | Total capacitor kVAR not available(nominal) | Float | DPF | kVAR | kVAR
3169 | DNOM Component | Feeder | FDR | output | FEEDCONNCUST | Total customer count of three phases. | Integer
3170 | DNOM Component | Feeder | FDR | output | FEEDCONNCUSTA | Customer count of phase A. | Integer
3171 | DNOM Component | Feeder | FDR | output | FEEDCONNCUSTB | Customer count of phase B. | Integer
3172 | DNOM Component | Feeder | FDR | output | FEEDCONNCUSTC | Customer count of phase C. | Integer
3173 | DNOM Component | Feeder | FDR | output | FEEDCONNKVA | Total connected load value of three phases (kVA). | Float
3174 | DNOM Component | Feeder | FDR | output | FEEDDISTTFCOPPERLOSSP | Total distribution transformer copper real loss | Float | DPF | Watt | Watt
3175 | DNOM Component | Feeder | FDR | output | FEEDDISTTFCOPPERLOSSQ | Total distribution transformer copper reactive loss - | Float | DPF | VAR | VAR
3176 | DNOM Component | Feeder | FDR | output | FEEDDISTTFCORELOSSP | Total distribution transformer core real loss | Float | DPF | Watt | Watt
3177 | DNOM Component | Feeder | FDR | output | FEEDDISTTFCORELOSSQ | Total distribution transformer core reactive loss | Float | DPF | VAR | VAR
3178 | DNOM Component | Feeder | FDR | input | FEEDERADDRESS | Feeder Address | String
3179 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERAMPA | Feeder breaker phase A current (amps). | Float | DPF | amps | amps
3180 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERAMPB | Feeder breaker phase B current (amps). | Float | DPF | amps | amps
3181 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERAMPC | Feeder breaker phase C current (amps). | Float | DPF | amps | amps
3182 | DNOM Component | Feeder | FDR |  | FEEDERBREAKERAMPN | Feeder breaker phase N current | Float |  | Amps | Amps
3183 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKVARA | Feeder breaker phase A reactive power (kVAR). | Float | DPF | kVAR | kVAR
3184 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKVARB | Feeder breaker phase B reactive power (kVAR). | Float | DPF | kVAR | kVAR
3185 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKVARC | Feeder breaker phase C reactive power (kVAR). | Float | DPF | kVAR | kVAR
3186 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKVARTOTAL | Feeder breaker total reactive power (kVAR). | Float | DPF | kVAR | kVAR
3187 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKWA | Feeder breaker phase A active power (kW). | Float | DPF | kW | kW
3188 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKWB | Feeder breaker phase B active power (kW). | Float | DPF | kW | kW
3189 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKWC | Feeder breaker phase C active power (kW). | Float | DPF | kW | kW
3190 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERKWTOTAL | Feeder breaker total active power (kW). | Float | DPF | kW | kW
3191 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERPF | Feeder breaker power factor. | Float | DPF | #N/A | #N/A
3192 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERPFA | Feeder breaker phase A power factor. | Float | DPF | #N/A | #N/A
3193 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERPFB | Feeder breaker phase B power factor. | Float | DPF | #N/A | #N/A
3194 | DNOM Component | Feeder | FDR | output | FEEDERBREAKERPFC | Feeder breaker phase C power factor. | Float | DPF | #N/A | #N/A
3195 | DNOM Component | Feeder | FDR | output | FEEDERCAPAMARGINVIO | Feeder capacity margin violation existed. | Boolean | DPF | #N/A | #N/A
3196 | DNOM Component | Feeder | FDR |  | FEEDERCURRENTCUSTOMERCOUNT | Current count of customers connected to the feeder | String
3197 | DNOM Component | Feeder | FDR |  | FEEDERCUSTCOUNTMISMATCH | A flag indicating the mismatch between the nominal and current customers connected | Boolean
3198 | DNOM Component | Feeder | FDR | output | FEEDERERRORCTPERBLA | Measurement island error count. | Integer
3199 | DNOM Component | Feeder | FDR | output | FEEDERFLOWOVERLIMITPERCENT | Percent of highest flow over the corresponding limit level | Float | DPF | percent | percent
3200 | DNOM Component | Feeder | FDR | output | FEEDERFLWIMBAL | Highest switch flow imbalance. | Float
3201 | DNOM Component | Feeder | FDR | output | FEEDERGROUNDRETURN | Feeder highest ground return current for breakers and reclosers (in percent). | Float |  | percent | percent
3202 | DNOM Component | Feeder | FDR | input | FEEDERHASMANENTRY | Flag indicating feeder is using a manual entry | Boolean
3203 | DNOM Component | Feeder | FDR | output | FEEDERHEADBRANCH | Associated feeder head branch (including the branch type). | String | NTP | #N/A | #N/A
3204 | DNOM Component | Feeder | FDR | input | FEEDERHEADBRANCHID | Feeder head branch unique ID | String
3205 | DNOM Component | Feeder | FDR | output | FEEDERHIGHESTVOLTOVERPERCENT | Percent of highest voltage over nominal percent | Float | DPF | percent | percent
3206 | DNOM Component | Feeder | FDR | output | FEEDERHIGHLOADDEVICE | Most heavily loaded branch ID | String | DPF
3207 | DNOM Component | Feeder | FDR | output | FEEDERHIGHVOLT | Feeder highest load (in percent). | Float | DPF | percent | percent
3208 | DNOM Component | Feeder | FDR | output | FEEDERLOWESTVOLTBELOWPERCENT | Percent of lowest voltage below norminal percent | Float | DPF | percent | percent
3209 | DNOM Component | Feeder | FDR | output | FEEDERLOWVOLT | Feeder lowest load voltage (in percent). | Float | DPF | percent | percent
3210 | DNOM Component | Feeder | FDR | output | FEEDERNEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
3211 | DNOM Component | Feeder | FDR |  | FEEDERNOMINALCUSTOMERCOUNT | Nominal count of customers connected to the feeder | String
3212 | DNOM Component | Feeder | FDR | output | FEEDERNUMHIGHVOLTVIOLATION | The number of high voltage violations | Integer | DPF
3213 | DNOM Component | Feeder | FDR | output | FEEDERNUMLOWVOLTVIOLATION | The number of low voltage violations | Integer | DPF
3214 | DNOM Component | Feeder | FDR | output | FEEDERNUMOVERLOAD | The number of overloads | Integer | DPF
3215 | DNOM Component | Feeder | FDR | output | FEEDEROVERLOAD | Feeder highest branch flow (in percent). | Float | DPF | percent | percent
3216 | DNOM Component | Feeder | FDR | output | FEEDEROVERLOADLEVEL | Feeder highest branch flow overload level. | Integer | DPF | percent | percent
3217 | DNOM Component | Feeder | FDR | output | FEEDERVLTIMBAL | Feeder highest three-phase load imbalance (in percent). | Float | DPF | percent | percent
3218 | DNOM Component | Feeder | FDR | output | FEEDERVOLTAGE | Nominal feeder voltage. | Float | DPF
3219 | DNOM Component | Feeder | FDR | output | FEEDKVARA | Feeder head phase A reactive power (kVAR). | Float | DPF | kVAR | kVAR
3220 | DNOM Component | Feeder | FDR | output | FEEDKVARB | Feeder head phase B reactive power (kVAR). | Float | DPF | kVAR | kVAR
3221 | DNOM Component | Feeder | FDR | output | FEEDKVARC | Feeder head phase C reactive power (kVAR). | Float | DPF | kVAR | kVAR
3222 | DNOM Component | Feeder | FDR | output | FEEDKVARTOTAL | Feeder head total reactive power (kVAR). | Float | DPF | kVAR | kVAR
3223 | DNOM Component | Feeder | FDR | output | FEEDKVLLA | Voltage magnitude of phase A | Float | DPF | kV | kV
3224 | DNOM Component | Feeder | FDR | output | FEEDKVLLAVG | Average Feeder head voltage magnitude. | Float |  | kV | kV
3225 | DNOM Component | Feeder | FDR | output | FEEDKVLLB | Voltage magnitude of phase B | Float | DPF | kV | kV
3226 | DNOM Component | Feeder | FDR | output | FEEDKVLLC | Voltage magnitude of phase C | Float | DPF | kV | kV
3227 | DNOM Component | Feeder | FDR | output | FEEDKVLLNOM | Feeder actual voltage base (line-to line) | Float | DPF | kV | kV
3228 | DNOM Component | Feeder | FDR | output | FEEDKWA | Feeder head phase A active power (kW). | Float | DPF | kW | kW
3229 | DNOM Component | Feeder | FDR | output | FEEDKWB | Feeder head phase B active power (kW). | Float | DPF | kW | kW
3230 | DNOM Component | Feeder | FDR | output | FEEDKWC | Feeder head phase C active power (kW). | Float | DPF | kW | kW
3231 | DNOM Component | Feeder | FDR | output | FEEDKWLOSSLINES | The lines loss which subtract the distribution transformer and regulator losses from the total feeder loss. | Float
3232 | DNOM Component | Feeder | FDR | output | FEEDKWTOTAL | Feeder head total active power (kW). | Float | DPF | kW | kW
3233 | DNOM Component | Feeder | FDR | input | FEEDMANENTRYAMPSA | A manually entered phase A feeder amp value | Float
3234 | DNOM Component | Feeder | FDR | input | FEEDMANENTRYAMPSB | A manually entered phase B feeder amp value | Float
3235 | DNOM Component | Feeder | FDR | input | FEEDMANENTRYAMPSC | A manually entered phase C feeder amp value | Float
3236 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSS | The greatest kW (real power loss) by three phases. | Float
3237 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSA | The greatest kW (real power loss) by phase A. | Float
3238 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSADEVICE | The id of node which has greatest kW (real power loss) by phase A. | String
3239 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSB | The greatest kW (real power loss) by phase B. | Float
3240 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSBDEVICE | The id of node which has greatest kW (real power loss) by phase B. | String
3241 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSC | The greatest kW (real power loss) by phase C. | Float
3242 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSCDEVICE | The id of node which has greatest kW (real power loss) by phase C. | String
3243 | DNOM Component | Feeder | FDR | output | FEEDMAXKWLOSSDEVICE | The id of node which has greatest kW (real power loss) by three phases. | String
3244 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADEDADEVICE | The id of the device which has greatest loading percent by phase A. | String
3245 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADEDBDEVICE | The id of the device which has greatest loading percent by phase B. | String
3246 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADEDCDEVICE | The id of the device which has greatest loading percent by phase C. | String
3247 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADEDDEVICE | The id of the device which has greatest loading percent by three phases. | String
3248 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADING | The greatest loading percent by three phases | Float
3249 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADINGA | The greatest loading percent by phase A | Float
3250 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADINGB | The greatest loading percent by phase A | Float
3251 | DNOM Component | Feeder | FDR | output | FEEDMAXLOADINGC | The greatest loading percent by phase A | Float
3252 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLT | The greatest nodal voltage (either from or to node) by three phases. | Float
3253 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTA | The greatest nodal voltage (either from or to node) by phase A. | Float
3254 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTADEVICE | The id of node which has greatest voltage(either from or to node) by phase A. | String
3255 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTB | The greatest nodal voltage (either from or to node) by phase B. | Float
3256 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTBDEVICE | The id of node which has greatest voltage(either from or to node) by phase B. | String
3257 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTC | The greatest nodal voltage (either from or to node) by phase C. | Float
3258 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTCDEVICE | The id of node which has greatest voltage(either from or to node) by phase C. | String
3259 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDEVICE | The id of node which has greatest voltage(either from or to node) by three phases. | String
3260 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROP | The greatest voltage drop by three phases. | Float
3261 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPA | The greatest voltage drop by phase A. | Float
3262 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPADEVICE | The id of node which has greatest voltage drop by phase A. | String
3263 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPB | The greatest voltage drop by phase B. | Float
3264 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPBDEVICE | The id of node which has greatest voltage drop by phase B. | String
3265 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPC | The greatest voltage drop by phase C. | Float
3266 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPCDEVICE | The id of node which has greatest voltage drop by phase C. | String
3267 | DNOM Component | Feeder | FDR | output | FEEDMAXVOLTDROPDEVICE | The id of node which has greatest voltage drop by three phases. | String
3268 | DNOM Component | Feeder | FDR | output | FEEDMINVOLT | The lowest nodal voltage (either from or to node) by three phases. | Float
3269 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTA | The lowest nodal voltage (either from or to node) by phase A. | Float
3270 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTADEVICE | The id of node which has lowest voltage(either from or to node) by phase A. | String
3271 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTB | The lowest nodal voltage (either from or to node) by phase B. | Float
3272 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTBDEVICE | The id of node which has lowest voltage(either from or to node) by phase B. | String
3273 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTC | The lowest nodal voltage (either from or to node) by phase C. | Float
3274 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTCDEVICE | The id of node which has lowest voltage(either from or to node) by phase C. | String
3275 | DNOM Component | Feeder | FDR | output | FEEDMINVOLTDEVICE | The id of node which has lowest voltage(either from or to node) by three phases. | String
3276 | DNOM Component | Feeder | FDR | output | FEEDPERCENTKWLOSS | Total instantaneous percent loss (P). | Float
3277 | DNOM Component | Feeder | FDR | output | FEEDPERCENTLOADINGA | Feeder amp percent loading by phase A. | Float
3278 | DNOM Component | Feeder | FDR | output | FEEDPERCENTLOADINGB | Feeder amp percent loading by phase B. | Float
3279 | DNOM Component | Feeder | FDR | output | FEEDPERCENTLOADINGC | Feeder amp percent loading by phase C. | Float
3280 | DNOM Component | Feeder | FDR | output | FEEDPF | Feeder head power factor. | Float | DPF | #N/A | #N/A
3281 | DNOM Component | Feeder | FDR | output | FEEDPFA | Average Feeder head voltage magnitude. | Float |  | #N/A | #N/A
3282 | DNOM Component | Feeder | FDR | output | FEEDPFB | Average Feeder head voltage magnitude. | Float |  | #N/A | #N/A
3283 | DNOM Component | Feeder | FDR | output | FEEDPFC | Average Feeder head voltage magnitude. | Float |  | #N/A | #N/A
3284 | DNOM Component | Feeder | FDR | output | FEEDREGCOPPERLOSSP | Total regulator copper real loss | Float | DPF | Watt | Watt
3285 | DNOM Component | Feeder | FDR | output | FEEDREGCOPPERLOSSQ | Total regulator copper reactive loss | Float | DPF | VAR | VAR
3286 | DNOM Component | Feeder | FDR | output | FEEDREGCORELOSSP | Total regulator core real loss | Float | DPF | Watt | Watt
3287 | DNOM Component | Feeder | FDR | output | FEEDREGCORELOSSQ | Total regulator core reactive loss | Float | DPF | VAR | VAR
3288 | DNOM Component | Feeder | FDR | output | FEEDTOTALLOADKVAR | Total instantaneous loss (Q). | Float
3289 | DNOM Component | Feeder | FDR | output | FEEDTOTALLOADKW | Total instantaneous loss (P). | Float
3290 | DNOM Component | Feeder | FDR | output | FEEDVOLTPERCENTIMB | Feeder volt percentage imbalance. | Float
3291 | DNOM Component | Feeder | FDR |  | FISRAUTOENABLEDTEXT | FISR auto enabled text | String
3292 | DNOM Component | Feeder | FDR | input | FISRLOSSVOLTPLANEXEC | Loss of voltage plan execution mode for FISR | Integer
3293 | DNOM Component | Feeder | FDR | input | FISRPERMFAULTPLANEXEC | Permanent Fault Plan Execution Mode for FISR | Integer
3294 | DNOM Component | Feeder | FDR | input | FISRPROFORMINDEX | The FISR problem formulation index | Integer
3295 | DNOM Component | Feeder | FDR | input | FISRPROFORMNAME | The FISR problem formulation name | Integer
3296 | DNOM Component | Feeder | FDR | input | FLLIMMLT | Flow limit scaling factor applied to all limits | Float
3297 | DNOM Component | Feeder | FDR | input | FLOWLIMTMULT | Flow limit scaling factor applied to all limits | Float
3298 | DNOM Component | Feeder | FDR | output | FLOWVIOL | A flag indicating that feeder has flow violation | Boolean
3299 | DNOM Component | Feeder | FDR | input | FSDAGGREGATIONDERACTIVEDEMAND | Total generation of DERs connected to the feeder (calculated by the FSD application) | Float |  | kW | kW
3300 | DNOM Component | Feeder | FDR | input | FSDFEEDERCRITCUSTOMERCOUNT | The total number of priority customers on the feeder | Integer
3301 | DNOM Component | Feeder | FDR | input | FSDFEEDERCUSTOMERCOUNT | Total customer count on the feeder (calculated by the FSD application) | Integer
3302 | DNOM Component | Feeder | FDR | input | FSDFEEDERHASSETFAULTIND | Specifies whether the feeder has Set fault indicators | Boolean
3303 | DNOM Component | Feeder | FDR | input | FSDFEEDERNOMPRIORITYCUSTOMERS | The number of priority customers normally connected to the feeder (calculated by the FSD application) | Integer
3304 | DNOM Component | Feeder | FDR | input | FSDFEEDEROVERHEADLENGTH | Total feeder overhead conductor length | Float |  | miles | miles
3305 | DNOM Component | Feeder | FDR | input | FSDFEEDERPRIORITYCUSTOMERCOUNT | The number of priority customers connected to the feeder (calculated by the FSD application) | Integer
3306 | DNOM Component | Feeder | FDR | input | FSDFEEDERRANKING | Feeder weight ranking for the FSD application | Float
3307 | DNOM Component | Feeder | FDR | input | FSDFEEDERSWITCHINGSTATUS | FSD Stage 1 feeder processing status (None = 0, NotTested = 1, InProgress = 2, TestedNotFaulty = 3, FaultIdentified = 4, NotEligible = 5) | Integer
3308 | DNOM Component | Feeder | FDR | input | FSDFEEDERSWITCHINGSTATUSSTRING | FSD Stage 1 feeder processing status (None, Not Tested, In Progress, Tested Not Faulty, Fault Identified, Not Eligible) | String
3309 | DNOM Component | Feeder | FDR | input | HEADBRN.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3310 | DNOM Component | Feeder | FDR | input | HEADBRN.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3311 | DNOM Component | Feeder | FDR | input | HEADBRN.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3312 | DNOM Component | Feeder | FDR | input | HEADBRN.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3313 | DNOM Component | Feeder | FDR | input | HEADBRN.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3314 | DNOM Component | Feeder | FDR | input | HEADBRN.ID | ID of the HEAD branch | String |  |  |  | DNMOBJ
3315 | DNOM Component | Feeder | FDR | input | HEADBRN.NAME | Object name | String |  |  |  | DNMOBJ
3316 | DNOM Component | Feeder | FDR | input | HEADBRN.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3317 | DNOM Component | Feeder | FDR | input | HEADBRN.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3318 | DNOM Component | Feeder | FDR | input | HEADBRN.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3319 | DNOM Component | Feeder | FDR | input | FSDFEEDERTOTALLOAD | Total load (in kW) connected to the feeder | Float |  | kW | kW
3320 | DNOM Component | Feeder | FDR | input | HEADBRN2.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3321 | DNOM Component | Feeder | FDR | input | HEADBRN2.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3322 | DNOM Component | Feeder | FDR | input | HEADBRN2.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3323 | DNOM Component | Feeder | FDR | input | HEADBRN2.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3324 | DNOM Component | Feeder | FDR | input | HEADBRN2.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3325 | DNOM Component | Feeder | FDR | input | HEADBRN2.ID | ID of the HEAD branch | String |  |  |  | DNMOBJ
3326 | DNOM Component | Feeder | FDR | input | HEADBRN2.NAME | Object name | String |  |  |  | DNMOBJ
3327 | DNOM Component | Feeder | FDR | input | HEADBRN2.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3328 | DNOM Component | Feeder | FDR | input | HEADBRN2.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3329 | DNOM Component | Feeder | FDR | input | HEADBRN2.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3330 | DNOM Component | Feeder | FDR | input | FSDPOSTSTAGE2PRIORITYCUSTOMERS | The number of de-energized priority customers after FSD Stage 2 (calculated by the FSD application) | Integer
3331 | DNOM Component | Feeder | FDR | input | FSDPRESTAGE2PRIORITYCUSTOMERS | The number of de-energized priority customers before FSD Stage 2 (calculated by the FSD application) | Integer
3332 | DNOM Component | Feeder | FDR |  | GNDRTNVIOL | A flag indicating that feeder has ground return violation | Boolean
3333 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_BUS_HV | Flag indicating feeder bus HV violation limit value is auto, inherited or manual | String
3334 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_BUS_LV | Flag indicating feeder bus HV optimization limit value is auto, inherited or manual | String
3335 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_BUSOPT_HV | Flag indicating feeder bus HV optimization limit value (p.u.) is auto, inherited or manual | String
3336 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_BUSOPT_LV | Flag indicating feeder bus HV optimization limit value is auto, inherited or manual | String
3337 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_FLOW | If all feeder devices flow limit % of nominal override limit value is auto, inherited or manual | String
3338 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LOAD_HV | If feeder load HV violation limit (p.u.) override limit value is auto, inherited or manual | String
3339 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LOAD_LV | If feeder load LV violation limit (p.u.) override limit value is auto, inherited or manual | String
3340 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LOADOPT_HV | Flag indicating feeder load HV optimization limit value is auto, inherited or manual | String
3341 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LOADOPT_LV | Flag indicating feeder load LV optimization limit value is auto, inherited or manual | String
3342 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LOADSCALING | If feeder load scaling factor override limit value is auto, inherited or manual | String
3343 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LVM_MAX_PF | If feeder LVM max PF target override limit value is auto, inherited or manual | String
3344 | DNOM Component | Feeder | FDR | input | HASMAN_FDR_LVM_MIN_PF | If feeder LVM min PF target override limit value is auto, inherited or manual | String
3345 | DNOM Component | Feeder | FDR | input | HASMANAMPS | Flag indicating feeder is using a manual entry. | Boolean
3346 | DNOM Component | Feeder | FDR | input | HASMANUALENTRY | If one or some fields of feeder has(have) value override. | Boolean
3347 | DNOM Component | Feeder | FDR | input | HEADBRN | Feeder head brach (near the applications head node) | String
3348 | DNOM Component | Feeder | FDR | input | HEADBRN2 | Feeder head brach 2 (near the applications head node). To handle dual pull-off feeders. | String
3349 | DNOM Component | Feeder | FDR | input | HEADNODE | Feeder Head Node Name | String
3350 | DNOM Component | Feeder | FDR | output | HIGHFEEDKVLL | Highest feeder line to line load and bus voltage | Float | DPF | kV | kV
3351 | DNOM Component | Feeder | FDR | output | HIGHFEEDV | Highest feeder load voltage (configurable voltage base). | Float | DPF | volt | volt
3352 | DNOM Component | Feeder | FDR | output | HISTFEEDCAPVARINSERVICE | Total capacitor kVAR in service. | Float | DPF | kVAR | kVAR
3353 | DNOM Component | Feeder | FDR | output | HISTFEEDCAPVAROUTOFSERVICE | Total capacitor kVAR not in service. | Float | DPF | kVAR | kVAR
3354 | DNOM Component | Feeder | FDR | output | HISTFEEDCAPVARUNAVAILABLE | Total capacitor kVAR not available. | Float | DPF | kVAR | kVAR
3355 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTREGCOPPPERLOSSP | Total regulator real power copper loss. | Float | DPF | Watt | Watt
3356 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTREGCOPPPERLOSSQ | Total regulator reactive power copper loss. | Float | DPF | VAR | VAR
3357 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTREGCORELOSSP | Total regulator real power core loss. | Float | DPF | Watt | Watt
3358 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTREGCORELOSSQ | Total regulator reactive power core loss. | Float | DPF | VAR | VAR
3359 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTTFCOPPPERLOSSP | Total transformer real power copper loss. | Float | DPF | Watt | Watt
3360 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTTFCOPPPERLOSSQ | Total transformer reactive power copper loss. | Float | DPF | VAR | VAR
3361 | DNOM Component | Feeder | FDR | input | LOOPFEED.ADDRESS | The feeder address | String |  |  |  | FDR
3362 | DNOM Component | Feeder | FDR | input | LOOPFEED.ALTERNATENAME | Alternate name of the looped feeder | String |  |  |  | FDR
3363 | DNOM Component | Feeder | FDR | input | LOOPFEED.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3364 | DNOM Component | Feeder | FDR | input | LOOPFEED.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
3365 | DNOM Component | Feeder | FDR | input | LOOPFEED.DEFCOLOR | Default color | Integer |  |  |  | FDR
3366 | DNOM Component | Feeder | FDR | input | LOOPFEED.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
3367 | DNOM Component | Feeder | FDR | input | LOOPFEED.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3368 | DNOM Component | Feeder | FDR | input | LOOPFEED.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3369 | DNOM Component | Feeder | FDR | input | LOOPFEED.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
3370 | DNOM Component | Feeder | FDR | input | LOOPFEED.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
3371 | DNOM Component | Feeder | FDR | input | LOOPFEED.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
3372 | DNOM Component | Feeder | FDR | input | LOOPFEED.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
3373 | DNOM Component | Feeder | FDR | input | LOOPFEED.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
3374 | DNOM Component | Feeder | FDR | input | LOOPFEED.ID | Unique and persistent ID of the looped feeder | String |  |  |  | DNMOBJ
3375 | DNOM Component | Feeder | FDR | input | LOOPFEED.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
3376 | DNOM Component | Feeder | FDR | input | LOOPFEED.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
3377 | DNOM Component | Feeder | FDR | input | LOOPFEED.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
3378 | DNOM Component | Feeder | FDR | input | LOOPFEED.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
3379 | DNOM Component | Feeder | FDR | input | LOOPFEED.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
3380 | DNOM Component | Feeder | FDR | input | LOOPFEED.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
3381 | DNOM Component | Feeder | FDR | input | LOOPFEED.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
3382 | DNOM Component | Feeder | FDR | input | LOOPFEED.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
3383 | DNOM Component | Feeder | FDR | input | LOOPFEED.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
3384 | DNOM Component | Feeder | FDR | input | LOOPFEED.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
3385 | DNOM Component | Feeder | FDR | input | LOOPFEED.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
3386 | DNOM Component | Feeder | FDR | input | LOOPFEED.NAME | Name of the looped feeder | String |  |  |  | DNMOBJ
3387 | DNOM Component | Feeder | FDR | input | LOOPFEED.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
3388 | DNOM Component | Feeder | FDR | input | LOOPFEED.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
3389 | DNOM Component | Feeder | FDR | input | LOOPFEED.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
3390 | DNOM Component | Feeder | FDR | input | LOOPFEED.NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String |  |  |  | FDR
3391 | DNOM Component | Feeder | FDR | input | LOOPFEED.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
3392 | DNOM Component | Feeder | FDR | input | LOOPFEED.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
3393 | DNOM Component | Feeder | FDR | input | LOOPFEED.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
3394 | DNOM Component | Feeder | FDR | input | LOOPFEED.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
3395 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTTFCORELOSSP | Total transformer real power core loss. | Float | DPF | Watt | Watt
3396 | DNOM Component | Feeder | FDR | output | HISTFEEDDISTTFCORELOSSQ | Total transformer reactive power core loss. | Float | DPF | VAR | VAR
3397 | DNOM Component | Feeder | FDR | output | HISTFEEDERKVARLOSS | Total reactive power loss. | Float | DPF | kVAR | kVAR
3398 | DNOM Component | Feeder | FDR | output | HISTFEEDERKWLOSS | Total real power loss. | Float | DPF | kW | kW
3399 | DNOM Component | Feeder | FDR | output | HISTFEEDTOTALP | Sum of load real power . | Float | DPF | Watt | Watt
3400 | DNOM Component | Feeder | FDR | output | HISTFEEDTOTALPQIHIGH | High PQI violation index | Float | DPF | #N/A | #N/A
3401 | DNOM Component | Feeder | FDR | output | HISTFEEDTOTALPQILOW | Low PQI violation index | Float | DPF | #N/A | #N/A
3402 | DNOM Component | Feeder | FDR | output | HISTFEEDTOTALQ | Sum of load reactive power. | Float | DPF | VAR | VAR
3403 | DNOM Component | Feeder | FDR |  | HLIMVIOL | A flag indicating that feeder has high limit violation | Boolean
3404 | DNOM Component | Feeder | FDR | input | ID | Object unique ID | String |  |  |  | DNMOBJ
3405 | DNOM Component | Feeder | FDR | input | INCREASABLE | Feeder DER output can be increased by this number of kW | String |  | kW | kW
3406 | DNOM Component | Feeder | FDR | output | ISDERGATEWAYCONTROLLED | Specifies whether the feeder has DERs that are controlled by the 2030.5 Gateway | Boolean
3407 | DNOM Component | Feeder | FDR | input | ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean
3408 | DNOM Component | Feeder | FDR |  | ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean
3409 | DNOM Component | Feeder | FDR | input | LDNAME | EMS Netmom Load Name | String
3410 | DNOM Component | Feeder | FDR |  | LLIMVIOL | A flag indicating that feeder has low limit violation | Boolean
3411 | DNOM Component | Feeder | FDR |  | LOADSHEDDEFCLASS | Load shed default circuit classification | Integer
3412 | DNOM Component | Feeder | FDR | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
3413 | DNOM Component | Feeder | FDR | input | LOOPFEED | Pointer to the looped feeder | String
3414 | DNOM Component | Feeder | FDR | output | LOWFEEDKVLL | Lowest feeder line to line load and bus voltage | Float | DPF | kV | kV
3415 | DNOM Component | Feeder | FDR | output | LOWFEEDV | Lowest feeder load voltage (configurable voltage base). | Float | DPF | volt | volt
3416 | DNOM Component | Feeder | FDR |  | LVMAUTOENABLEDTEXT | LVM auto enabled text | String
3417 | DNOM Component | Feeder | FDR | output | LVMFAILSAFEACTIVE | Specifies whether a failsafe LVM problem formulation is applied. | Boolean
3418 | DNOM Component | Feeder | FDR | output | LVMFAILSAFEREASON | This flag determines the LVM failsafe condition reason 1=Bus Voltage Mismatch, 2=DPF Solution State, 3=Bus Voltage Mismatch and DPF Solution State. | Integer
3419 | DNOM Component | Feeder | FDR | output | LVMFAILSAFEREVERSALMETHOD | This flag determines whether LVM automatically reverts the problem formulation to the one used before the heuristic failsafe problem formulation. 0=Manual Reversion, 1=Automatic Reversion. | Integer
3420 | DNOM Component | Feeder | FDR | input | LVMPLANEXEC | Plan Execution Mode for LVM | Integer
3421 | DNOM Component | Feeder | FDR | input | FRP | Feeder Restoration Priority (FRP). This is a fixed value, which defines the order in which feeder lockouts should be addressed mainly during times of severe weather. Feeders with lower FRP have higher restoration priority. | Integer
3422 | DNOM Component | Feeder | FDR | output | LVMPROFILEDATA | LVM profile data | Integer
3423 | DNOM Component | Feeder | FDR | input | LVMPROFORMINDEX | Index of the LVM problem formulation used for the feeder | Integer |  | #NA | #NA
3424 | DNOM Component | Feeder | FDR | input | LVMPROFORMNAME | Problem formulation Name. | String |  | #NA | #NA
3425 | DNOM Component | Feeder | FDR |  | LVMSTATUSMEAS | LVM status measurement Id | String
3426 | DNOM Component | Feeder | FDR | input | LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer
3427 | DNOM Component | Feeder | FDR | input | MAN_FDR_BUS_HV | Feeder bus HV violation limit (p.u.) override. | Float
3428 | DNOM Component | Feeder | FDR |  | MAN_FDR_BUS_HV_INHERITVAL | Inhereted value of the manual bus high voltage violation limit | Float |  | p.u.
3429 | DNOM Component | Feeder | FDR | input | MAN_FDR_BUS_LV | Feeder bus LV violation limit (p.u.) override. | Float
3430 | DNOM Component | Feeder | FDR |  | MAN_FDR_BUS_LV_INHERITVAL | Inhereted value of the manual bus low voltage violation limit | Float |  | p.u.
3431 | DNOM Component | Feeder | FDR | input | MAN_FDR_BUSOPT_HV | Feeder bus HV optimization limit (p.u.) override. | Float
3432 | DNOM Component | Feeder | FDR |  | MAN_FDR_BUSOPT_HV_INHERITVAL | Inhereted value of the manual bus high voltage optimization limit | Float |  | p.u.
3433 | DNOM Component | Feeder | FDR | input | MAN_FDR_BUSOPT_LV | Feeder bus LV optimization limit (p.u.) override. | Float
3434 | DNOM Component | Feeder | FDR |  | MAN_FDR_BUSOPT_LV_INHERITVAL | Inhereted value of the manual bus low voltage optimization limit | Float |  | p.u.
3435 | DNOM Component | Feeder | FDR | input | MAN_FDR_FLOW | All feeder devices flow limit % of nominal override. | Float
3436 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.AREAIND | Permission area index of the breaker | String |  |  |  | DNMOBJ
3437 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3438 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.CHGNOPEN | Change the normal open status flag | String |  |  |  | SWT
3439 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.CURROPEN | Current open status flag | String |  |  |  | SWT
3440 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | String |  |  |  | SWT
3441 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.DNOMX | X coordinate of the breaker | String |  |  |  | DNMOBJ
3442 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.DNOMY | Y coordinate of the breaker | String |  |  |  | DNMOBJ
3443 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.DSOOVER | Enumeration of advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | String |  |  |  | SWT
3444 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3445 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.ID | ID of the breaker | String |  |  |  | DNMOBJ
3446 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.NAME | Name of the breaker | String |  |  |  | DNMOBJ
3447 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3448 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3449 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.NOPEN | Normally open status flag | String |  |  |  | SWT
3450 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3451 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.REMOTE | Remote status flag | String |  |  |  | SWT
3452 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.SWMASK | Switch attribute mask | String |  |  |  | SWT
3453 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER.SWMASK2 | Switch attribute mask 2 | String |  |  |  | SWT
3454 | DNOM Component | Feeder | FDR | input | MAN_FDR_LOAD_HV | Feeder load HV violation limit (p.u.) override. | Float
3455 | DNOM Component | Feeder | FDR |  | MAN_FDR_LOAD_HV_INHERITVAL | Inhereted value of the manual load high voltage violation limit | Float |  | p.u.
3456 | DNOM Component | Feeder | FDR | input | MAN_FDR_LOAD_LV | Feeder load LV violation limit (p.u.) override. | Float
3457 | DNOM Component | Feeder | FDR |  | MAN_FDR_LOAD_LV_INHERITVAL | Inhereted value of the manual load low voltage violation limit | Float |  | p.u.
3458 | DNOM Component | Feeder | FDR | input | MAN_FDR_LOADOPT_HV | Feeder load HV optimization limit (p.u.) manual override value | Float
3459 | DNOM Component | Feeder | FDR | input | MAN_FDR_LOADOPT_LV | Feeder load LV optimization limit (p.u.) manual override value | Float
3460 | DNOM Component | Feeder | FDR | input | MAN_FDR_LOADSCALING | Feeder load scaling factor override. | Float
3461 | DNOM Component | Feeder | FDR | input | MAN_FDR_LVM_MAX_PF | Feeder LVM max PF target override. | Float
3462 | DNOM Component | Feeder | FDR |  | MAN_FDR_LVM_MAX_PF_INHERITVAL | Inhereted value of the manual feeder maximum power factor target limit for LVM | Float |  | p.u.
3463 | DNOM Component | Feeder | FDR | input | MAN_FDR_LVM_MIN_PF | Feeder LVM min PF target override. | Float
3464 | DNOM Component | Feeder | FDR |  | MAN_FDR_LVM_MIN_PF_INHERITVAL | Inhereted value of the manual feeder minimum power factor target limit for LVM | Float |  | p.u.
3465 | DNOM Component | Feeder | FDR | input | MANAMPSA | A manually entered phase A feeder amp value. | Float
3466 | DNOM Component | Feeder | FDR | input | MANAMPSB | A manually entered phase B feeder amp value. | Float
3467 | DNOM Component | Feeder | FDR | input | MANAMPSC | A manually entered phase C feeder amp value. | Float
3468 | DNOM Component | Feeder | FDR | input | MANPF | A manually entered power factor feeder head value. | Float
3469 | DNOM Component | Feeder | FDR | input | MAXUNCTRLCAPACITORS | Maximum Uncontrollable Capacitors. | Integer
3470 | DNOM Component | Feeder | FDR | input | MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers. | Integer
3471 | DNOM Component | Feeder | FDR | input | NAME | Object name | String |  |  |  | DNMOBJ
3472 | DNOM Component | Feeder | FDR | input | NOMINALBREAKER | Pointer to the nominal breaker, set at model build | String
3473 | DNOM Component | Feeder | FDR |  | NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String
3474 | DNOM Component | Feeder | FDR |  | NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String
3475 | DNOM Component | Feeder | FDR |  | NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String
3476 | DNOM Component | Feeder | FDR |  | NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String
3477 | DNOM Component | Feeder | FDR | output | NUMABNRM | Number of abnormal topology conditions. | Integer | NTP | count | count
3478 | DNOM Component | Feeder | FDR | output | NUMDEENG | Number of de-energized customers. | Integer | NTP | count | count
3479 | DNOM Component | Feeder | FDR |  | NUMDPFIT | Number of DPR iterations | String
3480 | DNOM Component | Feeder | FDR | input | NUMLDCAT | Number of load categories for the station | Integer
3481 | DNOM Component | Feeder | FDR | output | NUMNONTHRPHBALLDS | Number of non-balanced three-phase loads | Integer | DPF | count | count
3482 | DNOM Component | Feeder | FDR | output | NUMTHRPHBALLDS | Number of balanced three-phase loads. | Integer | DPF | count | count
3483 | DNOM Component | Feeder | FDR |  | NUMVIOL | Number of violations | String
3484 | DNOM Component | Feeder | FDR |  | OLDLVMPROFORMINDEX | Index of the LVM problem formulation that was specified in the DNAF System Configuration display for the feeder before applying a failsafe problem formulation. Used for Failsafe reversion. | Integer |  | #NA | #NA
3485 | DNOM Component | Feeder | FDR | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
3486 | DNOM Component | Feeder | FDR | input | PNOMLOAD | Array of nominal P load values by load category | String
3487 | DNOM Component | Feeder | FDR | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
3488 | DNOM Component | Feeder | FDR | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
3489 | DNOM Component | Feeder | FDR | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
3490 | DNOM Component | Feeder | FDR | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
3491 | DNOM Component | Feeder | FDR | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
3492 | DNOM Component | Feeder | FDR |  | PQIHIGH | High voltage power quality index (%kW) | String
3493 | DNOM Component | Feeder | FDR | output | PQIHIGHINDEX | Feeder high PQI value. | Float | DPF | #N/A | #N/A
3494 | DNOM Component | Feeder | FDR |  | PQIIMBAL | Imbalance voltage power quality index (%kW) | String
3495 | DNOM Component | Feeder | FDR | output | PQIIMBALANCEINDEX | Feeder imbalance PQI value. | Float | DPF | #N/A | #N/A
3496 | DNOM Component | Feeder | FDR |  | PQILOW | Low voltage power quality index (%kW) | String
3497 | DNOM Component | Feeder | FDR | output | PQILOWINDEX | Feeder low PQI value. | Float | DPF | #N/A | #N/A
3498 | DNOM Component | Feeder | FDR | input | PRVEVALUATION | Specifies the fault impedance evaluation type that is applied by the PRV application (NotSet = 0, BoltedFault = 1) | Integer
3499 | DNOM Component | Feeder | FDR | input | PWRTFBANKID | Power transformer bank ID | String
3500 | DNOM Component | Feeder | FDR | input | PWRTFNAME | The name of the associated power transformer | String
3501 | DNOM Component | Feeder | FDR | input | PWRTFID | The ID of the associated power transformer | String
3502 | DNOM Component | Feeder | FDR | output | REACTIVEDEMANDDIFF | Total reactive power demand difference between calculated and measured values | String |  | MVAR | MVAR
3503 | DNOM Component | Feeder | FDR |  | REGCOPLS | Total regulator copper loss | Float |  | P + jQ | P + jQ
3504 | DNOM Component | Feeder | FDR |  | REGCORLS | Total regulator core loss | Float |  | P + jQ | P + jQ
3505 | DNOM Component | Feeder | FDR | output | REGKVARLOSS | Total regulator reactive power loss | Float | DPF | kVAR | kVAR
3506 | DNOM Component | Feeder | FDR | output | REGKWLOSS | Total regulator real power loss | Float | DPF | kW | kW
3507 | DNOM Component | Feeder | FDR | input | TARGETPF.ID | ID of the object function schedule array | String |  |  |  | DNMOBJ
3508 | DNOM Component | Feeder | FDR | input | TARGETPF.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3509 | DNOM Component | Feeder | FDR | input | TARGETPF.Name | Name of the object function schedule array | String |  |  |  | DNMOBJ
3510 | DNOM Component | Feeder | FDR | input | TARGETPF.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3511 | DNOM Component | Feeder | FDR | input | TARGETPF.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3512 | DNOM Component | Feeder | FDR | input | TARGETPF.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3513 | DNOM Component | Feeder | FDR | input | TARGETPF.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3514 | DNOM Component | Feeder | FDR | input | TARGETPF.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3515 | DNOM Component | Feeder | FDR | input | TARGETPF.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3516 | DNOM Component | Feeder | FDR | input | TARGETPF.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3517 | DNOM Component | Feeder | FDR | input | TARGETPF.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3518 | DNOM Component | Feeder | FDR | input | TARGETPF.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3519 | DNOM Component | Feeder | FDR | input | TARGETPF.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3520 | DNOM Component | Feeder | FDR | input | TARGETPF.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3521 | DNOM Component | Feeder | FDR | output | SCADAACTIVEDEMAND | Total measured real power load | String |  | MW | MW
3522 | DNOM Component | Feeder | FDR |  | SCADAAFRENABLED | Indicates if the SCADA AFR is enabled | Boolean
3523 | DNOM Component | Feeder | FDR |  | SCADAFISRENABLED | Indicates if the SCADA FISR is enabled | Boolean
3524 | DNOM Component | Feeder | FDR |  | SCADALVMENABLED | Indicates if the SCADA LVM is enabled | Boolean
3525 | DNOM Component | Feeder | FDR | output | SCADAPOWERFACTOR | Measured power factor | String
3526 | DNOM Component | Feeder | FDR | output | SCADAREACTIVEDEMAND | Total measured reactive power load | String |  | MVAR | MVAR
3527 | DNOM Component | Feeder | FDR | input | TRANSFORMER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3528 | DNOM Component | Feeder | FDR | input | TRANSFORMER.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3529 | DNOM Component | Feeder | FDR | input | TRANSFORMER.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | TF
3530 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean |  |  |  | TF
3531 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer |  |  |  | TF
3532 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3533 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3534 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | TF
3535 | DNOM Component | Feeder | FDR | input | TRANSFORMER.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | TF
3536 | DNOM Component | Feeder | FDR | input | TRANSFORMER.FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float |  |  |  | TF
3537 | DNOM Component | Feeder | FDR | input | TRANSFORMER.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3538 | DNOM Component | Feeder | FDR | input | TRANSFORMER.GROUNDPR | Primary grounded flag | Boolean |  |  |  | TF
3539 | DNOM Component | Feeder | FDR | input | TRANSFORMER.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | TF
3540 | DNOM Component | Feeder | FDR | input | TRANSFORMER.GROUNDTE | Tertiary grounded flag | Boolean |  |  |  | TF
3541 | DNOM Component | Feeder | FDR | input | TRANSFORMER.ID | ID of the upstream branch | String |  |  |  | DNMOBJ
3542 | DNOM Component | Feeder | FDR | input | TRANSFORMER.LVMPROFORMINDEX | LVM problem formulation index | Integer |  |  |  | TF
3543 | DNOM Component | Feeder | FDR | input | TRANSFORMER.MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer |  |  |  | TF
3544 | DNOM Component | Feeder | FDR | input | TRANSFORMER.MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  |  |  | TF
3545 | DNOM Component | Feeder | FDR | input | TRANSFORMER.NAME | Object name | String |  |  |  | DNMOBJ
3546 | DNOM Component | Feeder | FDR | input | TRANSFORMER.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3547 | DNOM Component | Feeder | FDR | input | TRANSFORMER.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3548 | DNOM Component | Feeder | FDR | input | TRANSFORMER.NOMCCUST | The number of nominally connected customers | Integer |  |  |  | TF
3549 | DNOM Component | Feeder | FDR | input | TRANSFORMER.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3550 | DNOM Component | Feeder | FDR | input | TRANSFORMER.PRIMGNDR | Primary grounding branch resistance | Float |  | Ohms | Ohms | TF
3551 | DNOM Component | Feeder | FDR | input | TRANSFORMER.PRIMGNDX | Primary grounding branch reactance | Float |  | Ohms | Ohms | TF
3552 | DNOM Component | Feeder | FDR | input | TRANSFORMER.PRIMWIND | Primary winding connection type | Integer |  |  |  | TF
3553 | DNOM Component | Feeder | FDR | input | TRANSFORMER.REGULATIONMARGIN | Regulation margin | Float |  |  |  | TF
3554 | DNOM Component | Feeder | FDR | input | TRANSFORMER.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | TF
3555 | DNOM Component | Feeder | FDR | input | TRANSFORMER.SEC1GNDR | Secondary grounding branch resistance | Float |  | Ohms | Ohms | TF
3556 | DNOM Component | Feeder | FDR | input | TRANSFORMER.SEC1GNDX | Secondary grounding branch reactance | Float |  | Ohms | Ohms | TF
3557 | DNOM Component | Feeder | FDR | input | TRANSFORMER.SEC2GNDR | Tertiary grounding branch resistance | Float |  | Ohms | Ohms | TF
3558 | DNOM Component | Feeder | FDR | input | TRANSFORMER.SEC2GNDX | Tertiary grounding branch reactance | Float |  | Ohms | Ohms | TF
3559 | DNOM Component | Feeder | FDR | input | TRANSFORMER.SECWIND | Secondary winding connection type | Integer |  |  |  | TF
3560 | DNOM Component | Feeder | FDR | input | TRANSFORMER.TERTWIND | Tertiary winding connection type | Integer |  |  |  | TF
3561 | DNOM Component | Feeder | FDR | input | TRANSFORMER.TFLOADED | Connected load flag | Boolean |  |  |  | TF
3562 | DNOM Component | Feeder | FDR | input | TRANSFORMER.TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean |  |  |  | TF
3563 | DNOM Component | Feeder | FDR | input | TRANSFORMER.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | TF
3564 | DNOM Component | Feeder | FDR | input | TRANSFORMER.VOLTPR | Primary voltage (kV line to ground) | Float |  | kV | kV | TF
3565 | DNOM Component | Feeder | FDR | input | TRANSFORMER.VOLTSC | Secondary voltage (kV line to ground) | Float |  | kV | kV | TF
3566 | DNOM Component | Feeder | FDR | input | TRANSFORMER.VOLTTE | Tertiary voltage (kV line to ground) | Float |  | kV | kV | TF
3567 | DNOM Component | Feeder | FDR | input | SERVCNTR | Pointer to the associated service center | String
3568 | DNOM Component | Feeder | FDR | input | SERVCNTRNAME | Service center name | String
3569 | DNOM Component | Feeder | FDR | input | STATIONID | Feeder's substation ID | String
3570 | DNOM Component | Feeder | FDR |  | STATIONNAME | Nominal station name of the feeder | String
3571 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERFLOWSORT | Highest Overload (in percent) | Float | DPF | percent | percent
3572 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERFLWIMBSORT | Flow imbalance (in percent) | Float | DPF | percent | percent
3573 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERGRNDRTSORT | The highest ground return current in the breaker and recloser in percent | Float | PRV | percent | percent
3574 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
3575 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3576 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
3577 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.DIRECTIONA | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
3578 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3579 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3580 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
3581 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
3582 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.ID | ID of the object | String |  |  |  | DNMOBJ
3583 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.NAME | Object name | String |  |  |  | DNMOBJ
3584 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
3585 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
3586 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERNEUCURRTSORT | The highest neutral relay current in the breaker and recloser in percent | Float | PRV | percent | percent
3587 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
3588 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3589 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
3590 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.DIRECTIONA | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
3591 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3592 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3593 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
3594 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
3595 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.ID | ID of the object | String |  |  |  | DNMOBJ
3596 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.NAME | Object name | String |  |  |  | DNMOBJ
3597 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
3598 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
3599 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERVHISORT | The highest voltage in percent (may be a violation) | Float | DPF | percent | percent
3600 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERVIMBSORT | The highest voltage imbalance in percent (may be a violation) | Float | DPF | percent | percent
3601 | DNOM Component | Feeder | FDR | output | STNEXCPTFEEDERVLOSORT | The lowest voltage in percent (may be a violation) | Float | DPF | percent | percent
3602 | DNOM Component | Feeder | FDR | input | TARGETPF | Target power factor schedule for the feeder head | String
3603 | DNOM Component | Feeder | FDR | output | TCFEEDERSTATUS | TC solution quality description | Integer | TC | enumeration | enumeration
3604 | DNOM Component | Feeder | FDR |  | TFCOPLSS | Total transformer copper loss | Float |  | P + jQ | P + jQ
3605 | DNOM Component | Feeder | FDR |  | TFCORLSS | Total transformer core loss | Float |  | P + jQ | P + jQ
3606 | DNOM Component | Feeder | FDR |  | TOTALLD | Total load | Float |  | P + jQ | P + jQ
3607 | DNOM Component | Feeder | FDR |  | TOTALLSS | Total instantaneous loss | Float |  | P + jQ | P + jQ
3608 | DNOM Component | Feeder | FDR | input | TRANSFORMER | Pointer to connected transformers | String
3609 | DNOM Component | Feeder | FDR |  | VIMBVIOL | A flag indicating that feeder has voltage imbalance violation | Boolean
3610 | DNOM Component | Feeder | FDR | input | VOLTAGE | Nominal voltage level (kV line to ground). | Float
3611 | DNOM Component | Feeder | FDR | input | VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float
3612 | DNOM Component | Feeder | FDR | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
3613 | DNOM Component | Feeder | FDR | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
3614 | DNOM Component | Feeder Output | FDROUT | output | NEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
3615 | DNOM Component | Feeder Output | FDROUT | output | NEUCURVIOL | Specifies whether the neutral current violation exists | Boolean | PRV
3616 | DNOM Component Placement | Fault Indicator Label Placement | FILBPL | input | FAULTIND | Pointer to the associated fault indicator | String
3617 | DNOM Component Placement | Fault Indicator Placement | FIPLE | input | FAULTIND | Pointer to the associated fault indicator | String
3618 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | FISRCARESULTID | Result ID | String
3619 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | FISRCARESULTPLANAVAIL | Result plan available | String
3620 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | FISRCASOLUTIONID | Solution ID | String
3621 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | FISRCASUBNAME | Substation name | String
3622 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONEVALTIME | Solution evaluation time | String
3623 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONEVALTIME_TICKS | Last solution evaluation time | String
3624 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONEXETIME | Solution execution time | String
3625 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONEXETIME_TICKS | Last solution execution time | String
3626 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONPEAKEVALTIME | Solution peak evaluation time | String
3627 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SOLUTIONPEAKEVALTIME_TICKS | Last solution peak evaluation time | String
3628 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SWITCHABLESECTIONLINE | Switchable section line | String
3629 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SWITCHNAME | Switch name | String
3630 | DNAF Object | FISRCA Result Summary | FISRCARESULTSUMMARY |  | SWITCHABLESECTIONNAME | Switchable section name | String
3631 | DNAF Object | Fault Location | FLFLTL | output | BAND | Relative location of the fault | String
3632 | DNAF Object | Fault Location | FLFLTL | output | DISPLAYFAULTLOCATION | Display the fault location results | Boolean | DPF
3633 | DNAF Object | Fault Location | FLFLTL |  | ESTFAULTGEOMETRYNAME | Estimated fault location geometry name | String
3634 | DNAF Object | Fault Location | FLFLTL |  | ESTFAULTHASPLACEMENT | Estimated fault location has placement? | String
3635 | DNAF Object | Fault Location | FLFLTL | output | ESTFAULTLOCATION | Component's fault location. | String | DPF
3636 | DNAF Object | Fault Location | FLFLTL |  | ESTFAULTLOCATIONBRTYPE | Fault location branch type | String
3637 | DNAF Object | Fault Location | FLFLTL | output | ESTFAULTLOCATIONSUBNAME | The name of the substation which contains the specified fault location. | String | DPF
3638 | DNAF Object | Fault Location | FLFLTL |  | ESTFAULTLOCATIONUNDERGROUND | Estimated fault location underground | String
3639 | DNAF Object | Fault Location | FLFLTL | output | EXACT | Exact location of the fault | String
3640 | DNAF Object | Fault Location | FLFLTL | output | FAULTAMPSA | The fault amp flow of phase A in the fault location. | Float
3641 | DNAF Object | Fault Location | FLFLTL | output | FAULTAMPSB | The fault amp flow of phase B in the fault location. | Float
3642 | DNAF Object | Fault Location | FLFLTL | output | FAULTAMPSC | The fault amp flow of phase C in the fault location. | Float
3643 | DNAF Object | Fault Location | FLFLTL | output | FAULTAMPSG | The fault amp flow of phase G in the fault location. | Float
3644 | DNAF Object | Fault Location | FLFLTL | output | FAULTAMPSMAX | The high mesured fault amp flow in the fault location. | Float
3645 | DNAF Object | Fault Location | FLFLTL | output | FAULTFLTYPE | The fault type in the fault location. | String
3646 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCCURRENTA | Fault location result's amp flow of phase A | Float | DPF | Amps | Amps
3647 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCCURRENTB | Fault location result's amp flow of phase B | Float | DPF | Amps | Amps
3648 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCCURRENTC | Fault location result's amp flow of phase C | Float | DPF | Amps | Amps
3649 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCDIFFA | Fault location's current percent difference of phase A | Float | DPF | % | %
3650 | DNOM Component | Fault Indicator | FLTIND | input | ADDRESS.NOAPPSTR | Address of the composite switch | String |  |  |  | NDPFST
3651 | DNOM Component | Fault Indicator | FLTIND | input | ADDRESS.NOAPPSTRING | Address. | String
3652 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCDIFFB | Fault location's current percent difference of phase B | Float | DPF | % | %
3653 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCDIFFC | Fault location's current percent difference of phase C | Float | DPF | % | %
3654 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCDIFFTOTAL | Fault location's average current percent difference of all phases | Float | DPF
3655 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCRESULTID | Id of fault location result. | String | DPF
3656 | DNAF Object | Fault Location | FLFLTL | input | FAULTLOCRESULTID | Id of fault location result. | String
3657 | DNAF Object | Fault Location | FLFLTL | input | FAULTLOCSUBNAME | The name of the substation which contains the specified fault location. | String
3658 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCVOLTA | Calculated phase A voltage magnitude at the faulted node | Float | FL | p.u. | p.u.
3659 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCVOLTB | Calculated phase B voltage magnitude at the faulted node | Float | FL | p.u. | p.u.
3660 | DNAF Object | Fault Location | FLFLTL | output | FAULTLOCVOLTC | Calculated phase C voltage magnitude at the faulted node | Float | FL | p.u. | p.u.
3661 | DNAF Object | Fault Location | FLFLTL | input | FLBREAKERID | The id of break which is placed in the fault location. | String
3662 | DNAF Object | Fault Location | FLFLTL | input | FLBREAKERNAME | The name of break which is placed in the fault location. | String
3663 | DNAF Object | Fault Location | FLFLTL | output | FLSOLUTIONTIME | Last solution time of the fault location | String
3664 | DNAF Object | Fault Location | FLFLTL |  | FLSOLUTIONTIME_TICKS | Time of the latest fault location solution | String
3665 | DNAF Object | Fault Location | FLFLTL | output | NUMBRKFAULTLOCS | Number of fault locations. | Integer
3666 | DNAF Object | Fault Location | FLFLTL | input | NUMFAULTLOCATIONS | Net number of locations - after removal due to adjacent locations. | Integer
3667 | DNAF Object | Fault Location Result | FLRESC | input | DNAFDCEVERSION | The version number of danf parameters file. | Integer
3668 | DNAF Object | Fault Location Result | FLRESC | input | DNAFLASTMODIFIED | The last modified date of danf parameters file. | String
3669 | DNAF Object | Fault Location Result | FLRESC | input | DNAFREVISIONNUM | The revision number of dnaf parameter file. | Integer
3670 | DNOM Component | Fault Indicator | FLTIND | input | ADDRESS | Pointer to the address string in a station vector collection | String |  |  |  | NDPFST
3671 | DNOM Component | Fault Indicator | FLTIND | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
3672 | DNOM Component | Fault Indicator | FLTIND | input | AMPRATE | Device rating (amps). | Float
3673 | DNOM Component | Fault Indicator | FLTIND | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3674 | DNOM Component | Fault Indicator | FLTIND |  | BACKUPTYPE | Fault indicator backup type (1=battery, 2=super capacitor) | Integer
3675 | DNOM Component | Fault Indicator | FLTIND | input | COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
3676 | DNOM Component | Fault Indicator | FLTIND |  | DIRECTIONAL | A flag indicating that the fault indicator is directional | Boolean
3677 | DNOM Component | Fault Indicator | FLTIND |  | DIRECTIONALFAULTIND | Incicates if the fault indicator is directional | Boolean
3678 | DNOM Component | Fault Indicator | FLTIND |  | DIRECTIONMEASTYPE | Returns the measurement type of the directional fault indicator: 0 = No measurement 1 = Multi-state measurement 2 = Reverse single flag measurement (A single measurement that indicates the reserve fault current direction, the phase information is from the FaultStatus measurements for both directions.) 3 = Reverse phase measurement | Enumeration
3679 | DNOM Component | Fault Indicator | FLTIND | input | DNOMRECORDNAME | The DNOM record name of the fault indicator | String |  |  |  | DNMOBJ
3680 | DNOM Component | Fault Indicator | FLTIND | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3681 | DNOM Component | Fault Indicator | FLTIND | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3682 | DNOM Component | Fault Indicator | FLTIND | input | EMSFILE | A flag indicating that the fault indicator is on the station internals view | Boolean
3683 | DNOM Component | Fault Indicator | FLTIND | input | ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer
3684 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDABNORMAL | Indicates if the fault indicator has abnormal status | Boolean
3685 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDBACKUP | Fault indicator backup type | String
3686 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDDIRECTIONALTYPE | Returns the type of the directional fault indicator | String
3687 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDISVALID | Fault indicator is valid? | String
3688 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDLIGHTCOLOR | Fault indicator light color | String
3689 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDMEASTYPE | Returns the type of the fault indicator measurement. 1 = non-directional fault indicator status measurement, 2 = type 1 directional fault indicator status measurement, 3 = type 2 directional fault indicator with forward and reverse status measurement for every phase, 4 = type 2 directional fault indicator with single flag reverse status measurement. | Integer
3690 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDPHASEA | Flag indicating whether phase A exists in the indicator. | Boolean
3691 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDPHASEB | Flag indicating whether phase B exists in the indicator. | Boolean
3692 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDPHASEC | Flag indicating whether phase C exists in the indicator. | Boolean
3693 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDPHASEN | Flag indicating whether phase N exists in the indicator. | Boolean
3694 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDPHASING | Fault indicator phasing. | String
3695 | DNOM Component | Fault Indicator | FLTIND |  | FAULTINDQUALITY | Quality of the SCADA measurement from the fault indicator (e.g., Good, Bad, or Suspect) | String
3696 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDREMOTE | The control status of fault indicator. Return "MANUAL" or "REMOTE". | String
3697 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDSETSTATUS | The status of fault indicator. Return "SET" or "UNSET". | String
3698 | DNOM Component | Fault Indicator | FLTIND | input | FAULTINDSETSTATUSPHASE | Phases that are currently set (faulted). | String
3699 | DNOM Component | Fault Indicator | FLTIND |  | FINDVOLTLEVEL | Fault indicator line to line and line to ground voltage levels | Float |  | kV | kV
3700 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEAS | Fault indicator measurement | String
3701 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASA | SCADA measurement of the fault indicator phase A status (Set/Unset) | String
3702 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASB | SCADA measurement of the fault indicator phase B status (Set/Unset) | String
3703 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
3704 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
3705 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
3706 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
3707 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
3708 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASC | SCADA measurement of the fault indicator phase C status (Set/Unset) | String
3709 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3710 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3711 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3712 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3713 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3714 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.ID | ID of the upstream branch | String |  |  |  | DNMOBJ
3715 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.NAME | Object name | String |  |  |  | DNMOBJ
3716 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3717 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3718 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3719 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASG | SCADA measurement of the fault indicator ground status (Set/Unset) | String
3720 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASREVERSE | SCADA measurement of the single flag reverse fault indicator status (Set/Unset) | String
3721 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASREVERSEA | SCADA measurement of the reverse fault indicator phase A status (Set/Unset) | String
3722 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASREVERSEB | SCADA measurement of the reverse fault indicator phase B status (Set/Unset) | String
3723 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3724 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
3725 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3726 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3727 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3728 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.ID | ID of the upstream branch | String |  |  |  | DNMOBJ
3729 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.NAME | Object name | String |  |  |  | DNMOBJ
3730 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3731 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3732 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3733 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASREVERSEC | SCADA measurement of the reverse fault indicator phase C status (Set/Unset) | String
3734 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
3735 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3736 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
3737 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.DIRECTIONAL | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
3738 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3739 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3740 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
3741 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
3742 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.ID | ID of the upstream fault indicator | String |  |  |  | DNMOBJ
3743 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.NAME | Object name | String |  |  |  | DNMOBJ
3744 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
3745 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
3746 | DNOM Component | Fault Indicator | FLTIND |  | FLTINDMEASREVERSEG | SCADA measurement of the reverse fault indicator ground status (Set/Unset) | String
3747 | DNOM Component | Fault Indicator | FLTIND |  | FORWARDREVERSEFAULTIND | Incicates if the directional fault indicator is of type 2. | Boolean
3748 | DNOM Component | Fault Indicator | FLTIND | input | FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
3749 | DNOM Component | Fault Indicator | FLTIND | input | ID | Object unique ID | String |  |  |  | DNMOBJ
3750 | DNOM Component | Fault Indicator | FLTIND | input | ISDYNFEEDERLOOPED | Flag indicating whether the fault indicator's dynamic feeder is in loop. | Boolean
3751 | DNOM Component | Fault Indicator | FLTIND | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
3752 | DNOM Component | Fault Indicator | FLTIND | input | NAME | Object name | String |  |  |  | DNMOBJ
3753 | DNOM Component | Fault Indicator | FLTIND | input | NODE | Pointer to the associated node | String |  |  |  | COMELC
3754 | DNOM Component | Fault Indicator | FLTIND | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
3755 | DNOM Component | Fault Indicator | FLTIND |  | PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean
3756 | DNOM Component | Fault Indicator | FLTIND | input | PHASING | Connection phases + meas flags. | Integer
3757 | DNOM Component | Fault Indicator | FLTIND | input | SERVCNTR | Pointer to the associated service center | String
3758 | DNOM Component | Fault Indicator | FLTIND | input | SIDE1BRANCH | Pointer to the upstream branch | String
3759 | DNOM Component | Fault Indicator | FLTIND | input | SUBGIVENCOMMONELECT | Substation the component belongs to | String |  |  |  | COMELC
3760 | DNOM Component | Fault Indicator | FLTIND |  | TELEMETEREDFAULTIND | Indicates if the fault indicator is telemetered | Boolean
3761 | DNOM Component | Fault Indicator | FLTIND |  | TIMEDELAY | Time delay in seconds | Integer
3762 | DNOM Component | Fault Indicator | FLTIND | input | UPBRANCH | Pointer to the upstream branch | String
3763 | DNOM Component | Fault Indicator | FLTIND | input | UPFIND | Pointer to the upstream fault indicator | String
3764 | DNOM Component | Fault Indicator | FLTIND | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
3765 | DNOM Component | Fault Indicator | FLTIND | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
3766 |  | Fault Indicator | FLTIND |  | DISREGARDPHASINGFAULTIND | Specifies whether the phase-agnostic fault indication is applied. The fault indicator phase indication is not considered, the faulted phase is detected based on the device that triggers the fault. (Fault indicator phase indication may differ from the actual SCADA faulted phase indication.) | Boolean
3767 | DNAF Object | Fault Trigger | FLTRIGGER |  | _KEY | The unique identifier to represent the device | String
3768 | DNAF Object | Fault Trigger | FLTRIGGER | output | DEVICETYPE | Type of the device | String
3769 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLALTID | Alternate ID | String
3770 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALFAULTTYPE | User entered faulted phase | String
3771 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALPHASECURRENTINPUTA | User entered phase A fault current | Float
3772 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALPHASECURRENTINPUTB | User entered phase B fault current | Float
3773 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALPHASECURRENTINPUTC | User entered phase C fault current | Float
3774 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALPHASECURRENTINPUTMAX | User entered maximum fault current | Float
3775 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLMANUALSUBNAME | Name of the substation associated with the fault location | String
3776 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLPHASEAMANUALFAULTED | Flag indicating phase A fault current is manually entered | Boolean
3777 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLPHASEBMANUALFAULTED | Flag indicating phase B fault current is manually entered | Boolean
3778 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLPHASECMANUALFAULTED | Flag indicating phase C fault current is manually entered | Boolean
3779 | DNAF Object | Fault Trigger | FLTRIGGER |  | FLPHASEGMANUALFAULTED | Flag indicating ground fault current is manually entered | Boolean
3780 | DNAF Object | Fault Trigger | FLTRIGGER | input | ID | Object unique ID | String |  |  |  | DNMOBJ
3781 | DNAF Object | Fault Trigger | FLTRIGGER | input | NAME | Object name | String |  |  |  | DNMOBJ
3782 | DNAF Object | Fault Trigger | FLTRIGGER |  | PERPHASEFAULTAMPSGIVEN | A flag indicating that fault current is provided for phases | Boolean
3783 | DNAF Object | Flow Limit | FLWLIM | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
3784 | DNAF Object | Flow Limit | FLWLIM | output | OVERLOADFEEDERNAME | The name of the feeder that is associated with components with flow violations | String | DPF
3785 | DNOM Component | Future Topology Component | FUTURETOP | input | ACTIVEPHASESSTR | Active phases. | String
3786 | DNOM Component | Future Topology Component | FUTURETOP | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
3787 | DNOM Component | Future Topology Component | FUTURETOP | input | COMMISSIONSTATE | Commissioning status (Active, Future, Future Removed, or Removed) | String
3788 | DNOM Component | Future Topology Component | FUTURETOP | input | COMMISSIONSTATECODE | Specifies whether the component is active (=1) or non-active (=0) | Integer
3789 | DNOM Component | Future Topology Component | FUTURETOP | input | CONSTRUCTPHASES | Individual phases that are constructed but are not energized. | String
3790 | DNOM Component | Future Topology Component | FUTURETOP | input | FUTUREDEVSUB | Nominal DMS substation name. | String
3791 | DNOM Component | Future Topology Component | FUTURETOP | input | FUTUREPHASES | Future phases. | String
3792 | DNOM Component | Future Topology Component | FUTURETOP | input | FUTUREPHASESSTR | Future phases. | String
3793 | DNOM Component | Future Topology Component | FUTURETOP | input | FUTUREREMOVEPHASES | Enumeration of phases that are planned to be removed. | String
3794 | DNOM Component | Future Topology Component | FUTURETOP | input | FUTUREREMOVEPHASESSTR | Individual phases to be removed in future | String
3795 | DNOM Component | Future Topology Component | FUTURETOP | input | PROJECTID | ID of the project that is associated with the device commissioning or decommissioning | String
3796 | DNOM Component | Future Topology Component | FUTURETOP | input | PROJECTSTAGE | The device commissioning or decommissioning stage | String
3797 | DNOM Component | Future Topology Component | FUTURETOP | input | REMOVEDPHASES | Enumeration of phases that were recently removed. | String
3798 | DNOM Component | Future Topology Component | FUTURETOP | input | REMOVEDPHASESSTR | Individual phases that were recently removed | String
3799 | DNOM Component | Future Topology Component | FUTURETOP | input | SIMILIARDEVICEIDS | The list of devices with the same project ID and project stage | String
3800 | DNOM Component | Future Topology Component | FUTURETOP | input | TOPOAREANAME | Associated area name. | String
3801 | DNOM Component | Future Topology Component | FUTURETOP | input | TOPOOBFUTURE | Flag indicating whether the component has future phase. | Boolean
3802 | DNOM Component | Future Topology Component | FUTURETOP | input | TOPOOBNONACTIVE | Flag indicating whether the component is non-active (future, future remove, or removed) | Boolean
3803 | DNOM Component | Future Topology Component | FUTURETOPO | input | COMMISSION | Specifies whether the device is pending commissioning (has future phases) | Boolean
3804 | DNOM Component | Future Topology Component | FUTURETOPO | input | DECOMMISSION | Specifies whether the device is pending decommissioning (has future remove phases) | Boolean
3805 | DNOM Component | Generator | GEN | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
3806 | DNOM Component | Generator | GEN | input | GENMODEL.B0 | Zero sequence susceptance | Float |  |  |  | GENMOD
3807 | DNOM Component | Generator | GEN | input | GENMODEL.B1 | Positive sequence admittance | Float |  |  |  | GENMOD
3808 | DNOM Component | Generator | GEN | input | GENMODEL.B2 | Negative sequence admittance | Float |  |  |  | GENMOD
3809 | DNOM Component | Generator | GEN | input | GENMODEL.G0 | Zero sequence conductance | Float |  |  |  | GENMOD
3810 | DNOM Component | Generator | GEN | input | GENMODEL.G1 | Positive sequence conductance | Float |  |  |  | GENMOD
3811 | DNOM Component | Generator | GEN | input | GENMODEL.G2 | Negative sequence conductance | Float |  |  |  | GENMOD
3812 | DNOM Component | Generator | GEN | input | GENMODEL.ID | ID of the energy generator model | String |  |  |  | DNMOBJ
3813 | DNOM Component | Generator | GEN | input | GENMODEL.KVA | Generator rating | Float |  | kVA | kVA | GENMOD
3814 | DNOM Component | Generator | GEN | input | GENMODEL.NAME | Associated generator model name. | String
3815 | DNOM Component | Generator | GEN | input | GENMODEL.NUMOPSCHEDS | Number of statically defined operating schedules | String |  |  |  | GENMOD
3816 | DNOM Component | Generator | GEN | input | GENMODEL.PGENMAX | Maximum real power output | Float |  | kW | kW | GENMOD
3817 | DNOM Component | Generator | GEN | input | GENMODEL.PGENMIN | Minimum real power output | Float |  | kW | kW | GENMOD
3818 | DNOM Component | Generator | GEN | input | GENMODEL.QGENMAX | The maximum reactive power output | Float |  | kVAR | kVAR | GENMOD
3819 | DNOM Component | Generator | GEN | input | GENMODEL.QGENMIN | The minimum reactive power output | Float |  | kVAR | kVAR | GENMOD
3820 | DNOM Component | Generator | GEN | input | GENMODEL.R2 | Second sequence resistance | Float |  | p.u. | p.u. | GENMOD
3821 | DNOM Component | Generator | GEN | input | GENMODEL.RATEDAMPS | Rated stator current | Float |  | Amps | Amps | GENMOD
3822 | DNOM Component | Generator | GEN | input | GENMODEL.RATEDPF | Rated power factor | Float |  |  |  | GENMOD
3823 | DNOM Component | Generator | GEN | input | GENMODEL.RDPRIM | Unsaturated direct axis primary resistance | Float |  | p.u. | p.u. | GENMOD
3824 | DNOM Component | Generator | GEN | input | GENMODEL.RDSUB | Direct axis sub-transient resistance | Float |  | p.u. | p.u. | GENMOD
3825 | DNOM Component | Generator | GEN | input | GENMODEL.RDSYNC | Direct axis synchronous resistance (per unit) | Float |  | p.u. | p.u. | GENMOD
3826 | DNOM Component | Generator | GEN | input | GENMODEL.RQPRIM | Unsaturated quadrature axis primary resistance | Float |  | p.u. | p.u. | GENMOD
3827 | DNOM Component | Generator | GEN | input | GENMODEL.RQSUB | Quadrature axis sub-transient resistance | Float |  | p.u. | p.u. | GENMOD
3828 | DNOM Component | Generator | GEN | input | GENMODEL.RQSYNC | Quadrature axis synchronous resistance | Float |  | p.u. | p.u. | GENMOD
3829 | DNOM Component | Generator | GEN | input | GENMODEL.RZERO | Zero sequence resistance | Float |  | p.u. | p.u. | GENMOD
3830 | DNOM Component | Generator | GEN | input | GENMODEL.SWCOST | The operational cost of switching on/off a generator | Float |  | $/operation | $/operation | GENMOD
3831 | DNOM Component | Generator | GEN | input | GENMODEL.VOLTAGEBASE | Voltage base value | Float |  |  |  | GENMOD
3832 | DNOM Component | Generator | GEN | input | GENMODEL.VOLTUNIT | Enumerated flag indicating the voltage units that should be used. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer |  |  |  | GENMOD
3833 | DNOM Component | Generator | GEN | input | GENMODEL.X2 | Second sequence reactance | Float |  | p.u. | p.u. | GENMOD
3834 | DNOM Component | Generator | GEN | input | GENMODEL.XDPRIM | Unsaturated direct axis primary reactance | Float |  | p.u. | p.u. | GENMOD
3835 | DNOM Component | Generator | GEN | input | GENMODEL.XDSUB | Direct axis sub-transient reactance | Float |  | p.u. | p.u. | GENMOD
3836 | DNOM Component | Generator | GEN | input | GENMODEL.XDSYNC | Direct axis synchronous reactance | Float |  | p.u. | p.u. | GENMOD
3837 | DNOM Component | Generator | GEN | input | GENMODEL.XQPRIM | Unsaturated quadrature axis primary reactance | Float |  | p.u. | p.u. | GENMOD
3838 | DNOM Component | Generator | GEN | input | GENMODEL.XQSUB | Quadrature axis sub-transient reactance | Float |  | p.u. | p.u. | GENMOD
3839 | DNOM Component | Generator | GEN | input | GENMODEL.XQSYNC | Quadrature axis synchronous reactance | Float |  | p.u. | p.u. | GENMOD
3840 | DNOM Component | Generator | GEN | input | GENMODEL.XZERO | Zero sequence reactance | Float |  | p.u. | p.u. | GENMOD
3841 | DNOM Component | Generator | GEN | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
3842 | DNOM Component | Generator | GEN |  | AUTORECONNECTTIMEDELAY | Time delay in seconds that delays reconnection after the system voltage is restored if generator can automatically reconnect to the system when the system voltage is restored | Integer
3843 | DNOM Component | Generator | GEN |  | DEVICEDSOOVER | The override status for Distribution System Optimizer Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | Boolean
3844 | DNOM Component | Generator | GEN | input | DGCONNECTMEASID | ID of the connection status SCADA measurement | String
3845 | DNOM Component | Generator | GEN | input | DNOMRECORDNAME | The DNOM record name of the generator | String |  |  |  | DNMOBJ
3846 | DNOM Component | Generator | GEN | input | DNOMTABNAME | The DNOM table name of the generator | String
3847 | DNOM Component | Generator | GEN | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
3848 | DNOM Component | Generator | GEN | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
3849 | DNOM Component | Generator | GEN |  | DSOOVER | The override status for Distribution System Optimizer Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | Boolean
3850 | DNOM Component | Generator | GEN | input | FEEDERMAIN | Flag indicating if the generator is on feeder main. | Boolean
3851 | DNOM Component | Generator | GEN | input | FREQUENCYMAXSEP | Maximum frequency before separation from the network (Hz). By default, 63 Hz. | Double |  | Hz | Hz
3852 | DNOM Component | Generator | GEN | input | FREQUENCYMINSEP | Minimum frequency before separation from the network (Hz). By default, 56 Hz. | Double |  | Hz | Hz
3853 | DNOM Component | Generator | GEN | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3854 | DNOM Component | Generator | GEN | input | GDEVTYPE | Generator Device Type. 1 = co generation 2 = wind 3 = solar 4 = micro turbine 5 = fuel cell 6 = battery storage. | Integer
3855 | DNOM Component | Generator | GEN |  | GENDEVTYPE | Generator type (e.g., wind, solar) | String
3856 | DNOM Component | Generator | GEN | input | GENHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set. | Boolean
3857 | DNOM Component | Generator | GEN | input | GENHASQTARGETOVERRIDE | Indicates whether the generator has a manual Q target. | Boolean
3858 | DNOM Component | Generator | GEN | input | GENHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set. | Boolean
3859 | DNOM Component | Generator | GEN | input | GENMODEL | Pointer to the generator model | String
3860 | DNOM Component | Generator | GEN | input | GENNOMVOLT | Nominal voltage rating (kV) | Float
3861 | DNOM Component | Generator | GEN | input | GENNOMVTARGET | Nominal voltage target (percent) either from the generator or from the associated voltage regulation schedule. | Float
3862 | DNOM Component | Generator | GEN | input | GENPHASESENSED | Phases Measured. | String
3863 | DNOM Component | Generator | GEN | input | GENPTARGET | Actual real power target used (kW). | Float
3864 | DNOM Component | Generator | GEN | input | GENQTARGET | The actual reactive power target of the generator. | Float
3865 | DNOM Component | Generator | GEN | input | GENTYPE | The type of the generator (PV or PQ). | Integer
3866 | DNOM Component | Generator | GEN | input | GENTYPENAME | The type name of the generator(PV or PQ). | String
3867 | DNOM Component | Generator | GEN | input | GENVTARGET | Actual voltage Target used (percent). | Float
3868 | DNOM Component | Generator | GEN | input | GNBITMSK | Bitmask - for booleans. | Integer
3869 | DNOM Component | Generator | GEN | input | GROUNDED | Flag indicating if the generator is grounded. | Boolean |  |  |  | SHUNT
3870 | DNOM Component | Generator | GEN | input | HASMANUALENTRY | If one or some fields of generator has(have) value override. | Boolean
3871 | DNOM Component | Generator | GEN | input | ID | Object unique ID | String |  |  |  | DNMOBJ
3872 | DNOM Component | Generator | GEN | input | KVA | Energy resource rating. | Float |  | kVA | kVA
3873 | DNOM Component | Generator | GEN | input | LASTDISCREASONTEXT | The reason for the last disconnection: - "--" (for currently connected energy resources) - High Voltage Out of Range - Low Voltage Out of Range - High Frequency Out of Range - Low Frequency Out of Range - Manual Operation - SCADA Operation | String
3874 | DNOM Component | Generator | GEN | input | LASTDISCRSN | The reason for the last disconnection: 0 = Unknown (connected now) 1 = High Voltage Out of Range 2 = High Frequency Out of Range 3= Manual Operation 4 = SCADA Operation 5 = Low Voltage Out of Range 6 = Low Frequency Out of Range | String
3875 | DNOM Component | Generator | GEN | input | LASTDISCTIME | The time when the last disconnection occurred | String
3876 | DNOM Component | Generator | GEN | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
3877 | DNOM Component | Generator | GEN |  | LVMCONTROLTYPE | LVM control type (0 = VoltageControl = 0, 1 = VarControl, 2 = PowerFactorControl) | Integer
3878 | DNOM Component | Generator | GEN | input | MANPTARGET | Manually entered real power target value (kW). | Float
3879 | DNOM Component | Generator | GEN | input | MANQTARGET | The manual reactive power target of the generator. | Float
3880 | DNOM Component | Generator | GEN | input | MANVTARGET | Manually entered voltage target value (per unit). | Float
3881 | DNOM Component | Generator | GEN | input | MODELKVA | Size of the generator in kVA | Boolean |  | kVA | kVA
3882 | DNOM Component | Generator | GEN | input | NAME | Object name | String |  |  |  | DNMOBJ
3883 | DNOM Component | Generator | GEN | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3884 | DNOM Component | Generator | GEN | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3885 | DNOM Component | Generator | GEN | input | NOMPTARGET | Nominal real power target (kW) either from the generator or from the associated voltage regulation schedule. | Float
3886 | DNOM Component | Generator | GEN | input | NOMQTARGET | The nominal reactive power target of the generator. | Float
3887 | DNOM Component | Generator | GEN | input | NOMVOLT | Nominal voltage (kV line to ground). | Float
3888 | DNOM Component | Generator | GEN | input | REACPOWSCHD.ID | ID of the schedule | String |  |  |  | DNMOBJ
3889 | DNOM Component | Generator | GEN | input | REACPOWSCHD.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3890 | DNOM Component | Generator | GEN | input | REACPOWSCHD.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3891 | DNOM Component | Generator | GEN | input | REACPOWSCHD.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3892 | DNOM Component | Generator | GEN | input | REACPOWSCHD.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3893 | DNOM Component | Generator | GEN | input | REACPOWSCHD.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3894 | DNOM Component | Generator | GEN | input | REACPOWSCHD.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3895 | DNOM Component | Generator | GEN | input | REACPOWSCHD.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3896 | DNOM Component | Generator | GEN | input | REACPOWSCHD.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3897 | DNOM Component | Generator | GEN | input | REACPOWSCHD.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3898 | DNOM Component | Generator | GEN | input | REACPOWSCHD.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3899 | DNOM Component | Generator | GEN | input | REACPOWSCHD.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3900 | DNOM Component | Generator | GEN | input | REACPOWSCHD.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3901 | DNOM Component | Generator | GEN | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3902 | DNOM Component | Generator | GEN | input | REGNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
3903 | DNOM Component | Generator | GEN | input | REGNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
3904 | DNOM Component | Generator | GEN | input | REGNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
3905 | DNOM Component | Generator | GEN | input | REGNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
3906 | DNOM Component | Generator | GEN | input | REGNODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
3907 | DNOM Component | Generator | GEN | input | REGNODE.NAME | Regulation node. | String
3908 | DNOM Component | Generator | GEN | input | REGNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3909 | DNOM Component | Generator | GEN | input | REGNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
3910 | DNOM Component | Generator | GEN | input | REGNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
3911 | DNOM Component | Generator | GEN | input | REGNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
3912 | DNOM Component | Generator | GEN | input | PGENMAX | Maximum real power output. | Float |  | kW | kW
3913 | DNOM Component | Generator | GEN | input | PGENMIN | Minimum real power output. | Float |  | kW | kW
3914 | DNOM Component | Generator | GEN | input | RPOWSCHD.ID | ID of the schedule | String |  |  |  | DNMOBJ
3915 | DNOM Component | Generator | GEN | input | RPOWSCHD.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3916 | DNOM Component | Generator | GEN | input | RPOWSCHD.NAME | Associated real power generation schedule. | String
3917 | DNOM Component | Generator | GEN | input | RPOWSCHD.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3918 | DNOM Component | Generator | GEN | input | RPOWSCHD.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3919 | DNOM Component | Generator | GEN | input | RPOWSCHD.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3920 | DNOM Component | Generator | GEN | input | RPOWSCHD.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3921 | DNOM Component | Generator | GEN | input | RPOWSCHD.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3922 | DNOM Component | Generator | GEN | input | RPOWSCHD.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3923 | DNOM Component | Generator | GEN | input | RPOWSCHD.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3924 | DNOM Component | Generator | GEN | input | RPOWSCHD.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3925 | DNOM Component | Generator | GEN | input | RPOWSCHD.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3926 | DNOM Component | Generator | GEN | input | RPOWSCHD.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3927 | DNOM Component | Generator | GEN | input | RPOWSCHD.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3928 | DNOM Component | Generator | GEN | input | SERVCNTR.NAME | Service center. | String
3929 | DNOM Component | Generator | GEN | input | PHSENSE | Phases Measured. | Integer
3930 | DNOM Component | Generator | GEN | input | POUTPUTMAX | Maximum real power output. | Float |  | KW | KW
3931 | DNOM Component | Generator | GEN | input | POUTPUTMIN | Minimum real power output. | Float |  | KW | KW
3932 | DNOM Component | Generator | GEN |  | PQFlowA | Phase A output power (referenced out of the gen into the bus) | Complex |  | KVA | KVA
3933 | DNOM Component | Generator | GEN |  | PQFlowB | Phase B output power (referenced out of the gen into the bus) | Complex |  | KVA | KVA
3934 | DNOM Component | Generator | GEN |  | PQFlowC | Phase C output power (referenced out of the gen into the bus) | Complex |  | KVA | KVA
3935 | DNOM Component | Generator | GEN | input | PTARGET | Nominal real power target (kW) in the generator. | Float
3936 | DNOM Component | Generator | GEN | input | QGENMAX | The maximum reactive power output. | Float |  | kVAR | kVAR
3937 | DNOM Component | Generator | GEN | input | VOLTSCHD.ID | ID of the schedule | String |  |  |  | DNMOBJ
3938 | DNOM Component | Generator | GEN | input | VOLTSCHD.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3939 | DNOM Component | Generator | GEN | input | VOLTSCHD.NAME | Associated voltage regulation schedule. | String
3940 | DNOM Component | Generator | GEN | input | VOLTSCHD.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3941 | DNOM Component | Generator | GEN | input | VOLTSCHD.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3942 | DNOM Component | Generator | GEN | input | VOLTSCHD.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3943 | DNOM Component | Generator | GEN | input | VOLTSCHD.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3944 | DNOM Component | Generator | GEN | input | VOLTSCHD.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3945 | DNOM Component | Generator | GEN | input | VOLTSCHD.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3946 | DNOM Component | Generator | GEN | input | VOLTSCHD.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3947 | DNOM Component | Generator | GEN | input | VOLTSCHD.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3948 | DNOM Component | Generator | GEN | input | VOLTSCHD.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3949 | DNOM Component | Generator | GEN | input | VOLTSCHD.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3950 | DNOM Component | Generator | GEN | input | VOLTSCHD.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3951 | DNOM Component | Generator | GEN | input | QGENMIN | The minimum reactive power output. | Float |  | kVAR | kVAR
3952 | DNOM Component | Generator | GEN | input | QOUTPUTMAX | Maximum reactive power output. | Float |  | KVAR | KVAR
3953 | DNOM Component | Generator | GEN | input | QOUTPUTMIN | Minimum reactive power output. | Float |  | KVAR | KVAR
3954 | DNOM Component | Generator | GEN | input | QTARGET | Total 3 phase reactive power in kVar for PQ generator. | Float
3955 | DNOM Component | Generator | GEN | input | RATEDAMPS | Rated stator current | Float |  | Amps | Amps
3956 | DNOM Component | Generator | GEN | input | RATEDPF | Rated power factor | Float
3957 | DNOM Component | Generator | GEN | input | REACPOWSCHD | Pointer to the associated reactive power schedule | String
3958 | DNOM Component | Generator | GEN | input | REGNODE | Pointer to the associated regulation node | String
3959 | DNOM Component | Generator | GEN | input | RGROUND | Grounding resistance (ohms). | Float
3960 | DNOM Component | Generator | GEN | input | RPOWSCHD | Pointer to the associated real power schedule | String
3961 | DNOM Component | Generator | GEN | input | SLACKBUS | Flag indicating whether the generator is a slack bus. | Boolean
3962 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
3963 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3964 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3965 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3966 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3967 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3968 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3969 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3970 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3971 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3972 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3973 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3974 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3975 | DNOM Component | Generator | GEN | input | USETARGS | Flag indicating whether to use the voltage target in the generator or associated voltage and real power regulation schedules. True = use the voltage target in the generator. | Boolean
3976 | DNOM Component | Generator | GEN | input | VLIMHIGH | High voltage. | Float
3977 | DNOM Component | Generator | GEN | input | VLIMLOW | Low voltage limit. | Float
3978 | DNOM Component | Generator | GEN | input | VMAXSEP | Maximum voltage before separation from the network (per unit). | Float
3979 | DNOM Component | Generator | GEN | input | VMINSEP | Minimum voltage before separation from the network (per unit). | Float
3980 | DNOM Component | Generator | GEN | input | VOLTAGEBASE | Voltage base value. | Float |  | V | V
3981 | DNOM Component | Generator | GEN | input | VOLTSCHD | Pointer to associated voltage schedule | String
3982 | DNOM Component | Generator | GEN | input | VOLTUNIT | Enumeration indicating the voltage units that should be used. The following values are supported: -1 = Per unit voltage, 1 = Actual voltage (on a user-configured voltage base specified in VoltageBase field) | Integer |  | enumeration | enumeration
3983 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.ID | ID of the schedule | String |  |  |  | DNMOBJ
3984 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
3985 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
3986 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
3987 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
3988 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
3989 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
3990 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
3991 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
3992 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
3993 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
3994 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.YUNITONE | Y1 axis units | String |  |  |  | SCHED
3995 | Global Object | Generator Model | GENMOD | input | OPSCHEDS.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
3996 | DNOM Component | Generator | GEN | input | VREGLL | Whether line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation). | Boolean
3997 | DNOM Component | Generator | GEN | input | VTARGET | Nominal voltage target (percent) in generator. | Float
3998 | DNOM Component | Generator | GEN | input | WYE | Flag indicating if the generator is wye connected. | Boolean |  |  |  | SHUNT
3999 | DNOM Component | Generator | GEN | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
4000 | DNOM Component | Generator | GEN | input | XGROUND | Grounding reactance (ohms). | Float
4001 | DNOM Component | Generator | GEN | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
4002 | DNOM Component Placement | Generator | GEN |  | MANUALEXCLUSIONFLAG | Flag indicating that the device is manually excluded for LVM | Boolean
4003 | DNOM Component | Generator Model | GENMOD |  | PLANNEDRESTORATIONTIME | Planned restoration time after re-energization of the feeder (seconds). | Integer
4004 | Global Object | Generator Model | GENMOD |  | B0 | Zero sequence susceptance | Float
4005 | Global Object | Generator Model | GENMOD |  | B1 | Positive sequence admittance | Float
4006 | Global Object | Generator Model | GENMOD |  | B2 | Negative sequence admittance | Float
4007 | Global Object | Generator Model | GENMOD | input | CAPCURVESCHED | Pointer to the capability curve schedule | String
4008 | Global Object | Generator Model | GENMOD |  | G0 | Zero sequence conductance | Float
4009 | Global Object | Generator Model | GENMOD |  | G1 | Positive sequence conductance | Float
4010 | Global Object | Generator Model | GENMOD |  | G2 | Negative sequence conductance | Float
4011 | Global Object | Generator Model | GENMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
4012 | Global Object | Generator Model | GENMOD |  | KVA | Generator rating (kVA). | Float
4013 | Global Object | Generator Model | GENMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
4014 | Global Object | Generator Model | GENMOD |  | NUMOPSCHEDS | Number of statically defined operating schedules | String
4015 | Global Object | Generator Model | GENMOD | input | OPSCHEDS | Array of pointers to statically defined operating schedules | String
4016 | Global Object | Generator Model | GENMOD |  | PGENMAX | Maximum real power output (kW). | Float
4017 | Global Object | Generator Model | GENMOD |  | PGENMIN | Minimum real power output (kW). | Float
4018 | Global Object | Generator Model | GENMOD |  | QGENMAX | The maximum reactive power output (kVAR). | Float
4019 | Global Object | Generator Model | GENMOD |  | QGENMIN | The minimum reactive power output (kVAR). | Float
4020 | Global Object | Generator Model | GENMOD |  | R2 | Second sequence resistance | Float
4021 | Global Object | Generator Model | GENMOD |  | RATEDAMPS | Rated stator current | Float
4022 | Global Object | Generator Model | GENMOD |  | RATEDPF | Rated power factor | Float
4023 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4024 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4025 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4026 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4027 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GDEVTYPE | Generator device type. 1 = co generation 2 = wind 3 = solar 4 = micro turbine 5 = fuel cell 6 = battery storage. | Integer |  |  |  | GEN
4028 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GENHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set | Boolean |  |  |  | GEN
4029 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GENHASQTARGETOVERRIDE | Indicates whether the generator has a manual Q target | Boolean |  |  |  | GEN
4030 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GENHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set | Boolean |  |  |  | GEN
4031 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GENNOMVOLT | Nominal voltage rating | Float |  | kV | kV | GEN
4032 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GENTYPE | The type of the generator (PV or PQ) | Integer |  |  |  | GEN
4033 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GNBITMSK | Bitmask - for booleans | Integer |  |  |  | GEN
4034 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4035 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4036 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.MANPTARGET | Manually entered real power target value | Float |  | kW | kW | GEN
4037 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.MANQTARGET | The manual reactive power target of the generator | Float |  |  |  | GEN
4038 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.MANVTARGET | Manually entered voltage target value | Float |  | p.u. | p.u. | GEN
4039 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.NAME | Name of the object | String |  |  |  | DNMOBJ
4040 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4041 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4042 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4043 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.PHSENSE | Phases measured | Integer |  |  |  | GEN
4044 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.PTARGET | Nominal real power target in the generator | Float |  | kW | kW | GEN
4045 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.QTARGET | Total 3 phase reactive power in kVar for PQ generator | Float |  |  |  | GEN
4046 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.RGROUND | Grounding resistance (ohms). | Float |  |  |  | GEN
4047 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.SLACKBUS | Flag indicating whether the generator is a slack bus | Boolean |  |  |  | GEN
4048 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.USETARGS | Flag indicating whether to use the voltage target in the generator or associated voltage and real power regulation schedules. True = use the voltage target in the generator. | Boolean |  |  |  | GEN
4049 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.VMAXSEP | Maximum voltage before separation from the network | Float |  | p.u. | p.u. | GEN
4050 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.VMINSEP | Minimum voltage before separation from the network | Float |  | p.u. | p.u. | GEN
4051 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.VREGLL | Whether line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation) | Boolean |  |  |  | GEN
4052 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.VTARGET | Nominal voltage target (percent) in generator | Float |  |  |  | GEN
4053 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4054 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN.XGROUND | Grounding reactance (ohms). | Float |  |  |  | GEN
4055 | Global Object | Generator Model | GENMOD |  | RDPRIM | Unsaturated direct axis primary resistance | Float
4056 | Global Object | Generator Model | GENMOD |  | RDSUB | Direct axis sub-transient resistance (per unit). | Float
4057 | Global Object | Generator Model | GENMOD |  | RDSYNC | Direct axis synchronous resistance (per unit). | Float
4058 | Global Object | Generator Model | GENMOD |  | RQPRIM | Unsaturated quadrature axis primary resistance | Float
4059 | Global Object | Generator Model | GENMOD |  | RQSUB | Quadrature axis sub-transient resistance (per unit). | Float
4060 | Global Object | Generator Model | GENMOD |  | RQSYNC | Quadrature axis synchronous resistance (per unit). | Float
4061 | Global Object | Generator Model | GENMOD |  | RZERO | Zero sequence resistance (per unit). | Float
4062 | Global Object | Generator Model | GENMOD |  | SWCOST | The operational cost of switching on/off a generator. | Float
4063 | Global Object | Generator Model | GENMOD |  | VOLTAGEBASE | Voltage Base value | Float
4064 | Global Object | Generator Model | GENMOD |  | VOLTUNIT | Enumerated flag indicating the voltage units that should be used. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer
4065 | Global Object | Generator Model | GENMOD |  | X2 | Second sequence reactance | Float
4066 | Global Object | Generator Model | GENMOD |  | XDPRIM | Unsaturated direct axis primary reactance | Float
4067 | Global Object | Generator Model | GENMOD |  | XDSUB | Direct axis sub-transient reactance (per unit). | Float
4068 | Global Object | Generator Model | GENMOD |  | XDSYNC | Direct axis synchronous reactance (per unit). | Float
4069 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4070 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4071 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4072 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4073 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4074 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4075 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.NAME | Name of the object | String |  |  |  | DNMOBJ
4076 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4077 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4078 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.NPHASE | A flag indicating the neutral phase | Boolean |  |  |  | GRND
4079 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4080 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.RGROUND | Grounding resistance | Float |  | ohms | ohms | GRND
4081 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4082 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND.XGROUND | Grounding reactance | Float |  | ohms | ohms | GRND
4083 | Global Object | Generator Model | GENMOD |  | XQPRIM | Unsaturated quadrature axis primary reactance | Float
4084 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4085 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4086 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4087 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4088 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GDEVTYPE | Generator device type. 1 = co generation 2 = wind 3 = solar 4 = micro turbine 5 = fuel cell 6 = battery storage. | Integer |  |  |  | GEN
4089 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GENHASPTARGETOVERRIDE | Flag indicating that a manually entered real power target has been set | Boolean |  |  |  | GEN
4090 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GENHASQTARGETOVERRIDE | Indicates whether the generator has a manual Q target | Boolean |  |  |  | GEN
4091 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GENHASVTARGETOVERRIDE | Flag indicating that a manually entered voltage target has been set | Boolean |  |  |  | GEN
4092 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GENNOMVOLT | Nominal voltage rating | Float |  | kV | kV | GEN
4093 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GENTYPE | The type of the generator (PV or PQ) | Integer |  |  |  | GEN
4094 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GNBITMSK | Bitmask - for booleans | Integer |  |  |  | GEN
4095 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4096 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4097 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.MANPTARGET | Manually entered real power target value | Float |  | kW | kW | GEN
4098 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.MANQTARGET | The manual reactive power target of the generator | Float |  |  |  | GEN
4099 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.MANVTARGET | Manually entered voltage target value | Float |  | p.u. | p.u. | GEN
4100 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.NAME | Name of the object | String |  |  |  | DNMOBJ
4101 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4102 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4103 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4104 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.PHSENSE | Phases measured | Integer |  |  |  | GEN
4105 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.PTARGET | Nominal real power target in the generator | Float |  | kW | kW | GEN
4106 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.QTARGET | Total 3 phase reactive power in kVar for PQ generator | Float |  |  |  | GEN
4107 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.RGROUND | Grounding resistance (ohms). | Float |  |  |  | GEN
4108 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.SLACKBUS | Flag indicating whether the generator is a slack bus | Boolean |  |  |  | GEN
4109 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.USETARGS | Flag indicating whether to use the voltage target in the generator or associated voltage and real power regulation schedules. True = use the voltage target in the generator. | Boolean |  |  |  | GEN
4110 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.VMAXSEP | Maximum voltage before separation from the network | Float |  | p.u. | p.u. | GEN
4111 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.VMINSEP | Minimum voltage before separation from the network | Float |  | p.u. | p.u. | GEN
4112 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.VREGLL | Whether line-to-line or line-to ground voltage regulation is used (true = line-to-line voltage regulation) | Boolean |  |  |  | GEN
4113 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.VTARGET | Nominal voltage target (percent) in generator | Float |  |  |  | GEN
4114 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4115 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN.XGROUND | Grounding reactance (ohms). | Float |  |  |  | GEN
4116 | Global Object | Generator Model | GENMOD |  | XQSUB | Quadrature axis sub-transient reactance (per unit). | Float
4117 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4118 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4119 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4120 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4121 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4122 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4123 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.NAME | Name of the object | String |  |  |  | DNMOBJ
4124 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4125 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4126 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.NPHASE | A flag indicating the neutral phase | Boolean |  |  |  | GRND
4127 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4128 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.RGROUND | Grounding resistance | Float |  | ohms | ohms | GRND
4129 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4130 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND.XGROUND | Grounding reactance | Float |  | ohms | ohms | GRND
4131 | Global Object | Generator Model | GENMOD |  | XQSYNC | Quadrature axis synchronous reactance (per unit). | Float
4132 | Global Object | Generator Model | GENMOD |  | XZERO | Zero sequence reactance (per unit). | Float
4133 | DNOM Component Placement | Generator Placement | GENPLE | input | GEN | Pointer to the associated generator | String
4134 | DNOM Component Placement | Geometry | GEOM |  | DEFZOOML | Default zoom level | Float
4135 | DNOM Component Placement | Geometry | GEOM |  | ENUMTYPE | Enumerated geometry type (0 = Unset, 1 = Geographic, 2 = SemiGeographic, 3 = Schematic, 4= StationInternal, 5 = Internal, 6 = Loop) | Integer
4136 | DNOM Component Placement | Geometry | GEOM | input | ID | Object unique ID | String |  |  |  | DNMOBJ
4137 | DNOM Component Placement | Geometry | GEOM |  | MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean
4138 | DNOM Component Placement | Geometry | GEOM | input | NAME | Object name | String |  |  |  | DNMOBJ
4139 | DNOM Component Placement | Geometry | GEOM |  | XFOUR | X coordinate of the fourth boundary rectangle vertice | Float
4140 | DNOM Component Placement | Geometry | GEOM |  | XONE | X coordinate of the first boundary rectangle vertice | Float
4141 | DNOM Component Placement | Geometry | GEOM |  | XTHREE | X coordinate of the third boundary rectangle vertice | Float
4142 | DNOM Component Placement | Geometry | GEOM |  | XTWO | X coordinate of the second boundary rectangle vertice | Float
4143 | DNOM Component Placement | Geometry | GEOM |  | YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float
4144 | DNOM Component Placement | Geometry | GEOM |  | YONE | Y coordinate of the first boundary rectangle vertice | Float
4145 | DNOM Component Placement | Geometry | GEOM |  | YTHREE | Y coordinate of the third boundary rectangle vertice | Float
4146 | DNOM Component Placement | Geometry | GEOM |  | YTWO | Y coordinate of the second boundary rectangle vertice | Float
4147 | DNOM Component Placement | Ground Placement | GNDPLE | input | GROUND | Pointer to the associated grounding device | String
4148 | DNOM Component Placement | Generator Label Placement | GNLBPL | input | GEN | Pointer to the associated generator | String
4149 | DNOM Component | Injection Interface | INJBIF | input | NODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
4150 | DNOM Component | Injection Interface | INJBIF | input | NODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
4151 | DNOM Component | Injection Interface | INJBIF | input | NODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
4152 | DNOM Component | Injection Interface | INJBIF | input | NODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
4153 | DNOM Component | Injection Interface | INJBIF | input | NODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
4154 | DNOM Component | Injection Interface | INJBIF | input | NODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4155 | DNOM Component | Injection Interface | INJBIF | input | NODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4156 | DNOM Component | Injection Interface | INJBIF | input | NODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4157 | DNOM Component | Injection Interface | INJBIF | input | NODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
4158 | DNOM Component Placement | Ground Label Placement | GRLBPL | input | GROUND | Pointer to the associated grounding device | String
4159 | DNOM Component | Ground | GRND | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4160 | DNOM Component | Ground | GRND | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
4161 | DNOM Component | Ground | GRND |  | DNOMTABNAME | The DNOM table name of the ground | String
4162 | DNOM Component | Ground | GRND | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
4163 | DNOM Component | Ground | GRND | input | GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
4164 | DNOM Component | Ground | GRND | input | ID | Object unique ID | String |  |  |  | DNMOBJ
4165 | DNOM Component | Ground | GRND |  | IFLOW | Output power (referenced into the ground, i.e. load convention) | Complex
4166 | DNOM Component | Ground | GRND | input | NAME | Object name | String |  |  |  | DNMOBJ
4167 | DNOM Component | Ground | GRND | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4168 | DNOM Component | Ground | GRND | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4169 | DNOM Component | Ground | GRND |  | NPHASE | A flag indicating the neutral phase | Boolean
4170 | DNOM Component | Ground | GRND | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4171 | DNOM Component | Ground | GRND |  | RGROUND | Grounding resistance | Float |  | ohms | ohms
4172 | DNOM Component | Ground | GRND |  | SFLOW | Output power (referenced into the ground, i.e. load convention) | Complex
4173 | DNOM Component | Ground | GRND | input | WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
4174 | DNOM Component | Ground | GRND |  | XGROUND | Grounding reactance | Float |  | ohms | ohms
4175 | DNOM Component Placement | Global Find Placement | GSPLACEMENT | input | HASGEOMETRYINFO | Flag indicating at least one placement exists for this object. | Boolean
4176 | DNOM Component | Injection Interface | INJBIF | input | NODE | Pointer to the injection interface node | String
4177 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORFROMA | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. From node, phase A. | String
4178 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORFROMABC | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. From node, phases ABC. | String
4179 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORFROMB | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. From node, phase B. | String
4180 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORFROMC | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. From node, phase C. | String
4181 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORTOA | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. To node, phase A. | String
4182 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORTOABC | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. To node, phases ABC. | String
4183 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORTOB | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. To node, phase B. | String
4184 | Virtual Object | Inline Branches | INLINEBR | output | BRANCHPFACTORTOC | Power factor for inline branches including lines, switching devices, inline transformers (not load/secondary transformers), and reactors. To node, phase C. | String
4185 | DNOM Component | Inverter | INVERTER | input | ENERGYRESOURCES | Pointer to the energy resources that are associated with the inverter. | String
4186 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEVACHARGEMAX | Specifies whether the inverter has a manually specified maximum apparent power that DER can absorb from the grid | Boolean
4187 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEVAMAX | Specifies whether the inverter has a manually specified maximum apparent power that DER can deliver to the grid | Boolean
4188 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEVARCHARGEMAX | Specifies whether the inverter has a manually specified maximum reactive power that DER can absorb from the grid | Boolean
4189 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEVARMAX | Specifies whether the inverter has a manually specified maximum reactive power that DER can deliver to the grid | Boolean
4190 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEWCHARGEMAX | Specifies whether the inverter has a manually specified maximum real power that DER can absorb from the grid | Boolean
4191 | DNOM Component | Inverter | INVERTER |  | HASOVERRIDEWMAX | Specifies whether the inverter has a manually specified maximum real power that DER can deliver to the grid | Boolean
4192 | DNOM Component | Inverter | INVERTER |  | INVERTERHASVACHARGEMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum apparent power that DER can absorb from the grid | Boolean
4193 | DNOM Component | Inverter | INVERTER |  | INVERTERHASVAMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum apparent power that DER can deliver to the grid | Boolean
4194 | DNOM Component | Inverter | INVERTER |  | INVERTERHASVARCHARGEMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum reactive power that DER can absorb from the grid | Boolean
4195 | DNOM Component | Inverter | INVERTER |  | INVERTERHASVARMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum reactive power that DER can deliver to the grid | Boolean
4196 | DNOM Component | Inverter | INVERTER |  | INVERTERHASWCHARGEMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum real power that DER can absorb from the grid | Boolean
4197 | DNOM Component | Inverter | INVERTER |  | INVERTERHASWMAXOVERRIDE | Specifies whether the inverter has a manually specified maximum real power that DER can deliver to the grid | Boolean
4198 | DNOM Component | Inverter | INVERTER | input | INVERTERMODEL | Pointer to the inverter model. | String
4199 | DNOM Component | Inverter | INVERTER |  | MANVACHARGEMAX | Manually specified maximum apparent power that DER can absorb from the grid | Float |  | VA | VA
4200 | DNOM Component | Inverter | INVERTER |  | MANVAMAX | Manually specified maximum apparent power that DER can deliver to the grid | Float |  | VA | VA
4201 | DNOM Component | Inverter | INVERTER |  | MANVARCHARGEMAX | Manually specified maximum reactive power that DER can absorb from the grid | Float |  | VAR | VAR
4202 | DNOM Component | Inverter | INVERTER |  | MANVARMAX | Manually specified maximum reactive power that DER can deliver to the grid | Float |  | VAR | VAR
4203 | DNOM Component | Inverter | INVERTER |  | MANWCHARGEMAX | Manually specified maximum real power that DER can absorb from the grid | Float |  | W | W
4204 | DNOM Component | Inverter | INVERTER |  | MANWMAX | Manually specified maximum real power that DER can deliver to the grid | Float |  | W | W
4205 | DNOM Component | Inverter | INVERTER | input | NODE | Pointer to the inverter node. | String
4206 | DNOM Component | Inverter | INVERTER | input | NUMENERGYRESOURCE | The number of energy resources that are associated with the inverter. | Integer
4207 | DNOM Component | Inverter | INVERTER |  | OVERRIDEVACHARGEMAX | Manually specified maximum apparent power that DER can absorb from the grid | Float |  | VA | VA
4208 | DNOM Component | Inverter | INVERTER |  | OVERRIDEVAMAX | Manually specified maximum apparent power that DER can deliver to the grid | Float |  | VA | VA
4209 | DNOM Component | Inverter | INVERTER |  | OVERRIDEVARCHARGEMAX | Manually specified maximum reactive power that DER can absorb from the grid | Float |  | VAR | VAR
4210 | DNOM Component | Inverter | INVERTER |  | OVERRIDEVARMAX | Manually specified maximum reactive power that DER can deliver to the grid | Float |  | VAR | VAR
4211 | DNOM Component | Inverter | INVERTER |  | OVERRIDEWCHARGEMAX | Manually specified maximum real power that DER can absorb from the grid | Float |  | W | W
4212 | DNOM Component | Inverter | INVERTER |  | OVERRIDEWMAX | Manually specified maximum real power that DER can deliver to the grid | Float |  | W | W
4213 | DNOM Component | Inverter | INVERTER | input | PABSORBMAX | Maximum real power absorbable. | Float |  | KW | KW
4214 | DNOM Component | Inverter | INVERTER | input | PEAKPLIMIT | Peak real power limit | Float |  | kW | kW
4215 | DNOM Component | Inverter | INVERTER | input | PEAKPOWERLIMIT | The peak power target power level limit (Watts). | Float |  | W | W
4216 | DNOM Component | Inverter | INVERTER | input | PHASE | Inverter phasing. | String
4217 | DNOM Component | Inverter | INVERTER | input | POUTPUTMAX | Maximum real power deliverable. | Float |  | KW | KW
4218 | DNOM Component | Inverter | INVERTER | input | QABSORBMAX | Maximum reactive power absorbable. | Float |  | KVAR | KVAR
4219 | DNOM Component | Inverter | INVERTER | input | QOUTPUTMAX | Maximum reactive power deliverable. | Float |  | KVAR | KVAR
4220 | DNOM Component | Inverter | INVERTER | input | REFOFFSETVOLT | Inverter voltage offset in volts | Float |  | Volts | Volts
4221 | DNOM Component | Inverter | INVERTER | input | REFVOLT | Inverter voltage in volts | Float |  | Volts | Volts
4222 | DNOM Component | Inverter | INVERTER | input | SABSORBMAX | Maximum apparent power absorbable. | Float |  | KVA | KVA
4223 | DNOM Component | Inverter | INVERTER | input | SIZE | Inverter size | Float |  | kVA | kVA
4224 | DNOM Component | Inverter | INVERTER | input | SOUTPUTMAX | Maximum apparent power deliverable. | Float |  | KVA | KVA
4225 | DNOM Component | Inverter | INVERTER | input | STATIONNAME | Station name | String
4226 | DNOM Component | Inverter | INVERTER | input | VACHARGEMAX | The maximum apparent power the DER can absorb from the grid (VA, for energy storage charging). | Float |  | kVA | kVA
4227 | DNOM Component | Inverter | INVERTER | input | VAMAX | The maximum apparent power the DER can deliver to the grid (VA). | Float |  | kVA | kVA
4228 | DNOM Component | Inverter | INVERTER | input | VARCHARGEMAX | The maximum reactive power the DER can absorb from the grid (VAR), for energy storage charging). | Float |  | kVAR | kVAR
4229 | DNOM Component | Inverter | INVERTER | input | VARMAX | The maximum reactive power the DER can deliver to the grid (VAR). | Float |  | kVAR | kVAR
4230 | DNOM Component | Inverter | INVERTER | input | VOLTREF | The normal operating voltage for the DER site/service connection (V). | Float |  | V | V
4231 | DNOM Component | Inverter | INVERTER | input | VOLTREFOFFSET | An offset voltage that represents an adjustment for this DER, relative to VRef, in Volts. VRefOfs is defined as the voltage at the ECP, relative to the PCC. For example, if the PCC VRef is 120 V, and the nominal voltage at the DER’s ECP is 123 V, then VRefOfs = +3V. All inverters behind one Point of Common Coupling (PCC) have a common reference voltage, but may differ in the voltage between their own Electrical Connection Point (ECP) and the PCC due to instrumentation errors or voltage shifts within a plant. These differences can be corrected by the parameter VRefOfs that is to be applied by each inverter. | Float |  | V | V
4232 | DNOM Component | Inverter | INVERTER | input | WCHARGEMAX | The maximum real power the DER can absorb from the grid (W, for energy storage charging). | Float |  | kW | kW
4233 | DNOM Component | Inverter | INVERTER | input | WMAX | The maximum real power the DER can deliver to the grid (W). | Float |  | kW | kW
4234 | DNOM Component | Inverter Function | INVERTERFUNC | input | APPLYLOWPASSFILTER | This parameter determines if a low pass filter is used for limiting the rate of change of the upper Watt limit produced by the inverter or absorbed for energy storage devices (true means filter is applied). This may be applicable to the Volt-Watt function. (Optional) | Boolean
4235 | DNOM Component | Inverter Function | INVERTERFUNC | input | APPLYRATEOFCHANGELIMITER | This parameter determines if a rising rate and falling rate are used for limiting the rate of change of the upper Watt limit produced by the inverter or absorbed for energy storage devices (true means rates are applied). This may be applicable to the Volt-Watt function. (Optional) | Boolean
4236 | DNOM Component | Inverter Function | INVERTERFUNC | input | AXISSCALINGTYPE | Axis scaling type 0 = None 1 = Percent Maximum Rated Active Power 2 = Percent Maximum Rated Reactive Power VARs (for Watt-VAR and Volt-VAR functions) 3 = Percent Maximum Rated Reactive Power Watts 4 = Percent Maximum Available Reactive Power Watts 5 = Percent Maximum Rated Apparent Power (for Watt-VAR function) | Integer
4237 | DNOM Component | Inverter Function | INVERTERFUNC | input | BLOCKINGZONEV | This setting is a voltage limit (% of VRef) used to define a lower voltage boundary, below which dynamic reactive current support is not active. | Float
4238 | DNOM Component | Inverter Function | INVERTERFUNC | input | CURTAILWATTS | This setting (boolean) determines whether or not Watts should be curtailed in order to produce the reactive current required by the Dynamic Reactive-Current Support function. | Boolean
4239 | DNOM Component | Inverter Function | INVERTERFUNC | input | DESCRIPTION | Description | String
4240 | DNOM Component | Inverter Function | INVERTERFUNC | input | DYNAMICWATTGRADIENT | This is a signed unit-less quantity that establishes the ratio of dynamic Watts (% WMax) to the present delta-voltage of the reference ECP (% VRef). | Float
4241 | DNOM Component | Inverter Function | INVERTERFUNC | input | FALLLIMIT | The maximum rate at which the Max Watt limit may be decreased in response to changes in the local voltage (WMax per second). | Float |  | W | W
4242 | DNOM Component | Inverter Function | INVERTERFUNC | input | FALLLIMITCHARGE | The maximum rate at which the Max Watt limit may be decreased in response to changes in the local voltage (% of WCHARGEMAX per second). This parameter only applies to energy storage systems. | Float |  | W | W
4243 | DNOM Component | Inverter Function | INVERTERFUNC | input | GRADIENTSAG | This is a gradient, expressed in unit-less terms of %/%, to establish the ratio by which Capacitive % VAR production is increased as %Delta-Voltage decreases below the minimum deadband voltage. | Float
4244 | DNOM Component | Inverter Function | INVERTERFUNC | input | GRADIENTSWELL | This is a gradient, expressed in unit-less terms of %/%, to establish the ratio by which Inductive % VAR production is increased as %Delta-Voltage increases above the maximum deadband voltage. | Float
4245 | DNOM Component | Inverter Function | INVERTERFUNC | input | HYSTBLOCKINGZONEV | This setting defines a hysteresis added to m_vBlockingZone in order to create a hysteresis range (% of VRef). | Float |  | p.u. | p.u.
4246 | DNOM Component | Inverter Function | INVERTERFUNC | input | NUMPOINTS | The number of X, Y value pairs. This is a repeating field. | Integer
4247 | DNOM Component | Inverter Function | INVERTERFUNC | input | NUMSCHEDULES | The number of pre-programmed schedules. This is a repeating field. | Integer
4248 | DNOM Component | Inverter Function | INVERTERFUNC | input | RAMPINPUTDN | Ramp input down | Float
4249 | DNOM Component | Inverter Function | INVERTERFUNC | input | RAMPINPUTUP | Ramp rate for increasing input (for storage systems only). | Float
4250 | DNOM Component | Inverter Function | INVERTERFUNC | input | RAMPOUTPUTDN | Ramp rate for decreasing input (for storage systems only). | Float
4251 | DNOM Component | Inverter Function | INVERTERFUNC | input | RAMPOUTPUTUP | Ramp rate for increasing output. | Float
4252 | DNOM Component | Inverter Function | INVERTERFUNC | input | RISELIMIT | The maximum rate at which the Max Watt limit may be increased in response to changes in the local voltage (WMax per second). | Float |  | W | W
4253 | DNOM Component | Inverter Function | INVERTERFUNC | input | RISELIMITCHARGE | The maximum rate at which the Max Watt limit may be increased in response to changes in the local voltage (% of WCHARGEMAX per second). This parameter only applies to energy storage systems. | Float
4254 | DNOM Component | Inverter Function | INVERTERFUNC | input | SCADAMEASVALUE | SCADA analog measurement value for the inverter function | Float
4255 | DNOM Component | Inverter Function | INVERTERFUNC | input | SCHEDULES | Pointer to schedules | String
4256 | DNOM Component | Inverter Function | INVERTERFUNC | input | TIMELOWPASSFILTER | Time constant for the low pass filter (sec). (Optional) | Integer
4257 | DNOM Component | Inverter Function | INVERTERFUNC | input | TIMEOUTWINDOW | Time after which the mode is disabled (sec). This timeout window begins when the mode becomes effective (as a result of a direct command or schedule). A value of zero shall be used to indicate that the setting does not expire. | Integer |  | sec | sec
4258 | DNOM Component | Inverter Function | INVERTERFUNC | input | TIMERANDOMWINDOW | Delay before a new command or newly activated mode begins to take effect (sec). | Integer |  | sec | sec
4259 | DNOM Component | Inverter Function | INVERTERFUNC | input | TYPE | Type | String
4260 | DNOM Component | Inverter Function | INVERTERFUNC | input | USEALTERNATIVEGRADIENT | Option (boolean) to enable the alternative gradient behavior (gradients trend toward zero at the center). | Boolean
4261 | DNOM Component | Inverter Function | INVERTERFUNC | input | VDEADBANDHI | Optional high voltage deadband setting (%Vref) that allow the creation of a dead-band inside which the dynamic Volt-Watt function does not produce any additional Watts. For example, setting m_vDeadbandLo = 10 and m_vDeadbandHi = 10 results in a dead-band that is 20% of VRef wide. | Float
4262 | DNOM Component | Inverter Function | INVERTERFUNC | input | VDEADBANDLO | Optional low voltage deadband setting (%Vref) that allow the creation of a dead-band inside which the dynamic Volt-Watt function does not produce any additional Watts. | Float
4263 | DNOM Component | Inverter Function | INVERTERFUNC | input | VMAXIMUMDEADBAND | This is the maximum voltage deviation relative to Vaverage (% Vref). For positive voltage deviations (voltage above the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. | Float
4264 | DNOM Component | Inverter Function | INVERTERFUNC | input | VMINIMUMDEADBAND | This is the minimum voltage deviation relative to Vaverage (% Vref). For negative voltage deviations (voltage below the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. | Float
4265 | DNOM Component | Inverter Function | INVERTERFUNC | input | XAXISTYPE | X axis type | String
4266 | DNOM Component | Inverter Function | INVERTERFUNC | input | XAXISUNITS | X axis units | Double
4267 | DNOM Component | Inverter Function | INVERTERFUNC | input | XPOINTS | Array of X axis point values. | String
4268 | DNOM Component | Inverter Function | INVERTERFUNC | input | YAXISTYPE | Y axis type | String
4269 | DNOM Component | Inverter Function | INVERTERFUNC | input | YAXISUNITS | Y axis units | Float
4270 | DNOM Component | Inverter Function | INVERTERFUNC | input | YPOINTS | Array of Y axis point values. | String
4271 | DNOM Component | Inverter Group | INVERTERGROUP | input | CUSTOMFIELD | Custom field | String
4272 | DNOM Component | Inverter Group | INVERTERGROUP |  | INVERTERS | Pointer to inverters | String
4273 | DNOM Component | Inverter Group | INVERTERGROUP | input | NUMINVERTERS | The number of inverters in the group | Integer
4274 | DNOM Component Placement | Inverter Group Label Placement | INVERTERGRPLBPL | input | INVERTERGROUP | Pointer to the inverter group | String
4275 | DNOM Component Placement | Inverter Group Placement | INVERTERGRPPLE | input | INVERTERGROUP | Pointer to the inverter group | String
4276 | DNOM Component Placement | Inverter Label Placement | INVERTERLBPL | input | INVERTER | Pointer to the inverter | String
4277 | Global Object | Inverter Model | INVERTERMOD | input | AMPRATING | The maximum nameplate AC current level of the DER (RMS Amps). | Float |  | RMS Amps | RMS Amps
4278 | Global Object | Inverter Model | INVERTERMOD | input | DESCRIPTION | Description of the inverter model | String
4279 | Global Object | Inverter Model | INVERTERMOD | input | DISCONNECTCAPABILITY | The inverter disconnect capability enumeration. The following values are supported: 1 = Physical - isolation between the inverter and the grid 2 = Virtual - real and reactive power output are set to 0 3 = Physical and Virtual 4 = None | Integer |  | enumeration | enumeration
4280 | Global Object | Inverter Model | INVERTERMOD | input | DISCONNECTCAPABILITYTEXT | The inverter disconnect capability text. The following values are supported: - Physical - isolation between the inverter and the grid - Virtual - real and reactive power output are set to 0 - Physical and Virtual - None | String
4281 | Global Object | Inverter Model | INVERTERMOD | input | DISCREVERSIONTIMEOUT | ime after which a command to disconnect expires and the device is able to reconnect (sec). A value of 0 means there is no timeout. | Integer |  | second | second
4282 | Global Object | Inverter Model | INVERTERMOD | input | DYNREACMODES | The array of pointers to the Dynamic Reactive Current Support modes/curves. | String
4283 | Global Object | Inverter Model | INVERTERMOD | input | DYNVLTWMODES | The array of pointers to the Dynamic Volt-Watt modes/curves. | String
4284 | Global Object | Inverter Model | INVERTERMOD | input | FIXEDPFMODES | The array of pointers to the Fixed Power Factor modes/curves. | String
4285 | Global Object | Inverter Model | INVERTERMOD | input | FREQWATTMODES | The array of pointers to the Freq-Watt modes/curves. | String
4286 | Global Object | Inverter Model | INVERTERMOD | input | HFRTMODES | The array of pointers to the High Frequency Ride Through modes/curves. | String
4287 | Global Object | Inverter Model | INVERTERMOD | input | HVRTMODES | The array of pointers to the High Voltage Ride Through modes/curves. | String
4288 | Global Object | Inverter Model | INVERTERMOD | input | LFRTMODES | The array of pointers to the Low Frequency Ride Through modes/curves. | String
4289 | Global Object | Inverter Model | INVERTERMOD | input | LIMITTIMEWINDOW | A time over which a new setting is taking place (sec). For example, if the time window is set to 60 seconds, then the DER would delay a random time between 0 and 60 seconds prior to the new setting taking effect. This setting is provided to accommodate communication systems that might address large numbers of devices in groups. (Optional) | Integer |  | second | second
4290 | Global Object | Inverter Model | INVERTERMOD | input | LVRTMODES | Inverter supports one or more Low Voltage Ride Through modes (true = does support LVRT modes/curves). | String
4291 | Global Object | Inverter Model | INVERTERMOD | input | MAXPOWERLIMITINGMODES | The array of pointers to the Maximum Power Limiting modes/curves. | String
4292 | Global Object | Inverter Model | INVERTERMOD | input | NUMDYNREACMODES | The number of Dynamic Reactive Current Support modes/curves configured in the inverter. | Integer
4293 | Global Object | Inverter Model | INVERTERMOD | input | NUMDYNVLTWMODES | The number of Dynamic Volt-Watt modes/curves configured in the inverter. | Integer
4294 | Global Object | Inverter Model | INVERTERMOD | input | NUMFIXEDPFMODES | The number of Fixed Power Factor modes/curves configured in the inverter. | Integer
4295 | Global Object | Inverter Model | INVERTERMOD | input | NUMFREQWATTMODES | The number of Freq-Watt modes/curves configured in the inverter. | Integer
4296 | Global Object | Inverter Model | INVERTERMOD | input | NUMHFRTMODES | The number of High Frequency Ride Through modes/curves configured in the inverter. | Integer
4297 | Global Object | Inverter Model | INVERTERMOD | input | NUMHVRTMODES | The number of High Voltage Ride Through modes/curves configured in the inverter. | Integer
4298 | Global Object | Inverter Model | INVERTERMOD | input | NUMLFRTMODES | The number of Low Frequency Ride Through modes/curves configured in the inverter | Integer
4299 | Global Object | Inverter Model | INVERTERMOD | input | NUMLVRTMODES | The number of Low Voltage Ride Through modes/curves configured in the inverter. | Integer
4300 | Global Object | Inverter Model | INVERTERMOD | input | NUMMAXPOWERLIMITINGMODES | The number of Maximum Power Limiting modes/curves configured in the inverter. | Integer
4301 | Global Object | Inverter Model | INVERTERMOD | input | NUMVOLTVARMODES | The number of Volt-VAR modes/curves configured in the inverter. | Integer
4302 | Global Object | Inverter Model | INVERTERMOD | input | NUMVOLTWATTMODES | The number of Volt-Watt modes/curves configured in the inverter. | Integer
4303 | Global Object | Inverter Model | INVERTERMOD | input | NUMWATTPFMODES | The number of Watt-Power Factor modes/curves configured in the inverter. | Integer
4304 | Global Object | Inverter Model | INVERTERMOD | input | NUMWATTVARMODES | The number of Watt-Power Factor modes/curves configured in the inverter. | Integer
4305 | Global Object | Inverter Model | INVERTERMOD | input | PEAKPOWERLIMIT | The peak power target power level limit (kW). | Float |  | kW | kW
4306 | Global Object | Inverter Model | INVERTERMOD | input | PFREVERSIONTIMEOUT | Time after which a DER will return to its default power factor setting (sec). A value of 0 means there is no timeout. | Integer |  | second | second
4307 | Global Object | Inverter Model | INVERTERMOD | input | POWERFACTORTYPE | The power factor setting interpretation type. Can be one of the following: 0 = Leading-Lagging Convention - The leading (capacitive) power factor is negative and the lagging (inductive) power factor is positive. (Quadrants 2 and 4 have a negative power factor, and quadrants 1 and 3 have a positive power factor). Used in internal DNAF calculations. 1 = IEC Convention - Supplying or generating active power is positive and demanding active power is negative. (Quadrants 2 and 3 have a negative power factor, and quadrants 1 and 4 have a positive power factor). 2= IEEE Convention - Leading(capacitive) power factor is positive and a lagging(inductive) power factor is negative. (Quadrants 1 and 3 have a negative power factor, and quadrants 2 and 4 have a positive power factor). | Enumeration
4308 | Global Object | Inverter Model | INVERTERMOD | input | POWERFACTORTYPE | An enumeration to identify how the power factor setting is to be interpreted. The enumeration has the following values: 1 = IEC Convention - supplying or generating active power is positive and demanding active power is negative (quadrants 2 and 3 have negative power factor, quadrants 1 and 4 have a positive power factor). 2 = IEEE Convention - leading(capacitive) power factor is positive and a lagging(inductive) power factor is negative" | Integer |  | enumeration | enumeration
4309 | Global Object | Inverter Model | INVERTERMOD | input | SHORTCIRCUITRATING | The short circuit rating specified as a multiplier of the nameplate AC rating (typically between 2 - 5 times). Range is from 0.0 to 15.0 (floating point value). | Float
4310 | Global Object | Inverter Model | INVERTERMOD | input | SPTDYNREACMODES | Inverter supports one or more Dynamic Reactive Current Support modes (true = does support Dynamic Reactive Current Support modes/curves). | Boolean
4311 | Global Object | Inverter Model | INVERTERMOD | input | SPTDYNVLTWMODES | Inverter supports one or more Dynamic Volt-Watt modes (true = does support Dynamic Volt-Watt modes/curves). | Boolean
4312 | Global Object | Inverter Model | INVERTERMOD | input | SPTFIXEDPFMODES | Inverter supports one or more Fixed Power Factor modes (true = does support Fixed Power Factor modes/curves). | Boolean
4313 | Global Object | Inverter Model | INVERTERMOD | input | SPTFREQWATTMODES | Inverter supports one or more Freq-Watt modes (true = does support Freq-Watt modes/curves). | Boolean
4314 | Global Object | Inverter Model | INVERTERMOD | input | SPTHFRTMODES | Inverter supports one or more High Frequency Ride Through modes (true = does support HFRT modes/curves). | Boolean
4315 | Global Object | Inverter Model | INVERTERMOD | input | SPTHVRTMODES | Inverter supports one or more High Voltage Ride Through modes (true = does support HVRT modes/curves). | Boolean
4316 | Global Object | Inverter Model | INVERTERMOD | input | SPTLFRTMODES | Inverter supports one or more Low Frequency Ride Through modes (true = does support LFRT modes/curves). | Boolean
4317 | Global Object | Inverter Model | INVERTERMOD | input | SPTLVRTMODES | Inverter supports one or more Low Voltage Ride Through modes (true = does support LVRT modes/curves). | Boolean
4318 | Global Object | Inverter Model | INVERTERMOD | input | SPTMAXPOWERLIMITINGMODES | Inverter supports one or more Maximum Power Limiting modes (true = does support Maximum Power Limiting modes/curves). | Boolean
4319 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4320 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4321 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
4322 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4323 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4324 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1.TYPEMASK | Type | String |  |  |  | JUNCCT
4325 | Global Object | Inverter Model | INVERTERMOD | input | SPTVOLTVARMODES | Inverter supports one or more Volt-VAR modes (true = does support Volt-VAR modes/curves). The Volt-VAR autonomous function // provide a mechanism through which a DER may be configured to manage its own VAR output in response to the local service voltage. | Boolean
4326 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4327 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4328 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
4329 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4330 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4331 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2.TYPEMASK | Type | String |  |  |  | JUNCCT
4332 | Global Object | Inverter Model | INVERTERMOD | input | SPTVOLTWATTMODES | Inverter supports one or more Volt-Watt modes (true = does support Volt-Watt modes/curves). The Volt-Watt autonomous function provide a mechanism whereby an inverter system could gradually reduce its own maximum power output as the voltage at the Point of Common Coupling (PCC) exceeds a configurable, utility defined limit. | Boolean
4333 | DNOM Component | Junction Branch | JUNCBR | input | DNOMOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4334 | DNOM Component | Junction Branch | JUNCBR | input | DNOMOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4335 | DNOM Component | Junction Branch | JUNCBR | input | DNOMOBJ.ID | Object unique ID | String |  |  |  | DNMOBJ
4336 | DNOM Component | Junction Branch | JUNCBR | input | DNOMOBJ.NAME | Object name | String |  |  |  | DNMOBJ
4337 | Global Object | Inverter Model | INVERTERMOD | input | SPTWATTPFMODES | Inverter supports one or more Watt-Power Factor modes (true = does support Watt-Power Factor modes/curves). The Watt-Power Factor autonomous mode expresses real power on the X axis (expressed as %Wmax) and the Y axis contains the controlled parameter which is power factor (expressed as a signed value greater than 0 and less than or equal to 1.0). | Boolean
4338 | Global Object | Inverter Model | INVERTERMOD | input | SPTWATTVARMODES | Inverter supports one or more Watt-VAR modes (true = does support Watt-VAR modes/curves). The Watt-VAR autonomous mode provides a mechanism through which the DER actively controls the reactive power output as a function of the real power output following a target real power reactive power curve. | Boolean
4339 | Global Object | Inverter Model | INVERTERMOD | input | VACHARGEMAX | The maximum apparent power the DER can absorb from the grid (VA, for energy storage charging). | Float |  | VA | VA
4340 | Global Object | Inverter Model | INVERTERMOD | input | VAMAX | The maximum apparent power the DER can deliver to the grid (VA). | Float |  | VA | VA
4341 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
4342 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
4343 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
4344 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
4345 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.ID | ID of the regulation node | String |  |  |  | DNMOBJ
4346 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4347 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4348 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4349 | DNOM Component | Junction Branch | JUNCBR | input | NODE1.VOLTCALC | Node mask | Integer |  |  |  | NODE
4350 | Global Object | Inverter Model | INVERTERMOD | input | VARCHARGEMAX | The maximum reactive power the DER can absorb from the grid (VAR), for energy storage charging). | Float |  | VAR | VAR
4351 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
4352 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
4353 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
4354 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
4355 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.ID | ID of the regulation node | String |  |  |  | DNMOBJ
4356 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4357 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4358 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4359 | DNOM Component | Junction Branch | JUNCBR | input | NODE2.VOLTCALC | Node mask | Integer |  |  |  | NODE
4360 | Global Object | Inverter Model | INVERTERMOD | input | VARMAX | The maximum reactive power the DER can deliver to the grid (VAR). | Float |  | VAR | VAR
4361 | Global Object | Inverter Model | INVERTERMOD | input | VOLTREF | The normal operating voltage for the DER site/service connection (V). | Float |  | V | V
4362 | Global Object | Inverter Model | INVERTERMOD | input | VOLTREFOFFSET | An offset voltage that represents an adjustment for this DER, relative to VRef, in Volts. VRefOfs is defined as the voltage at the ECP, relative to the PCC. For example, if the PCC VRef is 120 V, and the nominal voltage at the DERs ECP is 123 V, then VRefOfs = +3V. All inverters behind one Point of Common Coupling(PCC) have a common reference voltage, but may differ in the voltage between their own Electrical Connection Point(ECP) and the PCC due to instrumentation errors or voltage shifts within a plant.These differences can be corrected by the parameter VRefOfs that is to be applied by each inverter. | Float
4363 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4364 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4365 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4366 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ.ID | Object unique ID | String |  |  |  | DNMOBJ
4367 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ.NAME | Object name | String |  |  |  | DNMOBJ
4368 | Global Object | Inverter Model | INVERTERMOD | input | VOLTVARMODES | The array of pointers to the Volt-VAR modes/curves. | String
4369 | Global Object | Inverter Model | INVERTERMOD | input | VOLTWATTMODES | The array of pointers to the Volt-Watt modes/curves. | String
4370 | Global Object | Inverter Model | INVERTERMOD | input | WATTPFMODES | The array of pointers to the Watt-Power Factor modes/curves. | String
4371 | Global Object | Inverter Model | INVERTERMOD | input | WATTVARMODES | The array of pointers to the Watt-Power Factor modes/curves. | String
4372 | Global Object | Inverter Model | INVERTERMOD | input | WCHARGEMAX | The maximum real power the DER can absorb from the grid (W, for energy storage charging). | Float |  | W | W
4373 | Global Object | Inverter Model | INVERTERMOD | input | WMAX | The maximum real power the DER can deliver to the grid (W). | Float |  | W | W
4374 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4375 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4376 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
4377 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4378 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4379 | DNOM Component | Junction Container | JUNCCT | input | PARCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
4380 | DNOM Component Placement | Inverter Placement | INVERTERPLE | input | INVERTER | Pointer to the inverter | String
4381 | DNOM Component | Junction Branch | JUNCBR | input | BRANCH | - | - |  |  |  | Commented out
4382 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC1 | Pointer to the first connected junction | String
4383 | DNOM Component | Junction Branch | JUNCBR | input | CONJUNC2 | Pointer to the second connected junction | String
4384 | DNOM Component | Junction Branch | JUNCBR | input | DNOMOBJ | Pointer to a DNOM object, typically a line, a transformer, a reactor, or other branch | String
4385 | DNOM Component | Junction Branch | JUNCBR |  | LINELEN | Line length | Float
4386 | DNOM Component | Junction | JUNCT | input | DNOMOBJ.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4387 | DNOM Component | Junction | JUNCT | input | DNOMOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4388 | DNOM Component | Junction | JUNCT | input | DNOMOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4389 | DNOM Component | Junction | JUNCT | input | DNOMOBJ.ID | Object unique ID | String |  |  |  | DNMOBJ
4390 | DNOM Component | Junction | JUNCT | input | DNOMOBJ.NAME | Object name | String |  |  |  | DNMOBJ
4391 | DNOM Component | Junction Branch | JUNCBR | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
4392 | DNOM Component | Junction Branch | JUNCBR | input | NAME | Object name | String |  |  |  | DNMOBJ
4393 | DNOM Component | Junction Branch | JUNCBR | input | NODE1 | Pointer to the first node | String
4394 | DNOM Component | Junction Branch | JUNCBR | input | NODE2 | Pointer to the second node | String
4395 | DNOM Component | Junction | JUNCT | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4396 | DNOM Component | Junction | JUNCT | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4397 | DNOM Component | Junction | JUNCT | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
4398 | DNOM Component | Junction | JUNCT | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4399 | DNOM Component | Junction | JUNCT | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
4400 | DNOM Component | Junction | JUNCT | input | JUNCCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
4401 | DNOM Component | Junction Branch | JUNCBR | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
4402 | DNOM Component | Junction Branch | JUNCBR | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
4403 | DNOM Component | Junction Container | JUNCCT | input | DNOMOBJ | Pointer to a DNOM object, typically a comp switch, a switch cabinet, a UI container, a vault, or a substation | String
4404 | DNOM Component | Junction Container | JUNCCT |  | GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | Float
4405 | DNOM Component | Junction Container | JUNCCT |  | GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | Float
4406 | DNOM Component | Junction Container | JUNCCT | input | JUNCTS | - | - |  |  |  | Commented out
4407 | DNOM Component | Junction Container | JUNCCT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
4408 | DNOM Component | Junction Container | JUNCCT |  | NTPFLAG | Enumerated NTP flag | Integer
4409 | DNOM Component | Junction Container | JUNCCT | input | PARCONT | Pointer to the parent container | String
4410 | DNOM Component | Junction Container | JUNCCT |  | RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | Float
4411 | DNOM Component | Junction Container | JUNCCT |  | RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | Float
4412 | DNOM Component | Junction Container | JUNCCT |  | TYPEMASK | Type | Integer
4413 | DNOM Component | Junction Container | JUNCCT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
4414 | DNOM Component | Junction Container | JUNCCT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
4415 | DNOM Component | Junction | JUNCT | input | DNOMOBJ | Pointer to a DNOM object, typically a node or a switch | String
4416 | DNOM Component | Junction | JUNCT |  | GEOX | X geoschematic coordinate of the junction | Float
4417 | DNOM Component | Junction | JUNCT |  | GEOY | Y geoschematic coordinate of the junction | Float
4418 | DNOM Component | Junction | JUNCT | input | JBRANCHS | - | - |  |  |  | Commented out
4419 | DNOM Component | Junction | JUNCT | input | JUNCCONT | Pointer to the junction container | String
4420 | DNOM Component | Junction | JUNCT |  | RAWX | X geographic coordinate of the junction | Float
4421 | DNOM Component | Junction | JUNCT |  | RAWY | Y geographic coordinate of the junction | Float
4422 | DNOM Component | Junction | JUNCT |  | TYPEMASK | Type mask | Integer
4423 | DNOM Component Placement | Lavel Placement | LBPLCE | input | CHRROTATION | Placement character rotation angle. Defines rotation of characters within a label string. | Integer
4424 | DNOM Component Placement | Lavel Placement | LBPLCE | input | CONNECTIONPOINT | Placement connection point: 0 - Connection point for individual label string is not used for this specific label. The default connection point specified in the viewer configuration is used instead. 1 - NW - Upper left corner of this label's bounding rectangle is associated label placement x,y. 2 - N - Center of north edge of this label's bounding rectangle is associated label placement x,y. 3 - NE - Upper right corner of this label's bounding rectangle is associated label placement x,y. 4 - W - Center of west edge of this label's bounding rectangle is associated label placement x,y. 5 - Center - Center of this label's bounding rectangle is associated label placement x,y. 6 - E - Center of east edge of this label's bounding rectangle is associated label placement x,y. 7 - SW - Lower left corner of this label's bounding rectangle is associated label placement x,y. 8 - S - Center of south edge of this label's bounding rectangle is associated label placement x,y. 9 - SE - Lower right corner of this label's bounding rectangle is associated label placement x,y. | Integer
4425 | DNOM Component Placement | Lavel Placement | LBPLCE | input | ROTATION | Rotation angle of the placement | Integer
4426 | DNOM Component Placement | Lavel Placement | LBPLCE | input | SIZE | Size of the label font | Integer
4427 | DNOM Component Placement | Lavel Placement | LBPLCE | input | TEXT | Label text | String
4428 | DNOM Component Placement | Lavel Placement | LBPLCE | input | VLCOLOR | Label voltage level color (primarily for switching devices) | Integer
4429 | DNOM Component Placement | Lavel Placement | LBPLCE | input | X | X coordinate of the placement | Float
4430 | DNOM Component Placement | Label Placement | LBPLCE | input | X2 | X coordinate as double data type coming from GIS. Has more precision compared to common X. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
4431 | DNOM Component Placement | Lavel Placement | LBPLCE | input | Y | Y coordinate of the placement | Float
4432 | DNOM Component Placement | Label Placement | LBPLCE | input | Y2 | Y coordinate as double data type coming from GIS. Has more precision compared to common Y. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
4433 | Virtual Object | Load and Bus | LDBUS | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
4434 | Virtual Object | Load and Bus | LDBUS | input | LDNAMEBUSID | Load name or Bus ID. | String
4435 | Virtual Object | Load and Bus | LDBUS | input | LDVNORMLMTHIGH | Normal high voltage limit (per unit or configurable voltage base). | Float |  | Volts | Volts
4436 | Virtual Object | Load and Bus | LDBUS | input | LDVNORMLMTLOW | Normal low voltage limit (per unit or configurable voltage base). | Float |  | Volts | Volts
4437 | Virtual Object | Load and Bus | LDBUS | input | LOADIMBALVOLTLIMITVALUE | Voltage imbalance limit value (%) | Float |  | % | %
4438 | Virtual Object | Load and Bus | LDBUS | input | LOADIMBALVOLTVALUE | Voltage imbalance value (%). | Float |  | % | %
4439 | Virtual Object | Load and Bus | LDBUS | input | LOADIMBALVOLTVALUESORT | Voltage imbalance value (%). Used for applying the red background to the field in grid tabular display. | Float |  | % | %
4440 | Virtual Object | Load and Bus | LDBUS |  | LOADORBUSCONNECTIONTYPE | Load or bus connection type | String
4441 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHASHIGHVOLTVIOLATION | Flag indicating whether there is high voltage violations. Return TRUE or FALSE. | Boolean
4442 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHASLOWVOLTVIOLATION | Flag indicating whether there is low voltage violations. Return TRUE or FALSE. | Boolean
4443 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHIGHLIMITPERCENT | Highest voltage magnitude in percent. | Float |  | % | %
4444 | Virtual Object | Load and Bus | LDBUS |  | LOADORBUSHIGHLINELINEVOLT | The highest Line to line voltage on a load or bus (configurable voltage base). | Float |  | % | %
4445 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHIGHVOLTLIMITNAME | Name of the high voltage limit that has been highest violated. Return “NORMAL”, “EMERGENCY”, or “STABILITY”. | String
4446 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHIGHVOLTLIMITVALUE | Value of the high voltage limit that has been highest violated in configurable voltage base. | Float |  | Volts | Volts
4447 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSHIGHVOLTVALUE | Highest voltage magnitude in configurable voltage base. | Float |  | Volts | Volts
4448 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSLOWLIMITPERCENT | Lowest voltage magnitude in percent. | Float |  | % | %
4449 | Virtual Object | Load and Bus | LDBUS |  | LOADORBUSLOWLINELINEVOLT | The lowest Line to line voltage on a load or bus (configurable voltage base). | Float
4450 | Global Object | Load Category | LDCAT | input | ALDARRAY.ID | ID of the schedule | String |  |  |  | DNMOBJ
4451 | Global Object | Load Category | LDCAT | input | ALDARRAY.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4452 | Global Object | Load Category | LDCAT | input | ALDARRAY.NAME | Name | String |  |  |  | DNMOBJ
4453 | Global Object | Load Category | LDCAT | input | ALDARRAY.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4454 | Global Object | Load Category | LDCAT | input | ALDARRAY.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4455 | Global Object | Load Category | LDCAT | input | ALDARRAY.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4456 | Global Object | Load Category | LDCAT | input | ALDARRAY.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4457 | Global Object | Load Category | LDCAT | input | ALDARRAY.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4458 | Global Object | Load Category | LDCAT | input | ALDARRAY.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4459 | Global Object | Load Category | LDCAT | input | ALDARRAY.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4460 | Global Object | Load Category | LDCAT | input | ALDARRAY.XAXTYPE | Type of value on x axis (time for a load schedule) | String
4461 | Global Object | Load Category | LDCAT | input | ALDARRAY.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4462 | Global Object | Load Category | LDCAT | input | ALDARRAY.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4463 | Global Object | Load Category | LDCAT | input | ALDARRAY.YUNITONE | Y1 axis units | String
4464 | Global Object | Load Category | LDCAT | input | ALDARRAY.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4465 | Global Object | Load Category | LDCAT | input | ALDARRAY.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4466 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSLOWVOLTLIMITNAME | Name of the low voltage limit that has been highest violated. Return “NORMAL”, “EMERGENCY”, or “STABILITY”. | String
4467 | Global Object | Load Category | LDCAT | input | BILLSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
4468 | Global Object | Load Category | LDCAT | input | BILLSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4469 | Global Object | Load Category | LDCAT | input | BILLSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4470 | Global Object | Load Category | LDCAT | input | BILLSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4471 | Global Object | Load Category | LDCAT | input | BILLSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4472 | Global Object | Load Category | LDCAT | input | BILLSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4473 | Global Object | Load Category | LDCAT | input | BILLSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4474 | Global Object | Load Category | LDCAT | input | BILLSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4475 | Global Object | Load Category | LDCAT | input | BILLSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4476 | Global Object | Load Category | LDCAT | input | BILLSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4477 | Global Object | Load Category | LDCAT | input | BILLSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4478 | Global Object | Load Category | LDCAT | input | BILLSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4479 | Global Object | Load Category | LDCAT | input | BILLSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4480 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSLOWVOLTLIMITVALUE | Value of the low voltage limit that has been highest violated in configurable voltage base. | Float |  | Volts | Volts
4481 | Virtual Object | Load and Bus | LDBUS | output | LOADORBUSLOWVOLTVALUE | Lowest voltage magnitude in configurable voltage base. | Float |  | Volts | Volts
4482 | Virtual Object | Load and Bus | LDBUS |  | LOADORBUSVOLTAGEABOVELIMITPERCENT | Percent of voltage over the corresponding limit level | Float
4483 | Virtual Object | Load and Bus | LDBUS |  | LOADORBUSVOLTAGEBELOWLIMITPERCENT | Percent of voltage below the corresponding limit level | Float |  | % | %
4484 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTALL | Phase A line to line voltage expressed as 120V base | Float |  | Volts | Volts
4485 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTALLANG | Phase A line to line voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4486 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTALN | Phase A line to ground voltage expressed as 120V base | Float |  | Volts | Volts
4487 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTALNANG | Phase A line to ground voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4488 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTBLL | Phase B line to line voltage expressed as 120V base | Float |  | Volts | Volts
4489 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTBLLANG | Phase B line to line voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4490 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTBLN | Phase B line to ground voltage expressed as 120V base | Float |  | Volts | Volts
4491 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTBLNANG | Phase B line to ground voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4492 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTCLL | Phase C line to line voltage expressed as 120V base | Float |  | Volts | Volts
4493 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTCLLANG | Phase C line to line voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4494 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTCLN | Phase C line to ground voltage expressed as 120V base | Float |  | Volts | Volts
4495 | Virtual Object | Load and Bus | LDBUS |  | LOADPFVOLTCLNANG | Phase C line to ground voltage expressed as 120V base and phase angle in degrees | Float |  | Volts and degs | Volts and degs
4496 | Virtual Object | Load and Bus | LDBUS | output | VIOLATIONTYPE | Voltage violation type. Return “High” or “Low”. | String
4497 | Virtual Object | Load and Bus | LDBUS | output | VOLTVIOLATIONLEVEL | Voltage violation level. | String
4498 | Global Object | Load Category | LDCAT |  | ACCURACY | Load data accuracy (percent – used in determining the allocated loads). | Float
4499 | Global Object | Load Category | LDCAT | input | ALDARRAY | Associated typical load shapes. Each schedule has one P and Q or PF schedule. | String
4500 | Global Object | Load Category | LDCAT |  | BILLSCH | Associated billing schedule. | String
4501 | Global Object | Load Category | LDCAT |  | BLASCHEDPFFINAL | Interpolated power factor multiplier or actual value if sub hour schedule is provided. | Float
4502 | Global Object | Load Category | LDCAT |  | BLASCHEDPFINAL | Real power multiplier. | Float
4503 | Global Object | Load Category | LDCAT |  | BLASCHEDQFINAL | Reactive power (or power factor) multiplier. | Float
4504 | Global Object | Load Category | LDCAT |  | CURRENTCLPUSCHED | The current cold load pickupvschedule | String
4505 | Global Object | Load Category | LDCAT |  | CURRENTLDSCHED | The current load schedule | String
4506 | Global Object | Load Category | LDCAT |  | DNOMX | X coordinate | Float
4507 | Global Object | Load Category | LDCAT |  | DNOMY | Y coordinate | Float
4508 | Global Object | Load Category | LDCAT |  | ECOSTINT | Value of uninterrupted service ($/kWh). | Float
4509 | Global Object | Load Category | LDCAT |  | ENDTM | Subinterval end times (hours). | Float
4510 | Global Object | Load Category | LDCAT | input | LOADVLTH.ID | ID of the schedule | String |  |  |  | DNMOBJ
4511 | Global Object | Load Category | LDCAT | input | LOADVLTH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4512 | Global Object | Load Category | LDCAT | input | LOADVLTH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4513 | Global Object | Load Category | LDCAT | input | LOADVLTH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4514 | Global Object | Load Category | LDCAT | input | LOADVLTH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4515 | Global Object | Load Category | LDCAT | input | LOADVLTH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4516 | Global Object | Load Category | LDCAT | input | LOADVLTH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4517 | Global Object | Load Category | LDCAT | input | LOADVLTH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4518 | Global Object | Load Category | LDCAT | input | LOADVLTH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4519 | Global Object | Load Category | LDCAT | input | LOADVLTH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4520 | Global Object | Load Category | LDCAT | input | LOADVLTH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4521 | Global Object | Load Category | LDCAT | input | LOADVLTH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4522 | Global Object | Load Category | LDCAT | input | LOADVLTH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4523 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALA | A flag indicating the manual load to voltage coefficient A | Boolean
4524 | Global Object | Load Category | LDCAT | input | LOADVLTO.ID | ID of the schedule | String |  |  |  | DNMOBJ
4525 | Global Object | Load Category | LDCAT | input | LOADVLTO.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4526 | Global Object | Load Category | LDCAT | input | LOADVLTO.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4527 | Global Object | Load Category | LDCAT | input | LOADVLTO.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4528 | Global Object | Load Category | LDCAT | input | LOADVLTO.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4529 | Global Object | Load Category | LDCAT | input | LOADVLTO.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4530 | Global Object | Load Category | LDCAT | input | LOADVLTO.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4531 | Global Object | Load Category | LDCAT | input | LOADVLTO.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4532 | Global Object | Load Category | LDCAT | input | LOADVLTO.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4533 | Global Object | Load Category | LDCAT | input | LOADVLTO.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4534 | Global Object | Load Category | LDCAT | input | LOADVLTO.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4535 | Global Object | Load Category | LDCAT | input | LOADVLTO.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4536 | Global Object | Load Category | LDCAT | input | LOADVLTO.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4537 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALB | A flag indicating the manual load to voltage coefficient C | Boolean
4538 | Global Object | Load Category | LDCAT | input | LOADVLTT.ID | ID of the schedule | String |  |  |  | DNMOBJ
4539 | Global Object | Load Category | LDCAT | input | LOADVLTT.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4540 | Global Object | Load Category | LDCAT | input | LOADVLTT.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4541 | Global Object | Load Category | LDCAT | input | LOADVLTT.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4542 | Global Object | Load Category | LDCAT | input | LOADVLTT.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4543 | Global Object | Load Category | LDCAT | input | LOADVLTT.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4544 | Global Object | Load Category | LDCAT | input | LOADVLTT.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4545 | Global Object | Load Category | LDCAT | input | LOADVLTT.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4546 | Global Object | Load Category | LDCAT | input | LOADVLTT.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4547 | Global Object | Load Category | LDCAT | input | LOADVLTT.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4548 | Global Object | Load Category | LDCAT | input | LOADVLTT.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4549 | Global Object | Load Category | LDCAT | input | LOADVLTT.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4550 | Global Object | Load Category | LDCAT | input | LOADVLTT.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4551 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALC | A flag indicating the manual load to voltage coefficient E | Boolean
4552 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALD | A flag indicating the manual load to voltage coefficient B | Boolean
4553 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALE | A flag indicating the manual load to voltage coefficient D | Boolean
4554 | Global Object | Load Category | LDCAT |  | HASLOADVOLTMANUALF | A flag indicating the manual load to voltage coefficient F | Boolean
4555 | Global Object | Load Category | LDCAT |  | HASMANUALENTRY | Indicates if the operator manually entered load voltage coefficients | Boolean
4556 | Global Object | Load Category | LDCAT |  | HOUR1 | First schedule point hour | Integer
4557 | Global Object | Load Category | LDCAT |  | HOUR2 | Second schedule point hour | Integer
4558 | Global Object | Load Category | LDCAT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
4559 | Global Object | Load Category | LDCAT |  | INDEXINT | Array of sub-interval's major interval indices | String
4560 | Global Object | Load Category | LDCAT |  | INTNAME | The name of each major study interval. | String
4561 | Global Object | Load Category | LDCAT |  | LDCATSCHEDSECVOLTNAME | Associated secondary voltage drop schedule name | String
4562 | Global Object | Load Category | LDCAT |  | LDSCHEDP1 | Real power at the first schedule point hour. | Float
4563 | Global Object | Load Category | LDCAT |  | LDSCHEDP2 | Real power at the second schedule point hour. | Float
4564 | Global Object | Load Category | LDCAT |  | LDSCHEDPF1 | Power factor at the first schedule point hour. | Float
4565 | Global Object | Load Category | LDCAT |  | LDSCHEDPF2 | Power factor at the second schedule point hour. | Float
4566 | Global Object | Load Category | LDCAT |  | LDSCHEDQ1 | Reactive power at the first schedule point hour. | Float
4567 | Global Object | Load Category | LDCAT |  | LDSCHEDQ2 | Reactive power at the second schedule point hour. | Float
4568 | Global Object | Load Category | LDCAT |  | LIMCOST | Voltage limit violation cost | Float
4569 | Global Object | Load Category | LDCAT | input | LOADVLTH | Pointer to the load-to-voltage sensitivity schedule (coefficents C and F) | String
4570 | Global Object | Load Category | LDCAT | input | LOADVLTO | Pointer to the load-to-voltage sensitivity schedule (coefficents A and D) | String
4571 | Global Object | Load Category | LDCAT | input | LOADVLTT | Pointer to the load-to-voltage sensitivity schedule (coefficents B and E) | String
4572 | Global Object | Load Category | LDCAT |  | LOADVOLTAD | Name of associated load to voltage sensitivity coefficient schedule (coefficients A and D). | String
4573 | Global Object | Load Category | LDCAT |  | LOADVOLTBE | Name of associated load to voltage sensitivity coefficient schedule (coefficients B and E). | String
4574 | Global Object | Load Category | LDCAT |  | LOADVOLTCF | Name of associated load to voltage sensitivity coefficient schedule (coefficients C and F). | String
4575 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALA | Manual entry coefficient A. | Float
4576 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALAA | Manual load to voltage coefficient A | Boolean
4577 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALB | Manual entry coefficient B. | Float
4578 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALBB | Manual load to voltage coefficient C | Boolean
4579 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALC | Manual entry coefficient C. | Float
4580 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALCC | Manual load to voltage coefficient E | Boolean
4581 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALD | Manual entry coefficient D. | Float
4582 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALDD | Manual load to voltage coefficient B | Boolean
4583 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALE | Manual entry coefficient E. | Float
4584 | Global Object | Load Category | LDCAT | input | PROFMULT.CLDLDSCH | Associated cold load schedule (only for a load schedule). This field is optional. | String |  |  |  | SCHED
4585 | Global Object | Load Category | LDCAT | input | PROFMULT.DAYTYPE | Associated day type (for a load schedule only) | String |  |  |  | SCHED
4586 | Global Object | Load Category | LDCAT | input | PROFMULT.ID | Unique and persistent ID | String |  |  |  | DNMOBJ
4587 | Global Object | Load Category | LDCAT | input | PROFMULT.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4588 | Global Object | Load Category | LDCAT | input | PROFMULT.LOADCATSFORLDSCHEDULE | Name of associated load category | String |  |  |  | SCHED
4589 | Global Object | Load Category | LDCAT | input | PROFMULT.NAME | Name | String |  |  |  | DNMOBJ
4590 | Global Object | Load Category | LDCAT | input | PROFMULT.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4591 | Global Object | Load Category | LDCAT | input | PROFMULT.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4592 | Global Object | Load Category | LDCAT | input | PROFMULT.PAVERAGE | Load average(real power) value | Float |  |  |  | SCHED
4593 | Global Object | Load Category | LDCAT | input | PROFMULT.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4594 | Global Object | Load Category | LDCAT | input | PROFMULT.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4595 | Global Object | Load Category | LDCAT | input | PROFMULT.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4596 | Global Object | Load Category | LDCAT | input | PROFMULT.SEASON | Associated season (for a load schedule only) | String |  |  |  | SCHED
4597 | Global Object | Load Category | LDCAT | input | PROFMULT.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4598 | Global Object | Load Category | LDCAT | input | PROFMULT.SKPTARRY | Associated array of schedule points | String |  |  |  | SCHED
4599 | Global Object | Load Category | LDCAT | input | PROFMULT.TEMPSCH | Associated temperature adjustment schedule (only for a load schedule). This field is optional. | String |  |  |  | SCHED
4600 | Global Object | Load Category | LDCAT | input | PROFMULT.XAXTYPE | Type of value on x axis (time for a load schedule) | String |  |  |  | SCHED
4601 | Global Object | Load Category | LDCAT | input | PROFMULT.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4602 | Global Object | Load Category | LDCAT | input | PROFMULT.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4603 | Global Object | Load Category | LDCAT | input | PROFMULT.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4604 | Global Object | Load Category | LDCAT | input | PROFMULT.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4605 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALEE | Manual load to voltage coefficient D | Boolean
4606 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALENABLED | Flag indicating whether manual load voltage coefficients A to F are enabled. | Boolean
4607 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALF | Manual entry coefficient F. | Float
4608 | Global Object | Load Category | LDCAT |  | LOADVOLTMANUALFF | Manual load to voltage coefficient F | Boolean
4609 | Global Object | Load Category | LDCAT | input | NAME | Object name | String |  |  |  | DNMOBJ
4610 | Global Object | Load Category | LDCAT |  | NMDAYINT | The number of daily study mode historical load data major intervals (for use by study DPF). | Integer
4611 | Global Object | Load Category | LDCAT |  | NMSUBINT | The number of subintervals for the study interval (time intervals do not have to be consecutive, interval may cover 9–11 AM and 3–5 PM). | Integer
4612 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTA | Nominal coefficient A of associated load to voltage sensitivity coefficient schedule. | Float
4613 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTB | Nominal coefficient B of associated load to voltage sensitivity coefficient schedule. | Float
4614 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTC | Nominal coefficient C of associated load to voltage sensitivity coefficient schedule. | Float
4615 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTD | Nominal coefficient D of associated load to voltage sensitivity coefficient schedule. | Float
4616 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTE | Nominal coefficient E of associated load to voltage sensitivity coefficient schedule. | Float
4617 | Global Object | Load Category | LDCAT |  | NORMINALLOADVOLTF | Nominal coefficient F of associated load to voltage sensitivity coefficient schedule. | Float
4618 | Global Object | Load Category | LDCAT | input | VOLTSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
4619 | Global Object | Load Category | LDCAT | input | VOLTSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
4620 | Global Object | Load Category | LDCAT | input | VOLTSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
4621 | Global Object | Load Category | LDCAT | input | VOLTSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
4622 | Global Object | Load Category | LDCAT | input | VOLTSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
4623 | Global Object | Load Category | LDCAT | input | VOLTSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
4624 | Global Object | Load Category | LDCAT | input | VOLTSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
4625 | Global Object | Load Category | LDCAT | input | VOLTSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
4626 | Global Object | Load Category | LDCAT | input | VOLTSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
4627 | Global Object | Load Category | LDCAT | input | VOLTSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
4628 | Global Object | Load Category | LDCAT | input | VOLTSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
4629 | Global Object | Load Category | LDCAT | input | VOLTSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
4630 | Global Object | Load Category | LDCAT | input | VOLTSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
4631 | Global Object | Load Category | LDCAT |  | NUMLDSCH | The number of associated load schedules. | Integer
4632 | Global Object | Load Category | LDCAT |  | OPTVEMGHIGH | Optimization emergency high voltage limit | Integer
4633 | Global Object | Load Category | LDCAT |  | OPTVEMGLOW | Optimization emergency low voltage limit | Integer
4634 | Global Object | Load Category | LDCAT |  | OPTVNRMHIGH | Optimization normal high voltage limit | Integer
4635 | Global Object | Load Category | LDCAT |  | OPTVNRMLOW | Optimization normal low voltage limit | Integer
4636 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4637 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4638 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4639 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4640 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4641 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4642 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NAME | Name of the object | String |  |  |  | DNMOBJ
4643 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4644 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4645 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4646 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NUMCUST | Customer count | Integer |  |  |  | LOAD
4647 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NUMREGDT | The number of regular day types | Integer |  |  |  | LOAD
4648 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.NUMSTBIN | The total number of historical data bins for study mode | Integer |  |  |  | LOAD
4649 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.PNOMA | Nominal phase A real power demand | Float |  | kW | kW | LOAD
4650 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.PNOMB | Nominal phase B real power demand | Float |  | kW | kW | LOAD
4651 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.PNOMC | Nominal phase C real power demand | Float |  | kW | kW | LOAD
4652 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.PRIMCONN | Composite flag (mask) | Integer |  |  |  | LOAD
4653 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.QNOMA | Nominal phase A reactive power demand | Float |  | kW | kW | LOAD
4654 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.QNOMB | Nominal phase B reactive power demand | Float |  | kW | kW | LOAD
4655 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.QNOMC | Nominal phase C reactive power demand | Float |  | kW | kW | LOAD
4656 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.STDELTAC | The load delta iteration counter | Integer |  |  |  | LOAD
4657 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.STDELTAP | The values of the schedule correction factors for power | String |  |  |  | LOAD
4658 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.STDELTAQ | The values of the schedule correction factors for reactive power | String |  |  |  | LOAD
4659 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.SUPPLIER | Energy supplier | Integer |  |  |  | LOAD
4660 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4661 | Global Object | Load Category | LDCAT |  | PCOSTINT | Value of uninterrupted service ($/kW). | Float
4662 | Global Object | Load Category | LDCAT |  | PEAKLOAD | Flag indicating the load P and Q nominal values represent peak values (true = peak). | Boolean
4663 | Global Object | Load Category | LDCAT | input | PROFMULT | Pointer to the associated profile multiplier schedule | String
4664 | Global Object | Load Category | LDCAT |  | REACTSCH | Flag indicating the reactive power schedule is given (true = reactive power schedule is given, false = power factor schedule is given). | Boolean
4665 | Global Object | Load Category | LDCAT |  | SCHEDMULTIPLIERNAME | Schedule multiplier name | String
4666 | Global Object | Load Category | LDCAT |  | SCHEDMULTIPLIERP | Schedule multiplier real power | String
4667 | Global Object | Load Category | LDCAT |  | SCHEDMULTIPLIERQ | Schedule multiplier reactive power | String
4668 | Global Object | Load Category | LDCAT |  | STARTTM | Subinterval start times (hours). | Float
4669 | Global Object | Load Category | LDCAT |  | STATIONNAME | Nominal station name. | String
4670 | Global Object | Load Category | LDCAT |  | VEMGHIGH | Emergency high voltage limit (per unit or configurable voltage base). | Float
4671 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4672 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4673 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4674 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4675 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
4676 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4677 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NAME | Name of the object | String |  |  |  | DNMOBJ
4678 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4679 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4680 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4681 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NUMCUST | Customer count | Integer |  |  |  | LOAD
4682 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NUMREGDT | The number of regular day types | Integer |  |  |  | LOAD
4683 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.NUMSTBIN | The total number of historical data bins for study mode | Integer |  |  |  | LOAD
4684 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.PNOMA | Nominal phase A real power demand | Float |  | kW | kW | LOAD
4685 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.PNOMB | Nominal phase B real power demand | Float |  | kW | kW | LOAD
4686 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.PNOMC | Nominal phase C real power demand | Float |  | kW | kW | LOAD
4687 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.PRIMCONN | Composite flag (mask) | Integer |  |  |  | LOAD
4688 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.QNOMA | Nominal phase A reactive power demand | Float |  | kW | kW | LOAD
4689 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.QNOMB | Nominal phase B reactive power demand | Float |  | kW | kW | LOAD
4690 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.QNOMC | Nominal phase C reactive power demand | Float |  | kW | kW | LOAD
4691 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.STDELTAC | The load delta iteration counter | Integer |  |  |  | LOAD
4692 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.STDELTAP | The values of the schedule correction factors for power | String |  |  |  | LOAD
4693 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.STDELTAQ | The values of the schedule correction factors for reactive power | String |  |  |  | LOAD
4694 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.SUPPLIER | Energy supplier | Integer |  |  |  | LOAD
4695 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
4696 | Global Object | Load Category | LDCAT |  | VEMGLOW | Emergency low voltage limit (per unit or configurable voltage base). | Float
4697 | Global Object | Load Category | LDCAT |  | VIMBAL | Voltage imbalance limit for three-phase loads (percent). | Float
4698 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4699 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
4700 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
4701 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.CURROPEN | Current open status | Boolean |  |  |  | SWT
4702 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
4703 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4704 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4705 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
4706 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
4707 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
4708 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.NAME | Name of the object | String |  |  |  | DNMOBJ
4709 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4710 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
4711 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.NOPEN | Normally Open | Boolean |  |  |  | SWT
4712 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
4713 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.REMOTE | Remote | Boolean |  |  |  | SWT
4714 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
4715 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
4716 | Global Object | Load Category | LDCAT |  | VNRMHIGH | Normal high voltage limit (per unit or configurable voltage base). | Float
4717 | Global Object | Load Category | LDCAT |  | VNRMLOW | Normal low voltage limit (per unit or configurable voltage base). | Float
4718 | Global Object | Load Category | LDCAT |  | VOLTAGEBASE | Voltage Base value | Float
4719 | Global Object | Load Category | LDCAT |  | VOLTSCH | Associated transformer secondary voltage drop schedule (as a function of transformer loading). | String
4720 | Global Object | Load Category | LDCAT |  | VOLTUNIT | Enumerated units flag for the six voltage limits. The enumeration has the following values: 1 = per unit, 2 = Voltage on a configurable voltage base. | Boolean
4721 | Global Object | Load Category | LDCAT |  | VSTBHIGH | Load stability high voltage limit (per unit or configurable voltage base). | Float
4722 | Global Object | Load Category | LDCAT |  | VSTBLOW | Load stability low voltage limit (per unit or configurable voltage base). | Float
4723 | Global Object | Load Category | LDCAT |  | VUBFCOST | Voltage imbalance limit violation cost | Float
4724 | DNOM Component Placement | Label Placement | LDLBPL | input | LOAD | Pointer to the associated load | String
4725 | Global Object | Load Limit | LDLIM | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
4726 | DNOM Component | Load Output | LDOUT |  | LIMFLAGS | Limit violations flag | Integer
4727 | DNOM Component | Load Output | LDOUT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
4728 | DNOM Component | Load Output | LDOUT |  | PQIHIGH | High PQI violation | Float
4729 | DNOM Component | Load Output | LDOUT |  | PQIIMBAL | PQI imbalance violation | Float
4730 | DNOM Component | Load Output | LDOUT |  | PQILOW | Low PQI violation | Float
4731 | DNOM Component | Load Output | LDOUT |  | VIMBAL | Voltage imbalance factor | Integer
4732 | DNOM Component | Load Output | LDOUT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
4733 | DNOM Component | Load Output | LDOUT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
4734 | DNOM Component Placement | Load Placement | LDPLE | input | LOAD | Pointer to the associated load | String
4735 | DNOM Component Placement | Loop End Label Placement | LELPLE |  | ID | Unique identifier for the loop end label | String
4736 | DNOM Component Placement | Loop End Label Placement | LELPLE | input | LPFUSE | Pointer to the associated fuse | String
4737 | DNOM Component Placement | Loop End Label Placement | LELPLE |  | SCHEMEID | Display callup parameter identifying the specific horseshoe diagram to be called up when the loop label is selected. This field will only need to be set when multiple loops need to be shown on the same horseshoe diagram. | String
4738 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDCAPSTATS | Capacitor status | Integer
4739 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDCURRENT | Current violation | Integer
4740 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDHASCURRENT | A flag indicating the current violation | Integer
4741 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDHASHIGHVOLTAGE | A flag indicating the high voltage violation | Integer
4742 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDHASLOWVOLTAGE | A flag indicating the low voltage violation | Integer
4743 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDNMCPSTAT | The number of capacitors that have their status calculated and recorded | Integer
4744 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDNMTAPSTEPS | The number of tap changer steps | Integer
4745 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDTAPSTEPS | Tap changer step | Integer
4746 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDVOLTHIGH | High voltage violation | Integer
4747 | DNAF Object | Look Ahead Hour Result | LKAHRS |  | LKAHDVOLTLOW | Low voltage violation | Integer
4748 | DNOM Component | Line | LN | output | AMPA | From end phase A amp flow (magnitude and no angle). | String | DPF | Amps | Amps
4749 | DNOM Component | Line | LN | input | AMPALIMIT | Line Phase A limit value (amp or kVA) | Float
4750 | DNOM Component | Line | LN | output | AMPANDANGLEA | From end phase A amp flow (magnitude and angle). | Float | DPF | Amps | Amps
4751 | DNOM Component | Line | LN | output | AMPANDANGLEB | From end phase B amp flow (magnitude and angle). | Float | DPF | Amps | Amps
4752 | DNOM Component | Line | LN | output | AMPANDANGLEC | From end phase C amp flow (magnitude and angle). | Float | DPF | Amps | Amps
4753 | DNOM Component | Line | LN | output | AMPANDANGLEN | From end phase N amp flow (magnitude and angle). | Float | DPF | Amps | Amps
4754 | DNOM Component | Line | LN | output | AMPANDANGLENEUT | Vector Sum of the Amp flow on the Individual phases on the From Side (magnitude and angle) | Float | DPF
4755 | DNOM Component | Line | LN | output | AMPB | From end phase B amp flow (magnitude and no angle). | String | DPF | Amps | Amps
4756 | DNOM Component | Line | LN | input | AMPBLIMIT | Line Phase B limit value (amp of kVA) | Float
4757 | DNOM Component | Line | LN | output | AMPC | From end phase C amp flow (magnitude and no angle). | String | DPF | Amps | Amps
4758 | DNOM Component | Line | LN | input | AMPCLIMIT | Line Phase C limit (amp or kVA) | Float
4759 | DNOM Component | Line | LN | input | PHASEAFLOWVALUE | The individual phase flow value for phase A | Float | DPF | Amps | Amps
4760 | DNOM Component | Line | LN | input | PHASEBFLOWVALUE | The individual phase flow value for phase B | Float | DPF | Amps | Amps
4761 | DNOM Component | Line | LN | input | PHASECFLOWVALUE | The individual phase flow value for phase C | Float | DPF | Amps | Amps
4762 | DNOM Component | Line | LN | input | AREAIND | Integer (index) into station permission area list | Integer
4763 | DNOM Component | Line | LN | output | AVGAMPA | Phase A average injected current ("from" and "to" ends) | Float | DPF | Amps | Amps
4764 | DNOM Component | Line | LN | input | FAULTIND.ADDRESS.NOAPPSTR | Address. | String
4765 | DNOM Component | Line | LN | input | FAULTIND.ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String |  |  |  | OSMQUERYDEVICE
4766 | DNOM Component | Line | LN | input | FAULTIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
4767 | DNOM Component | Line | LN | input | FAULTIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4768 | DNOM Component | Line | LN | input | FAULTIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
4769 | DNOM Component | Line | LN |  | FAULTIND.DIRECTIONAL | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
4770 | DNOM Component | Line | LN |  | FAULTIND.DIRECTIONALFAULTIND | Incicates if the fault indicator is directional | Boolean |  |  |  | FLTIND
4771 | DNOM Component | Line | LN | input | FAULTIND.DNOMRECORDNAME | The DNOM record name of the fault indicator | String |  |  |  | FLTIND
4772 | DNOM Component | Line | LN | input | FAULTIND.DNOMX | Horizontal coordinate of DNOM object | Float |  |  |  | DNMOBJ
4773 | DNOM Component | Line | LN | input | FAULTIND.DNOMY | Vertical coordinate of DNOM object | Float |  |  |  | DNMOBJ
4774 | DNOM Component | Line | LN | input | FAULTIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
4775 | DNOM Component | Line | LN |  | FAULTIND.FAULTINDABNORMAL | Indicates if the fault indicator has abnormal status | Boolean |  |  |  | FLTIND
4776 | DNOM Component | Line | LN |  | FAULTIND.FAULTINDLIGHTCOLOR | Fault indicator light color | String |  |  |  | FLTIND
4777 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDPHASEA | Flag indicating whether phase A exists in the indicator. | Boolean |  |  |  | FLTIND
4778 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDPHASEB | Flag indicating whether phase B exists in the indicator. | Boolean |  |  |  | FLTIND
4779 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDPHASEC | Flag indicating whether phase C exists in the indicator. | Boolean |  |  |  | FLTIND
4780 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDPHASEN | Flag indicating whether phase N exists in the indicator. | Boolean |  |  |  | FLTIND
4781 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDPHASING | Fault indicator phasing. | String |  |  |  | FLTIND
4782 | DNOM Component | Line | LN |  | FAULTIND.FAULTINDQUALITY | Quality of the SCADA measurement from the fault indicator (e.g., Good, Bad, or Suspect) | String |  |  |  | FLTIND
4783 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDREMOTE | The control status of fault indicator. Return "MANUAL" or "REMOTE". | String |  |  |  | FLTIND
4784 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDSETSTATUS | The status of fault indicator. Return "SET" or "UNSET". | String |  |  |  | FLTIND
4785 | DNOM Component | Line | LN | input | FAULTIND.FAULTINDSETSTATUSPHASE | Phases that are currently set (faulted). | String |  |  |  | FLTIND
4786 | DNOM Component | Line | LN |  | FAULTIND.FINDVOLTLEVEL | Fault indicator line to line and line to ground voltage levels | Float |  | kV | kV | FIND
4787 | DNOM Component | Line | LN |  | FAULTIND.FLTINDMEAS | Fault indicator measurement | String |  |  |  | FLTIND
4788 | DNOM Component | Line | LN |  | FAULTIND.FLTINDMEASA | SCADA measurement of the fault indicator phase A status (Set/Unset) | String |  |  |  | FLTIND
4789 | DNOM Component | Line | LN |  | FAULTIND.FLTINDMEASB | SCADA measurement of the fault indicator phase B status (Set/Unset) | String |  |  |  | FLTIND
4790 | DNOM Component | Line | LN |  | FAULTIND.FLTINDMEASC | SCADA measurement of the fault indicator phase C status (Set/Unset) | String |  |  |  | FLTIND
4791 | DNOM Component | Line | LN |  | FAULTIND.FLTINDMEASG | SCADA measurement of the fault indicator ground status (Set/Unset) | String |  |  |  | FLTIND
4792 | DNOM Component | Line | LN | input | FAULTIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | String |  |  |  | COMELC
4793 | DNOM Component | Line | LN | input | FAULTIND.ID | Unique and persistent ID. | String |  |  |  | DNMOBJ
4794 | DNOM Component | Line | LN | input | FAULTIND.ISDYNFEEDERLOOPED | Flag indicating whether the fault indicator's dynamic feeder is in loop. | Boolean |  |  |  | FLTIND
4795 | DNOM Component | Line | LN | input | FAULTIND.NAME | Name. | String |  |  |  | DNMOBJ
4796 | DNOM Component | Line | LN |  | FAULTIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
4797 | DNOM Component | Line | LN | input | FAULTIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
4798 | DNOM Component | Line | LN | input | FAULTIND.SERVCNTR.NAME | Service center. | String
4799 | DNOM Component | Line | LN |  | FAULTIND.TELEMETEREDFAULTIND | Indicates if the fault indicator is telemetered | Boolean |  |  |  | FLTIND
4800 | DNOM Component | Line | LN | output | AVGAMPB | Phase B average injected current ("from" and "to" ends) | Float | DPF | Amps | Amps
4801 | DNOM Component | Line | LN | output | AVGAMPC | Phase C average injected current ("from" and "to" ends) | Float | DPF | Amps | Amps
4802 | DNOM Component | Line | LN | output | AVGKVAR3PH | Average three-phase power (kVAR) for from and to end. A negative value indicates flow is towards the source. | Float | DPF
4803 | DNOM Component | Line | LN | output | AVGKW3PH | Average three-phase power (kW) for from and to end. | Float | DPF | kW | kW
4804 | DNOM Component | Line | LN | output | AVGVOLTA | Average phase A voltage (configurable voltage base) for from and to end. | Float | DPF | Volt | Volt
4805 | DNOM Component | Line | LN | output | AVGVOLTB | Average phase B voltage (configurable voltage base) for from and to end. | Float | DPF | Volt | Volt
4806 | DNOM Component | Line | LN | output | AVGVOLTC | Average phase C voltage (configurable voltage base) for from and to end. | Float | DPF | Volt | Volt
4807 | DNOM Component | Line | LN |  | BITMASK | Line bitmask | String
4808 | DNOM Component | Line | LN | input | BOUNDARY | Flag indicating if the line is a boundary between two stations. | Boolean
4809 | DNOM Component | Line | LN | input | BRANCHENERGIZED | Phases energized. | String
4810 | DNOM Component | Line | LN | input | BRANCHREMTOP | Phases that are removed from topology due to multiple source energization. | String
4811 | DNOM Component | Line | LN | input | COMPTFHASPETSCOIL | Specifies whether the power transformers that the line is associated with has an arc suppression coil fault indicator connected to the secondary side | Float
4812 | DNOM Component | Line | LN | input | CONSTRUCTPHASES | Constructed Phase | String
4813 | DNOM Component | Line | LN | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
4814 | DNOM Component | Line | LN | input | DNOMTABNAME | Special DNOM Object name - tabular support | String
4815 | DNOM Component | Line | LN | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
4816 | DNOM Component | Line | LN | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
4817 | DNOM Component | Line | LN | input | DYNFEEDERALTLINE | Feeder alias (alternate name) | String
4818 | DNOM Component | Line | LN | input | DYNFEEDERLINE | Dynamic (energizing) feeder name. | String
4819 | DNOM Component | Line | LN | input | DYNSTATIONNAME | Dynamic (currently energizing) station name. | String
4820 | DNOM Component | Line | LN | input | FAULTIND | Pointer to the fault indicator object | String
4821 | DNOM Component | Line | LN | input | FAULTINDHALOCOMBINED | Phases with combined fault indicator halo | Boolean
4822 | DNOM Component | Line | LN | input | FAULTINDHALOMANUAL | Phases with manual fault indicator halo | Boolean
4823 | DNOM Component | Line | LN | input | FAULTINDHALOTELEMETERED | Phases with telemetered fault indicator halo | Boolean
4824 | DNOM Component | Line | LN |  | FEEDERBREAKERCK | Name of the energizing substation, energizing feeder breaker, and status point. Used for the Locate Dynamic Feeder Breaker on SCADA Oneline toolbar option. | String
4825 | DNOM Component | Line | LN | input | FEEDERMAIN | Flag indicating if the line is on feeder main. | Boolean
4826 | DNOM Component | Line | LN | input | FEEDERNAME | Nominal owning feeder name. | String
4827 | DNOM Component | Line | LN | input | FRAMEMODNAME | Construction (framing) model name. | String
4828 | DNOM Component | Line | LN | output | FRLNCURRENTVECTORSUM | From end current flow vector sum (phases A, B, and C). | Complex | DPF | Amps | Amps
4829 | DNOM Component | Line | LN | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
4830 | DNOM Component | Line | LN | input | FROMNODE | Line from-node name | String
4831 | DNOM Component | Line | LN | output | FROMNODEKVARA | To end phase A real power flow (kW). | Float | DPF | kVAR | kVAR
4832 | DNOM Component | Line | LN | output | FROMNODEKVARB | To end phase B real power flow (kW). | Float | DPF | kVAR | kVAR
4833 | DNOM Component | Line | LN | output | FROMNODEKVARC | To end phase C real power flow (kW). | Float | DPF | kVAR | kVAR
4834 | DNOM Component | Line | LN | output | FROMNODEKWA | From end phase A real power flow (kW). | Float | DPF | kW | kW
4835 | DNOM Component | Line | LN | output | FROMNODEKWB | From end phase B real power flow (kW). | Float | DPF | kW | kW
4836 | DNOM Component | Line | LN | output | FROMNODEKWC | From end phase C real power flow (kW). | Float | DPF | kW | kW
4837 | DNOM Component | Line | LN | input | HASENERGYSOURCE | Had energy resource connected? | Boolean
4838 | DNOM Component | Line | LN |  | HASMANUALENTRY | Indicates if the operator manually entered parameters for the line | Boolean
4839 | DNOM Component | Line | LN | input | ID | Object unique ID | String |  |  |  | DNMOBJ
4840 | DNOM Component | Line | LN | input | ISDYNFEEDERLOOPED | Dynamic Feeder is Looped | String
4841 | DNOM Component | Line | LN | input | ISRTAFRVALID | Specifies whether AFR is enabled for RT | Boolean
4842 | DNOM Component | Line | LN | input | ISRTDPFVALID | Specifies whether DPF is enabled for RT | Boolean
4843 | DNOM Component | Line | LN | input | ISRTFISRVALID | Specifies whether FISR is enabled for RT | Boolean
4844 | DNOM Component | Line | LN | input | ISRTFLVALID | Specifies whether FL is enabled for RT | Boolean
4845 | DNOM Component | Line | LN | input | ISRTLVMVALID | Specifies whether LVM is enabled for RT | Boolean
4846 | DNOM Component | Line | LN | input | ISRTPRVVALID | Specifies whether PRV is enabled for RT | Boolean
4847 | DNOM Component | Line | LN | input | ISRTSCCVALID | Specifies whether SCC is enabled for RT | Boolean
4848 | DNOM Component | Line | LN | input | ISSIMDPFVALID | Specifies whether DPF is enabled for SIM | Boolean
4849 | DNOM Component | Line | LN | input | ISSIMFLVALID | Specifies whether FL is enabled for SIM | Boolean
4850 | DNOM Component | Line | LN | input | ISSTAFRVALID | Specifies whether AFR is enabled for ST | Boolean
4851 | DNOM Component | Line | LN | input | ISSTDPFVALID | Specifies whether DPF is enabled for ST | Boolean
4852 | DNOM Component | Line | LN | input | ISSTFISRCAVALID | Specifies whether FISRCA is enabled for RT | Boolean
4853 | DNOM Component | Line | LN | input | ISSTFISRVALID | Specifies whether FISR is enabled for ST | Boolean
4854 | DNOM Component | Line | LN | input | ISSTFLVALID | Specifies whether FL is enabled for ST | Boolean
4855 | DNOM Component | Line | LN | input | ISSTLVMVALID | Specifies whether LVM is enabled for ST | Boolean
4856 | DNOM Component | Line | LN | input | ISSTPLOSVALID | Specifies whether PLOS is enabled for ST | Boolean
4857 | DNOM Component | Line | LN | input | ISSTPRVVALID | Specifies whether PRV is enabled for ST | Boolean
4858 | DNOM Component | Line | LN | input | ISSTSCCVALID | Specifies whether SCC is enabled for ST | Boolean
4859 | DNOM Component | Line | LN | output | KVAR3PH | From end total reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
4860 | DNOM Component | Line | LN | input | KVLLNOM | Operating voltage level (kV line to line). | Float
4861 | DNOM Component | Line | LN | output | KW3PH | From end total real power flow (kW). | Float | DPF | kW | kW
4862 | DNOM Component | Line | LN | input | LENGTH | Line length (feet/meters). | Float
4863 | DNOM Component | Line | LN | input | LINEABNORMAL | Phases currently abnormally energized. | String
4864 | DNOM Component | Line | LN | input | LINEADMITTANCE | Shunt admittance (G + jB in microSiemens). | Complex
4865 | DNOM Component | Line | LN | output | LINEALLPHASESENERGIZED | Flag indicating whether all phases are energized | Boolean | NTP | #N/A | #N/A
4866 | DNOM Component | Line | LN | input | LINECONDMODA | phase A conductor model name | String
4867 | DNOM Component | Line | LN | input | LINECONDMODB | phase B conductor model name | String
4868 | DNOM Component | Line | LN | input | LINECONDMODC | phase C conductor model name | String
4869 | DNOM Component | Line | LN | input | LINECONDMODN | phase N conductor model name | String
4870 | DNOM Component | Line | LN | input | LINECONDSIZEA | Phase A conductor size. | String
4871 | DNOM Component | Line | LN | input | LINECONDSIZEB | Phase B conductor size. | String
4872 | DNOM Component | Line | LN | input | LINECONDSIZEC | Phase C conductor size. | String
4873 | DNOM Component | Line | LN | input | LINECONDSIZEN | Phase N conductor size. | String
4874 | DNOM Component | Line | LN | input | LINECONDTYPEA | Phase A conductor type. | String
4875 | DNOM Component | Line | LN | input | LINECONDTYPEB | Phase B conductor type. | String
4876 | DNOM Component | Line | LN | input | LINECONDTYPEC | Phase C conductor type. | String
4877 | DNOM Component | Line | LN | input | LINECONDTYPEN | Phase N conductor type. | String
4878 | DNOM Component | Line | LN | input | LINEDERATEDLIM1A | Line derated limit 1 phase A | String |  | Amps | Amps
4879 | DNOM Component | Line | LN | input | LINEDERATEDLIM1B | Line derated limit 1 phase B | String |  | Amps | Amps
4880 | DNOM Component | Line | LN | input | LINEDERATEDLIM1C | Line derated limit 1 phase C | String |  | Amps | Amps
4881 | DNOM Component | Line | LN | input | LINEDERATEDLIM2A | Line derated limit 2 phase A | String |  | Amps | Amps
4882 | DNOM Component | Line | LN | input | LINEDERATEDLIM2B | Line derated limit 2 phase B | String |  | Amps | Amps
4883 | DNOM Component | Line | LN | input | LINEDERATEDLIM2C | Line derated limit 2 phase C | String |  | Amps | Amps
4884 | DNOM Component | Line | LN | input | LINEDERATEDLIM3A | Line derated limit 3 phase A | String |  | Amps | Amps
4885 | DNOM Component | Line | LN | input | LINEDERATEDLIM3B | Line derated limit 3 phase B | String |  | Amps | Amps
4886 | DNOM Component | Line | LN | input | LINEDERATEDLIM3C | Line derated limit 3 phase C | String |  | Amps | Amps
4887 | DNOM Component | Line | LN | input | LINEDERATEDLIM4A | Line derated limit 4 phase A | String |  | Amps | Amps
4888 | DNOM Component | Line | LN | input | LINEDERATEDLIM4B | Line derated limit 4 phase B | String |  | Amps | Amps
4889 | DNOM Component | Line | LN | input | LINEDERATEDLIM4C | Line derated limit 4 phase C | String |  | Amps | Amps
4890 | DNOM Component | Line | LN | input | LINEDERATEDLIM5A | Line derated limit 5 phase A | String |  | Amps | Amps
4891 | DNOM Component | Line | LN | input | LINEDERATEDLIM5B | Line derated limit 5 phase B | String |  | Amps | Amps
4892 | DNOM Component | Line | LN | input | LINEDERATEDLIM5C | Line derated limit 5 phase C | String |  | Amps | Amps
4893 | DNOM Component | Line | LN | output | LINEENERGIZEDA | Flag indicating whether PhaseA is energized | Boolean | NTP | #N/A | #N/A
4894 | DNOM Component | Line | LN | output | LINEENERGIZEDB | Flag indicating whether PhaseB is energized | Boolean | NTP | #N/A | #N/A
4895 | DNOM Component | Line | LN | output | LINEENERGIZEDC | Flag indicating whether PhaseC is energized | Boolean | NTP | #N/A | #N/A
4896 | DNOM Component | Line | LN | output | LINEFAULTAMPSA | Calculated phase A breaker fault current (amps). | Float | FL | amps | amps
4897 | DNOM Component | Line | LN | output | LINEFAULTAMPSB | Calculated phase B breaker fault current (amps). | Float | FL | amps | amps
4898 | DNOM Component | Line | LN | output | LINEFAULTAMPSC | Calculated phase C breaker fault current (amps). | Float | FL | amps | amps
4899 | DNOM Component | Line | LN | input | LINEFRAMEMOD | Construction Type | String
4900 | DNOM Component | Line | LN | output | LINEFROMA | Line phaseA voltage in from node | Float
4901 | DNOM Component | Line | LN | output | LINEFROMB | Line phaseB voltage in from node | Float
4902 | DNOM Component | Line | LN | output | LINEFROMC | Line phaseC voltage in from node | Float
4903 | DNOM Component | Line | LN | input | LINEFUTURE | Phases that are part of future construction . | String
4904 | DNOM Component | Line | LN | input | LINEIMPEDANCE | Series self impedance (R + jX in ohms). | Complex
4905 | DNOM Component | Line | LN | input | LINEISURDLOOP | Flag indicating construction is underground | Boolean
4906 | DNOM Component | Line | LN |  | LINELABELPLACEMENTTXT | Line label placement text | String
4907 | DNOM Component | Line | LN | input | LINELIM1A | Level 1 phase A flow limit. | Float
4908 | DNOM Component | Line | LN | input | LINELIM1B | Level 1 phase B flow limit. | Float
4909 | DNOM Component | Line | LN | input | LINELIM1C | Level 1 phase C flow limit. | Float
4910 | DNOM Component | Line | LN |  | LINELIM1N | Limit 1 name | String
4911 | DNOM Component | Line | LN | input | LINELIM1NAME | Level 1 limit name. | String
4912 | DNOM Component | Line | LN | input | LINELIM1SEASON | Level 1 limit season name. | String
4913 | DNOM Component | Line | LN | input | LINELIM2A | Level 2 phase A flow limit. | Float
4914 | DNOM Component | Line | LN | input | LINELIM2B | Level 2 phase B flow limit. | Float
4915 | DNOM Component | Line | LN | input | LINELIM2C | Level 2 phase C flow limit. | Float
4916 | DNOM Component | Line | LN |  | LINELIM2N | Limit 2 name | String
4917 | DNOM Component | Line | LN | input | LINELIM2NAME | Level 2 limit name. | String
4918 | DNOM Component | Line | LN | input | LINELIM2SEASON | Level 2 limit season name. | String
4919 | DNOM Component | Line | LN | input | LINELIM3A | Level 3 phase A flow limit. | Float
4920 | DNOM Component | Line | LN | input | LINELIM3B | Level 3 phase B flow limit. | Float
4921 | DNOM Component | Line | LN | input | LINELIM3C | Level 3 phase C flow limit. | Float
4922 | DNOM Component | Line | LN |  | LINELIM3N | Limit 3 name | String
4923 | DNOM Component | Line | LN | input | LINELIM3NAME | Level 3 limit name. | String
4924 | DNOM Component | Line | LN | input | LINELIM3SEASON | Level 3 limit season name. | String
4925 | DNOM Component | Line | LN | input | LINELIM4A | Level 4 phase A flow limit. | Float
4926 | DNOM Component | Line | LN | input | LINELIM4B | Level 4 phase B flow limit. | Float
4927 | DNOM Component | Line | LN | input | LINELIM4C | Level 4 phase C flow limit. | Float
4928 | DNOM Component | Line | LN |  | LINELIM4N | Limit 4 name | String
4929 | DNOM Component | Line | LN | input | LINELIM4NAME | Level 4 limit name. | String
4930 | DNOM Component | Line | LN | input | LINELIM4SEASON | Level 4 limit season name. | String
4931 | DNOM Component | Line | LN | input | LINELIM5A | Level 5 phase A flow limit. | Float
4932 | DNOM Component | Line | LN | input | LINELIM5B | Level 5 phase B flow limit. | Float
4933 | DNOM Component | Line | LN | input | LINELIM5C | Level 5 phase C flow limit. | Float
4934 | DNOM Component | Line | LN |  | LINELIM5N | Limit 5 name | String
4935 | DNOM Component | Line | LN | input | LINELIM5NAME | Level 5 limit name. | String
4936 | DNOM Component | Line | LN | input | LINELIM5SEASON | Level 5 limit season name. | String
4937 | DNOM Component | Line | LN | input | LINELOOPED | Phases currently in a loop. | String
4938 | DNOM Component | Line | LN | output | LINEMODNAME | Line model name | String
4939 | DNOM Component | Line | LN | input | LINENEGSEQUENCEIMPEDANCE | Line negative sequence impedances | Complex
4940 | DNOM Component | Line | LN | input | LINENOMLIM1A | Line limit 1 nominal value phase A | String
4941 | DNOM Component | Line | LN | input | LINENOMLIM1B | Line limit 1 nominal value phase B | String
4942 | DNOM Component | Line | LN | input | LINENOMLIM1C | Line limit 1 nominal value phase C | String
4943 | DNOM Component | Line | LN | input | LINENOMLIM1N | Line limit 1 nominal value phase N | String
4944 | DNOM Component | Line | LN | input | LINENOMLIM2A | Line limit 2 nominal value phase A | String
4945 | DNOM Component | Line | LN | input | LINENOMLIM2B | Line limit 2 nominal value phase B | String
4946 | DNOM Component | Line | LN | input | LINENOMLIM2C | Line limit 2 nominal value phase C | String
4947 | DNOM Component | Line | LN | input | LINENOMLIM2N | Line limit 2 nominal value phase N | String
4948 | DNOM Component | Line | LN | input | LINENOMLIM3A | Line limit 3 nominal value phase A | String
4949 | DNOM Component | Line | LN | input | LINENOMLIM3B | Line limit 3 nominal value phase B | String
4950 | DNOM Component | Line | LN | input | LINENOMLIM3C | Line limit 3 nominal value phase C | String
4951 | DNOM Component | Line | LN | input | LINENOMLIM3N | Line limit 3 nominal value phase N | String
4952 | DNOM Component | Line | LN | input | LINENOMLIM4A | Line limit 4 nominal value phase A | String
4953 | DNOM Component | Line | LN | input | LINENOMLIM4B | Line limit 4 nominal value phase B | String
4954 | DNOM Component | Line | LN | input | LINENOMLIM4C | Line limit 4 nominal value phase C | String
4955 | DNOM Component | Line | LN | input | LINENOMLIM4N | Line limit 4 nominal value phase N | String
4956 | DNOM Component | Line | LN | input | LINENOMLIM5A | Line limit 5 nominal value phase A | String
4957 | DNOM Component | Line | LN | input | LINENOMLIM5B | Line limit 5 nominal value phase B | String
4958 | DNOM Component | Line | LN | input | LINENOMLIM5C | Line limit 5 nominal value phase C | String
4959 | DNOM Component | Line | LN | input | LINENOMLIM5N | Line limit 5 nominal value phase N | String
4960 | DNOM Component | Line | LN | input | LINEOVERHEAD | Flag indicating construction is overhead | Boolean
4961 | DNOM Component | Line | LN | input | LINEPHSIZETYPE | Line Phase size type | String
4962 | DNOM Component | Line | LN | input | LINERECONFIGURABLE | Indicates if the line is reconfigurable (feeder main component) | Boolean
4963 | DNOM Component | Line | LN | input | LNMODEL.ARTFNEU | A flag indicating that artificial neutral is added | Boolean |  |  |  | LNMOD
4964 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA | Pointer to phase A conductor model | String |  |  |  | LNMODEL
4965 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
4966 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
4967 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
4968 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
4969 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
4970 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
4971 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4972 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
4973 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
4974 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
4975 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
4976 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.ID | Object unique ID | String |  |  |  | DNMOBJ
4977 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
4978 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
4979 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
4980 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
4981 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
4982 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
4983 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4984 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
4985 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4986 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4987 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
4988 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
4989 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
4990 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
4991 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4992 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
4993 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
4994 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
4995 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
4996 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
4997 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
4998 | DNOM Component | Line | LN | input | LNMODEL.CONDMODA.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
4999 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB | Pointer to phase B conductor model | String
5000 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5001 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5002 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5003 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5004 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5005 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5006 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5007 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5008 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5009 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5010 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5011 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.ID | Object unique ID | String |  |  |  | DNMOBJ
5012 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5013 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5014 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5015 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5016 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5017 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5018 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5019 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5020 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5021 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5022 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5023 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5024 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5025 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5026 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5027 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5028 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5029 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5030 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5031 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5032 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5033 | DNOM Component | Line | LN | input | LNMODEL.CONDMODB.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5034 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC | Pointer to phase C conductor model | String
5035 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5036 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5037 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5038 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5039 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5040 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5041 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5042 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5043 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5044 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5045 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5046 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.ID | Object unique ID | String |  |  |  | DNMOBJ
5047 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5048 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5049 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5050 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5051 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5052 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5053 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5054 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5055 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5056 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5057 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5058 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5059 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5060 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5061 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5062 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5063 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5064 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5065 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5066 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5067 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5068 | DNOM Component | Line | LN | input | LNMODEL.CONDMODC.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5069 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN | Pointer to phase N conductor model | String
5070 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5071 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5072 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5073 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5074 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5075 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5076 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5077 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5078 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5079 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5080 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5081 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.ID | Object unique ID | String |  |  |  | DNMOBJ
5082 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5083 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5084 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5085 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5086 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5087 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5088 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5089 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5090 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5091 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5092 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5093 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5094 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5095 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5096 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5097 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5098 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5099 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5100 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5101 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5102 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5103 | DNOM Component | Line | LN | input | LNMODEL.CONDMODN.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5104 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL | Pointer to associated construction model | String |  |  |  | LNMODEL
5105 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5106 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.bOverhead | Flag indicating overhead vs underground construction (true - overhead) | Boolean |  |  |  | CSTMOD
5107 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.ID | Object unique ID | String |  |  |  | DNMOBJ
5108 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rXPhaseA | X coordinate for conductor on position 1. The X coordinates are referenced to the pole (left/right). Usually, position 1 is the leftmost position, which means its X coordinate is smallest among all positions. | Float |  | meters | feet | CSTMOD
5109 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rXPhaseB | X coordinate for conductor on position 2 | Float |  | meters | feet | CSTMOD
5110 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rXPhaseC | X coordinate for conductor on position 3. Usually, position3 is the rightmost position, which means its X coordinate is the biggest among all positions. | Float |  | meters | feet | CSTMOD
5111 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rXPhaseN | X coordinate for conductor on position N. Usually, this position N is for neutral conductor. | Float |  | meters | feet | CSTMOD
5112 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rYPhaseA | Y coordinate for conductor on position 1. The Y coordinates are referenced to height above ground. | Float |  | meters | feet | CSTMOD
5113 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rYPhaseB | Y coordinate for conductor on position 2. Usually, position2 is the highest position, which means its Y coordinate is biggest among all positions. | Float |  | meters | feet | CSTMOD
5114 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rYPhaseC | Y coordinate for conductor on position 3 | Float |  | meters | feet | CSTMOD
5115 | DNOM Component | Line | LN | input | LNMODEL.FRMODEL.rYPhaseN | Y coordinate for conductor on position N | Float |  | meters | feet | CSTMOD
5116 | DNOM Component | Line | LN | input | LNMODEL.ID | ID | String |  |  |  | DNMOBJ
5117 | DNOM Component | Line | LN | input | LNMODEL.LinePhasing | Line phasing of the model | String |  |  |  | LNMOD
5118 | DNOM Component | Line | LN | input | LNMODEL.NAME | Name | String |  |  |  | DNMOBJ
5119 | DNOM Component | Line | LN | input | LINESEQUENCEADMITTANCE | Line sequence admittance (G + jB in microSiemens) | Complex
5120 | DNOM Component | Line | LN | input | LNPLACE.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
5121 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
5122 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
5123 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
5124 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
5125 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
5126 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
5127 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
5128 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
5129 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
5130 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
5131 | DNOM Component | Line | LN | input | LNPLACE.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
5132 | DNOM Component | Line | LN | input | LNPLACE.GSCOMPALTNAME | Alternate name of the component | String |  |  |  | PLACE
5133 | DNOM Component | Line | LN | input | LNPLACE.GSCOMPGEOMNAME | Name of the geometry | String |  |  |  | PLACE
5134 | DNOM Component | Line | LN | input | LNPLACE.GSCOMPID | ID of the component | String |  |  |  | PLACE
5135 | DNOM Component | Line | LN | input | LNPLACE.GSCOMPNAME | Name of the component | String |  |  |  | PLACE
5136 | DNOM Component | Line | LN | input | LNPLACE.GSSTATIONNAME | Name of the substation | String |  |  |  | PLACE
5137 | DNOM Component | Line | LN | input | LNPLACE.ROTATION | Rotation angle of the placement | Integer |  |  |  | LBPLCE
5138 | DNOM Component | Line | LN | input | LNPLACE.SIZE | Size of the point object | Integer |  |  |  | LBPLCE
5139 | DNOM Component | Line | LN | input | LNPLACE.TEXT | Label text | String |  |  |  | LBPLCE
5140 | DNOM Component | Line | LN | input | LNPLACE.VLCOLOR | Label voltage level color (primarily for switching devices) | Integer |  |  |  | LBPLCE
5141 | DNOM Component | Line | LN | input | LNPLACE.X | X coordinate of the placement | Float |  |  |  | LBPLCE
5142 | DNOM Component | Line | LN | input | LNPLACE.Y | Y coordinate of the placement | Float |  |  |  | LBPLCE
5143 | DNOM Component | Line | LN | input | LINESEQUENCEIMPEDANCE | Line sequence impedances (R + jX in ohms) | Complex
5144 | DNOM Component | Line | LN | output | LINETOA | Line phaseA voltage in to node | Float
5145 | DNOM Component | Line | LN | output | LINETOB | Line phaseB voltage in to node | Float
5146 | DNOM Component | Line | LN | output | LINETOC | Line phaseC voltage in to node | Float
5147 | DNOM Component | Line | LN |  | LINEVERTEXSX | X coordinates of the line vertices | Float
5148 | DNOM Component | Line | LN |  | LINEVERTEXSY | Y coordinates of the line vertices | Float
5149 | DNOM Component | Line | LN | output | LINEVOLTDROPEXCEEDED | Flag if the voltage drop of the line exceed the limit | Boolean
5150 | DNOM Component | Line | LN | input | LINEVOLTDROPLIMT | Line voltage drop limit | Float
5151 | DNOM Component | Line | LN | input | LINEZERSEQUENCEIMPEDANCE | Line zero sequence impedances | Complex
5152 | DNOM Component | Line | LN |  | LNHASMANFLOWLIM | Indicates if the user manually entered the line flow limit | Boolean |  | Amps | Amps
5153 | DNOM Component | Line | LN |  | LNMANFLOWLIM | User entered line flow limit. | String |  | Amps | Amps
5154 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHA | User entered line flow limit of phase A. | String |  | Amps | Amps
5155 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHA_ACTUAL | If user entered line flow limits are enabled, shows the phase A user entered limit. Otherwise shows "--". | String |  | Amps | Amps
5156 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHB | User entered line flow limit of phase B. | String |  | Amps | Amps
5157 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHB_ACTUAL | If user entered line flow limits are enabled, shows the phase B user entered limit. Otherwise shows "--". | String |  | Amps | Amps
5158 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHC | User entered line flow limit of phase C. | String |  | Amps | Amps
5159 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHC_ACTUAL | If user entered line flow limits are enabled, shows the phase C user entered limit. Otherwise shows "--". | String |  | Amps | Amps
5160 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHN | User entered line flow limit at neutral. | String |  | Amps | Amps
5161 | DNOM Component | Line | LN |  | LNMANFLOWLIM_PHN_ACTUAL | If user entered line flow limits are enabled, shows the user entered limit at neutral. Otherwise shows "--". | String |  | Amps | Amps
5162 | DNOM Component | Line | LN | input | LNMODEL | Pointer to the associated line model | String
5163 | DNOM Component | Line | LN | input | LNPLACE | Pointer to the associated line placement | String
5164 | DNOM Component | Line | LN | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
5165 | DNOM Component | Line | LN | output | LOSSKVAR | Total reactive power loss (kVAR). | Float | DPF | kVAR | kVAR
5166 | DNOM Component | Line | LN | output | LOSSKW | Total real power loss (kW). | Float | DPF | kW | kW
5167 | DNOM Component | Line | LN | input | NAME | Object name | String |  |  |  | DNMOBJ
5168 | DNOM Component | Line | LN |  | NETWORKLOOPED | Indicates loop conditions | String
5169 | DNOM Component | Line | LN | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5170 | DNOM Component | Line | LN | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5171 | DNOM Component | Line | LN | input | NODENUM | Node name | String
5172 | DNOM Component | Line | LN | input | NOMID | Nominal(original) line id | String
5173 | DNOM Component | Line | LN | input | NOMNAME | Nominal(original) line id | String
5174 | DNOM Component | Line | LN | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5175 | DNOM Component | Line | LN | input | NUMCIRC | Number of cables in the duct bank (for ampacity deration calculation in LM). | Integer
5176 | DNOM Component | Line | LN |  | NUMFLFAM | Number of fault location analog measurements | String
5177 | DNOM Component | Line | LN | input | OFFNOMINALSS | Flag indicating the switchable section is no longer in its nominal topology | Boolean
5178 | DNOM Component | Line | LN |  | PARALLELLOOPED | Indicates parallell conditions | String
5179 | DNOM Component | Line | LN | output | PERCENTLOADA | Phase A percent loading. | Float | DPF | percent | percent
5180 | DNOM Component | Line | LN | output | PERCENTLOADB | Phase B percent loading. | Float | DPF | percent | percent
5181 | DNOM Component | Line | LN | output | PERCENTLOADC | Phase C percent loading. | Float | DPF | percent | percent
5182 | DNOM Component | Line | LN | output | PFCOMPTIME | Latest power flow solution time. | String | DPF | #N/A | #N/A
5183 | DNOM Component | Line | LN | input | PRMFRATE | Permanent failure rate (failures/length-year). | Float
5184 | DNOM Component | Line | LN | input | REPAIRTM | Sustained outage mean time to repair (in hours). | Float
5185 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP1A | Level 1 phase A Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5186 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP1B | Level 1 phase B Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5187 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP1C | Level 1 phase C Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5188 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP2A | Level 2 phase A Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5189 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP2B | Level 2 phase B Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5190 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP2C | Level 2 phase C Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5191 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP3A | Level 3 phase A Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5192 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP3B | Level 3 phase B Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5193 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP3C | Level 3 phase C Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5194 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP4A | Level 4 phase A Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5195 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP4B | Level 4 phase B Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5196 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP4C | Level 4 phase C Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5197 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP5A | Level 5 phase A Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5198 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP5B | Level 5 phase B Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5199 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJAVAILCAPAMP5C | Level 5 phase C Amp limit minus maximum calcualted phase amps adjusted for reserved capacity. | String |  | Amps | Amps
5200 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJFLOWA | Phase A calculated Amps plus reserved capacity on phase A. | String |  | Amps | Amps
5201 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJFLOWB | Phase B calculated Amps plus reserved capacity on phase B. | String |  | Amps | Amps
5202 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJFLOWC | Phase C calculated Amps plus reserved capacity on phase C. | String |  | Amps | Amps
5203 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING1A | Percentage loading using level 1 phase A Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5204 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING1B | Percentage loading using level 1 phase B Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5205 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING1C | Percentage loading using level 1 phase C Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5206 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING2A | Percentage loading using level 2 phase A Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5207 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING2B | Percentage loading using level 2 phase B Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5208 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING2C | Percentage loading using level 2 phase C Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5209 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING3A | Percentage loading using level 3 phase A Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5210 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING3B | Percentage loading using level 3 phase B Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5211 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING3C | Percentage loading using level 3 phase C Amp limit and maximum calculated phase amps adjusted for reserved capacity | String |  | % | %
5212 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING4A | Percentage loading using level 4 phase A Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5213 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING4B | Percentage loading using level 4 phase B Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5214 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING4C | Percentage loading using level 4 phase C Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5215 | DNOM Component | Line | LN | input | SERVCNTR.NAME | Service center. | String
5216 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING5A | Percentage loading using level 5 phase A Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5217 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING5B | Percentage loading using level 5 phase B Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5218 | DNOM Component | Line | LN |  | RESERVEDCAPACITYADJLOADING5C | Percentage loading using level 5 phase C Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
5219 | DNOM Component | Line | LN |  | RESERVEDCAPACITYAMPA | Reserved capacity on phase A due to reserved capacity objects. | String |  | Amps | Amps
5220 | DNOM Component | Line | LN |  | RESERVEDCAPACITYAMPB | Reserved capacity on phase B due to reserved capacity objects. | String |  | Amps | Amps
5221 | DNOM Component | Line | LN |  | RESERVEDCAPACITYAMPC | Reserved capacity on phase C due to reserved capacity objects. | String |  | Amps | Amps
5222 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING1A | Percentage loading using de-rated level 1 phase A Amp limit and maximum calculated phase amps. | String |  | % | %
5223 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING1B | Percentage loading using de-rated level 1 phase B Amp limit and maximum calculated phase amps. | String |  | % | %
5224 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING1C | Percentage loading using de-rated level 1 phase C Amp limit and maximum calculated phase amps. | String |  | % | %
5225 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING2A | Percentage loading using de-rated level 2 phase A Amp limit and maximum calculated phase amps. | String |  | % | %
5226 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING2B | Percentage loading using de-rated level 2 phase B Amp limit and maximum calculated phase amps. | String |  | % | %
5227 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING2C | Percentage loading using de-rated level 2 phase C Amp limit and maximum calculated phase amps. | String |  | % | %
5228 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING3A | Percentage loading using de-rated level 3 phase A Amp limit and maximum calculated phase amps. | String |  | % | %
5229 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING3B | Percentage loading using de-rated level 3 phase B Amp limit and maximum calculated phase amps. | String |  | % | %
5230 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING3C | Percentage loading using de-rated level 3 phase C Amp limit and maximum calculated phase amps. | String |  | % | %
5231 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING4A | Percentage loading using de-rated level 4 phase A Amp limit and maximum calculated phase amps. | String |  | % | %
5232 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING4B | Percentage loading using de-rated level 4 phase B Amp limit and maximum calculated phase amps. | String |  | % | %
5233 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING4C | Percentage loading using de-rated level 4 phase C Amp limit and maximum calculated phase amps. | String |  | % | %
5234 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING5A | Percentage loading using de-rated level 5 phase A Amp limit and maximum calculated phase amps. | String |  | % | %
5235 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING5B | Percentage loading using de-rated level 5 phase B Amp limit and maximum calculated phase amps. | String |  | % | %
5236 | DNOM Component | Line | LN |  | RESERVEDCAPACITYDERATEDLIMITLOADING5C | Percentage loading using de-rated level 5 phase C Amp limit and maximum calculated phase amps. | String |  | % | %
5237 | DNOM Component | Line | LN | output | SSIAPERCNT | Percent current loading by phase A. The field pertains to a switchable section. | Float | DPF | percent | percent
5238 | DNOM Component | Line | LN | output | SSIAPKPERC | Percent current loading at peak by phase A. The field pertains to a switchable section. | Float | DPF | percent | percent
5239 | DNOM Component | Line | LN | output | SSIBPERCNT | Percent current loading by phase B. The field pertains to a switchable section. | Float | DPF | percent | percent
5240 | DNOM Component | Line | LN | output | SSIBPKPERC | Percent current loading at peak by phase B. The field pertains to a switchable section. | Float | DPF | percent | percent
5241 | DNOM Component | Line | LN | output | SSICPERCNT | Percent current loading by phase C. The field pertains to a switchable section. | Float | DPF | percent | percent
5242 | DNOM Component | Line | LN | output | SSICPKPERC | Percent current loading at peak by phase C. The field pertains to a switchable section. | Float | DPF | percent | percent
5243 | DNOM Component | Line | LN | output | SSINETA | Net phase A current flow. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5244 | DNOM Component | Line | LN | output | SSINETAPK | Peak net injection (Amps) for the section- PhaseA. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5245 | DNOM Component | Line | LN | output | SSINETB | Net phase B current flow. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5246 | DNOM Component | Line | LN | output | SSINETBPK | Peak net injection (Amps) for the section- PhaseB. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5247 | DNOM Component | Line | LN | output | SSINETC | Net phase C current flow. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5248 | DNOM Component | Line | LN | output | SSINETCPK | Peak net injection (Amps) for the section- PhaseC. The field pertains to a switchable section. | Float | DPF | Amps | Amps
5249 | DNOM Component | Line | LN | input | SSISOLSW | Name of isolation (boundary) switches of line associated switchable section. The field pertains to a switchable section. | String |  | #N/A | #N/A
5250 | DNOM Component | Line | LN | input | SSNUMCRTCUST | The total number of critical customers. The field pertains to a switchable section. | Integer
5251 | DNOM Component | Line | LN | input | SSNUMCUST3 | Number of customers with two or three-phase loads. The field pertains to a switchable section. | Integer
5252 | DNOM Component | Line | LN | input | SSNUMCUSTA | Number of customers on Phase A. The field pertains to a switchable section. | Integer
5253 | DNOM Component | Line | LN | input | SSNUMCUSTB | Number of customers on Phase B. The field pertains to a switchable section. | Integer
5254 | DNOM Component | Line | LN | input | SSNUMCUSTC | Number of customers on Phase C. The field pertains to a switchable section. | Integer
5255 | DNOM Component | Line | LN | input | SSNUMTF3 | The total number of three phase transformers. The field pertains to a switchable section. | Integer
5256 | DNOM Component | Line | LN | input | SSNUMTFA | The total number of transformers on phase A. The field pertains to a switchable section. | Integer
5257 | DNOM Component | Line | LN | input | SSNUMTFB | The total number of transformers on phase B. The field pertains to a switchable section. | Integer
5258 | DNOM Component | Line | LN | input | SSNUMTFC | The total number of transformers on phase C. The field pertains to a switchable section. | Integer
5259 | DNOM Component | Line | LN | output | SSPNETA | Net phase A real power flow. The field pertains to a switchable section. | Float | DPF | kW | kW
5260 | DNOM Component | Line | LN | output | SSPNETB | Net phase B real power flow. The field pertains to a switchable section. | Float | DPF | kW | kW
5261 | DNOM Component | Line | LN | output | SSPNETC | Net phase C real power flow. The field pertains to a switchable section. | Float | DPF | kW | kW
5262 | DNOM Component | Line | LN | output | SSQNETA | Net phase A reactive power flow. The field pertains to a switchable section. | Float | DPF | kVAR | kVAR
5263 | DNOM Component | Line | LN | output | SSQNETB | Net phase B reactive power flow. The field pertains to a switchable section. | Float | DPF | kVAR | kVAR
5264 | DNOM Component | Line | LN | output | SSQNETC | Net phase C reactive power flow. The field pertains to a switchable section. | Float | DPF | kVAR | kVAR
5265 | DNOM Component | Line | LN | output | SSSNETA | Net phase A apparent power flow. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5266 | DNOM Component | Line | LN | output | SSSNETAPK | Peak net load (kVA) for the section-PhaseA. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5267 | DNOM Component | Line | LN | output | SSSNETB | Net phase B apparent power flow. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5268 | DNOM Component | Line | LN | output | SSSNETBPK | Peak net load (kVA) for the section-PhaseB. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5269 | DNOM Component | Line | LN | output | SSSNETC | Net phase C apparent power flow. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5270 | DNOM Component | Line | LN | output | SSSNETCPK | Peak net load (kVA) for the section-PhaseC. The field pertains to a switchable section. | Float | DPF | kVA | kVA
5271 | DNOM Component | Line | LN |  | STATIONOFFEEDERBREAKER | Name of the energizing substation. Used for the Locate Dynamic Feeder Breaker on SCADA Oneline toolbar option. | String
5272 | DNOM Component | Line | LN | input | TMPFRATE | Temporary failure rate (failures/length-year). | Float
5273 | DNOM Component | Line | LN | output | TOLNCURRENTVECTORSUM | To end current flow vector sum (phases A, B, and C). | Complex | DPF | Amps | Amps
5274 | DNOM Component | Line | LN | input | TONODE | Line to-node name | String
5275 | DNOM Component | Line | LN | output | TONODEAMPA | To end phase A amp flow (magnitude and angle). | Float | DPF | Amps | Amps
5276 | DNOM Component | Line | LN | output | TONODEAMPB | To end phase B amp flow (magnitude and angle). | Float | DPF | Amps | Amps
5277 | DNOM Component | Line | LN | output | TONODEAMPC | To end phase C amp flow (magnitude and angle). | Float | DPF | Amps | Amps
5278 | DNOM Component | Line | LN | output | TONODEAMPN | To end phase N amp flow (magnitude and angle). | Float | DPF | Amps | Amps
5279 | DNOM Component | Line | LN | output | TONODEAMPNEUT | Vector Summation of the To end phase A,B,C current flows (magnitude and angle) | Float | DPF
5280 | DNOM Component | Line | LN | output | TONODEKVAR3PH | To end total reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5281 | DNOM Component | Line | LN | output | TONODEKVARA | To end phase A reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5282 | DNOM Component | Line | LN | output | TONODEKVARB | To end phase B reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5283 | DNOM Component | Line | LN | output | TONODEKVARC | To end phase C reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5284 | DNOM Component | Line | LN | output | TONODEKW3PH | To end total real power flow (kW). | Float | DPF | kW | kW
5285 | DNOM Component | Line | LN | output | TONODEKWA | From end phase A reactive power flow (kVAR). | Float | DPF | kW | kW
5286 | DNOM Component | Line | LN | output | TONODEKWB | From end phase B reactive power flow (kVAR). | Float | DPF | kW | kW
5287 | DNOM Component | Line | LN | output | TONODEKWC | From end phase C reactive power flow (kVAR). | Float | DPF | kW | kW
5288 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5289 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
5290 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
5291 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
5292 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
5293 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
5294 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.LENGTH | Line length | Float |  | Meters | Feet | LN
5295 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.NAME | Name of the object | String |  |  |  | DNMOBJ
5296 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5297 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5298 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5299 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.NUMFLFAM | Number of fault location analog measurements | String |  |  |  | LN
5300 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.PRMFRATE | Permanent failure rate (failures/length-year) | Float |  |  |  | LN
5301 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.REPAIRTM | Sustained outage mean time to repair | Float |  | Hours | Hours | LN
5302 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.TMPFRATE | Temporary failure rate (failures/length-year) | Float |  |  |  | LN
5303 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE.ZLENGTH | Impedance for PRV function (in pu) | Float |  |  |  | LN
5304 | DNOM Component | Line | LN | output | TONODEVOLTANAPG | To end phase A voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5305 | DNOM Component | Line | LN | output | TONODEVOLTANBPG | To end phase B voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5306 | Global Object | Line Model | LNMOD | input | CONDMODA.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5307 | Global Object | Line Model | LNMOD | input | CONDMODA.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5308 | Global Object | Line Model | LNMOD | input | CONDMODA.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5309 | Global Object | Line Model | LNMOD | input | CONDMODA.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5310 | Global Object | Line Model | LNMOD | input | CONDMODA.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5311 | Global Object | Line Model | LNMOD | input | CONDMODA.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5312 | Global Object | Line Model | LNMOD | input | CONDMODA.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5313 | Global Object | Line Model | LNMOD | input | CONDMODA.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5314 | Global Object | Line Model | LNMOD | input | CONDMODA.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5315 | Global Object | Line Model | LNMOD | input | CONDMODA.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5316 | Global Object | Line Model | LNMOD | input | CONDMODA.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5317 | Global Object | Line Model | LNMOD | input | CONDMODA.ID | Object unique ID | String |  |  |  | DNMOBJ
5318 | Global Object | Line Model | LNMOD | input | CONDMODA.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5319 | Global Object | Line Model | LNMOD | input | CONDMODA.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5320 | Global Object | Line Model | LNMOD | input | CONDMODA.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5321 | Global Object | Line Model | LNMOD | input | CONDMODA.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5322 | Global Object | Line Model | LNMOD | input | CONDMODA.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5323 | Global Object | Line Model | LNMOD | input | CONDMODA.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5324 | Global Object | Line Model | LNMOD | input | CONDMODA.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5325 | Global Object | Line Model | LNMOD | input | CONDMODA.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5326 | Global Object | Line Model | LNMOD | input | CONDMODA.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5327 | Global Object | Line Model | LNMOD | input | CONDMODA.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5328 | Global Object | Line Model | LNMOD | input | CONDMODA.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5329 | Global Object | Line Model | LNMOD | input | CONDMODA.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5330 | Global Object | Line Model | LNMOD | input | CONDMODA.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5331 | Global Object | Line Model | LNMOD | input | CONDMODA.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5332 | Global Object | Line Model | LNMOD | input | CONDMODA.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5333 | Global Object | Line Model | LNMOD | input | CONDMODA.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5334 | Global Object | Line Model | LNMOD | input | CONDMODA.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5335 | Global Object | Line Model | LNMOD | input | CONDMODA.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5336 | Global Object | Line Model | LNMOD | input | CONDMODA.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5337 | Global Object | Line Model | LNMOD | input | CONDMODA.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5338 | Global Object | Line Model | LNMOD | input | CONDMODA.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5339 | Global Object | Line Model | LNMOD | input | CONDMODA.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5340 | DNOM Component | Line | LN | output | TONODEVOLTANCPG | To end phase C voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5341 | Global Object | Line Model | LNMOD | input | CONDMODB.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5342 | Global Object | Line Model | LNMOD | input | CONDMODB.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5343 | Global Object | Line Model | LNMOD | input | CONDMODB.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5344 | Global Object | Line Model | LNMOD | input | CONDMODB.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5345 | Global Object | Line Model | LNMOD | input | CONDMODB.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5346 | Global Object | Line Model | LNMOD | input | CONDMODB.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5347 | Global Object | Line Model | LNMOD | input | CONDMODB.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5348 | Global Object | Line Model | LNMOD | input | CONDMODB.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5349 | Global Object | Line Model | LNMOD | input | CONDMODB.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5350 | Global Object | Line Model | LNMOD | input | CONDMODB.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5351 | Global Object | Line Model | LNMOD | input | CONDMODB.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5352 | Global Object | Line Model | LNMOD | input | CONDMODB.ID | Object unique ID | String |  |  |  | DNMOBJ
5353 | Global Object | Line Model | LNMOD | input | CONDMODB.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5354 | Global Object | Line Model | LNMOD | input | CONDMODB.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5355 | Global Object | Line Model | LNMOD | input | CONDMODB.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5356 | Global Object | Line Model | LNMOD | input | CONDMODB.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5357 | Global Object | Line Model | LNMOD | input | CONDMODB.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5358 | Global Object | Line Model | LNMOD | input | CONDMODB.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5359 | Global Object | Line Model | LNMOD | input | CONDMODB.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5360 | Global Object | Line Model | LNMOD | input | CONDMODB.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5361 | Global Object | Line Model | LNMOD | input | CONDMODB.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5362 | Global Object | Line Model | LNMOD | input | CONDMODB.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5363 | Global Object | Line Model | LNMOD | input | CONDMODB.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5364 | Global Object | Line Model | LNMOD | input | CONDMODB.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5365 | Global Object | Line Model | LNMOD | input | CONDMODB.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5366 | Global Object | Line Model | LNMOD | input | CONDMODB.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5367 | Global Object | Line Model | LNMOD | input | CONDMODB.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5368 | Global Object | Line Model | LNMOD | input | CONDMODB.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5369 | Global Object | Line Model | LNMOD | input | CONDMODB.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5370 | Global Object | Line Model | LNMOD | input | CONDMODB.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5371 | Global Object | Line Model | LNMOD | input | CONDMODB.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5372 | Global Object | Line Model | LNMOD | input | CONDMODB.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5373 | Global Object | Line Model | LNMOD | input | CONDMODB.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5374 | Global Object | Line Model | LNMOD | input | CONDMODB.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5375 | DNOM Component | Line | LN | output | TONODEVOLTOPAPG | To end phase A voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5376 | Global Object | Line Model | LNMOD | input | CONDMODC.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5377 | Global Object | Line Model | LNMOD | input | CONDMODC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5378 | Global Object | Line Model | LNMOD | input | CONDMODC.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5379 | Global Object | Line Model | LNMOD | input | CONDMODC.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5380 | Global Object | Line Model | LNMOD | input | CONDMODC.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5381 | Global Object | Line Model | LNMOD | input | CONDMODC.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5382 | Global Object | Line Model | LNMOD | input | CONDMODC.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5383 | Global Object | Line Model | LNMOD | input | CONDMODC.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5384 | Global Object | Line Model | LNMOD | input | CONDMODC.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5385 | Global Object | Line Model | LNMOD | input | CONDMODC.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5386 | Global Object | Line Model | LNMOD | input | CONDMODC.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5387 | Global Object | Line Model | LNMOD | input | CONDMODC.ID | Object unique ID | String |  |  |  | DNMOBJ
5388 | Global Object | Line Model | LNMOD | input | CONDMODC.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5389 | Global Object | Line Model | LNMOD | input | CONDMODC.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5390 | Global Object | Line Model | LNMOD | input | CONDMODC.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5391 | Global Object | Line Model | LNMOD | input | CONDMODC.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5392 | Global Object | Line Model | LNMOD | input | CONDMODC.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5393 | Global Object | Line Model | LNMOD | input | CONDMODC.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5394 | Global Object | Line Model | LNMOD | input | CONDMODC.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5395 | Global Object | Line Model | LNMOD | input | CONDMODC.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5396 | Global Object | Line Model | LNMOD | input | CONDMODC.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5397 | Global Object | Line Model | LNMOD | input | CONDMODC.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5398 | Global Object | Line Model | LNMOD | input | CONDMODC.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5399 | Global Object | Line Model | LNMOD | input | CONDMODC.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5400 | Global Object | Line Model | LNMOD | input | CONDMODC.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5401 | Global Object | Line Model | LNMOD | input | CONDMODC.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5402 | Global Object | Line Model | LNMOD | input | CONDMODC.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5403 | Global Object | Line Model | LNMOD | input | CONDMODC.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5404 | Global Object | Line Model | LNMOD | input | CONDMODC.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5405 | Global Object | Line Model | LNMOD | input | CONDMODC.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5406 | Global Object | Line Model | LNMOD | input | CONDMODC.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5407 | Global Object | Line Model | LNMOD | input | CONDMODC.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5408 | Global Object | Line Model | LNMOD | input | CONDMODC.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5409 | Global Object | Line Model | LNMOD | input | CONDMODC.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5410 | DNOM Component | Line | LN | output | TONODEVOLTOPBPG | To end phase B voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5411 | Global Object | Line Model | LNMOD | input | CONDMODN.AMPSCHED | Ampacity derating schedule name for cases when there are multiple cables in a duct bank. This schedule is not required. | String |  |  |  | CNDMOD
5412 | Global Object | Line Model | LNMOD | input | CONDMODN.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5413 | Global Object | Line Model | LNMOD | input | CONDMODN.BSHUNT | Shunt susceptance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5414 | Global Object | Line Model | LNMOD | input | CONDMODN.CONDCNST | Enumeration indicating that underground construction is direct buried (1), in conduit (2), or not applicable (0 – overhead construction) | Integer |  |  |  | CNDMOD
5415 | Global Object | Line Model | LNMOD | input | CONDMODN.CONDSIZE | Conductor size (568, 1.0, or other) | String |  |  |  | CNDMOD
5416 | Global Object | Line Model | LNMOD | input | CONDMODN.CONDTYPE | Enumerated cable type. The following enumeration is used: 0 = Bare wire (includes tree wire), 1 = Single tape shield cable, 2 = One three conductor tape shield cable, 3 = Single concentric neutral cable, 4 = One three conductor concentric neutral cable. | Integer |  |  |  | CNDMOD
5417 | Global Object | Line Model | LNMOD | input | CONDMODN.DIAMETER | Diameter of the conductor if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5418 | Global Object | Line Model | LNMOD | input | CONDMODN.DISTMOD | Flag indicating model represents a distribution conductor (true = distribution, false = transmission) | Boolean |  |  |  | CNDMOD
5419 | Global Object | Line Model | LNMOD | input | CONDMODN.GMRNEUT | Neutral conductor bundle self geometric mean radius for a concentric neutral cable if a distribution model is given (blank for a transmission model). | Float |  | millimeters | feet | CNDMOD
5420 | Global Object | Line Model | LNMOD | input | CONDMODN.GMRPHASE | Phase conductor geometric mean radius if a distribution model is given (blank for a transmission model) | Float |  | millimeters | feet | CNDMOD
5421 | Global Object | Line Model | LNMOD | input | CONDMODN.GSHUNT | Shunt conductance if a transmission model is given (blank for a distribution model) | Float |  | Siemens x 10-06/km | Siemens x 10-06/kft | CNDMOD
5422 | Global Object | Line Model | LNMOD | input | CONDMODN.ID | Object unique ID | String |  |  |  | DNMOBJ
5423 | Global Object | Line Model | LNMOD | input | CONDMODN.INSULTYP | Type of cable insulation. The enumeration is as follows: 1 = Cross-Linked Polyethylene (XLPE), 2 = Polyethylene (PE), 3 = Polyvinyl Chloride (PVC), 4 = Ethylene-Propylene Rubber (EPR), 5 = steel in paper, 6 = High Molecular Weight Polyethylene (HMWPE), 7 = Three-retardant cross-linked polyethylene (TR_XLPE), and 8 = Paper Insulated Lead Covered (PILC). | Integer |  |  |  | CNDMOD
5424 | Global Object | Line Model | LNMOD | input | CONDMODN.LIMITEVENT | A flag indicating a limit event | Boolean |  |  |  | CNDMOD
5425 | Global Object | Line Model | LNMOD | input | CONDMODN.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | CNDMOD
5426 | Global Object | Line Model | LNMOD | input | CONDMODN.LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String |  |  |  | CNDMOD
5427 | Global Object | Line Model | LNMOD | input | CONDMODN.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | CNDMOD
5428 | Global Object | Line Model | LNMOD | input | CONDMODN.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | CNDMOD
5429 | Global Object | Line Model | LNMOD | input | CONDMODN.NEUTDIST | Center to neutral conductor spacing for a concentric neutral cable (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5430 | Global Object | Line Model | LNMOD | input | CONDMODN.NUMLIMIT | The number of operational limits | Integer |  |  |  | CNDMOD
5431 | Global Object | Line Model | LNMOD | input | CONDMODN.OUTDIAM | Outside diameter over the shield for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5432 | Global Object | Line Model | LNMOD | input | CONDMODN.PHDIST | Phase conductor spacing for a three conductor cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5433 | Global Object | Line Model | LNMOD | input | CONDMODN.PRMFRATE | Default sustained failure rate (permanent failures/kft-year) or (permanent failures/km-year) | Float |  |  |  | CNDMOD
5434 | Global Object | Line Model | LNMOD | input | CONDMODN.REPTIME | Default mean time to repair | Float |  | Hours | Hours | CNDMOD
5435 | Global Object | Line Model | LNMOD | input | CONDMODN.RNEUTRAL | Neutral conductor resistance at 60 Hz for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | ohms/km | ohms/kft | CNDMOD
5436 | Global Object | Line Model | LNMOD | input | CONDMODN.RPHASE | Phase conductor resistance at 60 Hz for a transmission or distribution model | Float |  | ohms/km | ohms/kft | CNDMOD
5437 | Global Object | Line Model | LNMOD | input | CONDMODN.SHDTHICK | Shield thickness for a non-concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5438 | Global Object | Line Model | LNMOD | input | CONDMODN.SMALDISP | Flag indicating that a small conductor type has been found – used for displaying lines (True = small conductor) | Boolean |  |  |  | CNDMOD
5439 | Global Object | Line Model | LNMOD | input | CONDMODN.STRCTYPE | Conductor type (copper, other) | String |  |  |  | CNDMOD
5440 | Global Object | Line Model | LNMOD | input | CONDMODN.STRNDCNT | The number of concentric neutral strands for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Integer |  |  |  | CNDMOD
5441 | Global Object | Line Model | LNMOD | input | CONDMODN.STRNDIAM | Diameter (inches/millimeters) of a concentric neutral strand for a concentric neutral cable if a distribution model is given (blank for a transmission model) | Float |  | millimeters | inches | CNDMOD
5442 | Global Object | Line Model | LNMOD | input | CONDMODN.TEMPSCHED | The name of an associated temperature based ampacity schedule | String |  |  |  | CNDMOD
5443 | Global Object | Line Model | LNMOD | input | CONDMODN.TMPFRATE | Default momentary failure rate (temporary failures/kft-year) or (temporary failures/km-year) | Float |  |  |  | CNDMOD
5444 | Global Object | Line Model | LNMOD | input | CONDMODN.XPHASE | Phase conductor reactance or if a transmission model is given (blank for a distribution model) | Float |  | ohms/km | ohms/kft | CNDMOD
5445 | DNOM Component | Line | LN | output | TONODEVOLTOPCPG | To end phase C voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5446 | Global Object | Line Model | LNMOD | input | FRMODEL.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5447 | Global Object | Line Model | LNMOD | input | FRMODEL.bOverhead | Flag indicating overhead vs underground construction (true - overhead) | Boolean |  |  |  | CSTMOD
5448 | Global Object | Line Model | LNMOD | input | FRMODEL.ID | Object unique ID | String |  |  |  | DNMOBJ
5449 | Global Object | Line Model | LNMOD | input | FRMODEL.rXPhaseA | X coordinate for conductor on position 1. The X coordinates are referenced to the pole (left/right). Usually, position 1 is the leftmost position, which means its X coordinate is smallest among all positions. | Float |  | meters | feet | CSTMOD
5450 | Global Object | Line Model | LNMOD | input | FRMODEL.rXPhaseB | X coordinate for conductor on position 2 | Float |  | meters | feet | CSTMOD
5451 | Global Object | Line Model | LNMOD | input | FRMODEL.rXPhaseC | X coordinate for conductor on position 3. Usually, position3 is the rightmost position, which means its X coordinate is the biggest among all positions. | Float |  | meters | feet | CSTMOD
5452 | Global Object | Line Model | LNMOD | input | FRMODEL.rXPhaseN | X coordinate for conductor on position N. Usually, this position N is for neutral conductor. | Float |  | meters | feet | CSTMOD
5453 | Global Object | Line Model | LNMOD | input | FRMODEL.rYPhaseA | Y coordinate for conductor on position 1. The Y coordinates are referenced to height above ground. | Float |  | meters | feet | CSTMOD
5454 | Global Object | Line Model | LNMOD | input | FRMODEL.rYPhaseB | Y coordinate for conductor on position 2. Usually, position2 is the highest position, which means its Y coordinate is biggest among all positions. | Float |  | meters | feet | CSTMOD
5455 | Global Object | Line Model | LNMOD | input | FRMODEL.rYPhaseC | Y coordinate for conductor on position 3 | Float |  | meters | feet | CSTMOD
5456 | Global Object | Line Model | LNMOD | input | FRMODEL.rYPhaseN | Y coordinate for conductor on position N | Float |  | meters | feet | CSTMOD
5457 | DNOM Component | Line | LN | input | VALIDDYNSTATIONNAME | Dynamic (currently energizing) station name. | String
5458 | DNOM Component | Line | LN | output | VOLTANDANGLEANA | From end phase A voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5459 | DNOM Component | Line | LN | output | VOLTANDANGLEANB | From end phase B voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5460 | DNOM Component | Line | LN | output | VOLTANDANGLEANC | From end phase C voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
5461 | DNOM Component | Line | LN | output | VOLTANDANGLEOPA | From end phase A voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5462 | DNOM Component | Line | LN | output | VOLTANDANGLEOPB | From end phase B voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5463 | DNOM Component | Line | LN | output | VOLTANDANGLEOPC | From end phase C voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5464 | DNOM Component | Line | LN | output | VOLTDROPDIFFA | Line phaseA voltage drop (%) between From node and To node | Float
5465 | DNOM Component | Line | LN | output | VOLTDROPDIFFB | Line phaseB voltage drop (%) between From node and To node | Float
5466 | DNOM Component | Line | LN | output | VOLTDROPDIFFC | Line phaseC voltage drop (%) between From node and To node | Float
5467 | DNOM Component | Line | LN | input | VOLTNOMPG | the actual voltage base line-to-ground | Float
5468 | DNOM Component | Line | LN | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
5469 | DNOM Component | Line | LN | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
5470 | DNOM Component | Line | LN | input | ZLENGTH | Impedance for PRV function (in pu) | Float
5471 | DNOM Component Placement | Line Label Placement | LNLBPL | input | LINE | Pointer to the associated line | String
5472 | Global Object | Line Model | LNMOD |  | ARTFNEU | A flag indicating that artificial neutral is added | Boolean
5473 | Global Object | Line Model | LNMOD | input | CONDMODA | Pointer to phase A conductor model | String
5474 | Global Object | Line Model | LNMOD | input | CONDMODB | Pointer to phase B conductor model | String
5475 | Global Object | Line Model | LNMOD | input | CONDMODC | Pointer to phase C conductor model | String
5476 | Global Object | Line Model | LNMOD | input | CONDMODN | Pointer to phase N conductor model | String
5477 | Global Object | Line Model | LNMOD | input | FRMODEL | Pointer to associated construction model | String
5478 | Global Object | Line Model | LNMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
5479 | Global Object | Line Model | LNMOD |  | LinePhasing | Line phasing of the model | String
5480 | Global Object | Line Model | LNMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
5481 | DNOM Component | Line Output | LNOUT |  | IFROMA | Phase A current injected at from end of line into the line | Float |  | Amps | Amps
5482 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5483 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
5484 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
5485 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
5486 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
5487 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
5488 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.LENGTH | Line length | Float |  | Meters | Feet | LN
5489 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.NAME | Name of the object | String |  |  |  | DNMOBJ
5490 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5491 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5492 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5493 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.NUMFLFAM | Number of fault location analog measurements | String |  |  |  | LN
5494 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.PRMFRATE | Permanent failure rate (failures/length-year) | Float |  |  |  | LN
5495 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.REPAIRTM | Sustained outage mean time to repair | Float |  | Hours | Hours | LN
5496 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.TMPFRATE | Temporary failure rate (failures/length-year) | Float |  |  |  | LN
5497 | DNOM Component Placement | Line Placement | LNPLE | input | LINE.ZLENGTH | Impedance for PRV function (in pu) | Float |  |  |  | LN
5498 | DNOM Component | Line Output | LNOUT |  | IFROMB | Phase B current injected at from end of line into the line | Float |  | Amps | Amps
5499 | DNOM Component | Line Output | LNOUT |  | IFROMC | Phase C current injected at from end of line into the line | Float |  | Amps | Amps
5500 | DNOM Component | Line Output | LNOUT |  | IFROMN | Phase N current injected at from end of line into the line | Float |  | Amps | Amps
5501 | DNOM Component | Line Output | LNOUT |  | ITOA | Phase A current injected at from to of line into the line | Float |  | Amps | Amps
5502 | DNOM Component | Line Output | LNOUT |  | ITOB | Phase B current injected at from to of line into the line | Float |  | Amps | Amps
5503 | DNOM Component | Line Output | LNOUT |  | ITOC | Phase C current injected at from to of line into the line | Float |  | Amps | Amps
5504 | DNOM Component | Line Output | LNOUT |  | ITON | Phase N current injected at from to of line into the line | Float |  | Amps | Amps
5505 | DNOM Component | Line Output | LNOUT |  | LIMFLAGS | Limit violation flags | Integer
5506 | DNOM Component | Line Output | LNOUT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
5507 | DNOM Component | Line Output | LNOUT |  | LOSS | Total line loss (kVA) | Float |  | kVA | kVA
5508 | DNOM Component | Line Output | LNOUT |  | PQFROMA | Phase A power injected at from end of line into the line | Float |  | kVA | kVA
5509 | DNOM Component | Line Output | LNOUT |  | PQFROMB | Phase B power injected at from end of line into the line | Float |  | kVA | kVA
5510 | DNOM Component | Line Output | LNOUT |  | PQFROMC | Phase C power injected at from end of line into the line | Float |  | kVA | kVA
5511 | DNOM Component | Line Output | LNOUT |  | PQFROMN | Phase N power injected at from end of line into the line | Float |  | kVA | kVA
5512 | DNOM Component | Line Output | LNOUT |  | PQTOA | Phase A power injected at from to of line into the line | Float |  | kVA | kVA
5513 | DNOM Component | Line Output | LNOUT |  | PQTOB | Phase B power injected at from to of line into the line | Float |  | kVA | kVA
5514 | DNOM Component | Line Output | LNOUT |  | PQTOC | Phase C power injected at from to of line into the line | Float |  | kVA | kVA
5515 | DNOM Component | Line Output | LNOUT |  | PQTON | Phase N power injected at from to of line into the line | Float |  | kVA | kVA
5516 | DNOM Component | Line Output | LNOUT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
5517 | DNOM Component | Line Output | LNOUT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
5518 | DNOM Component Placement | Line Placement | LNPLE | input | LINE | Pointer to the associated line | String
5519 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVAA | From end phase A apparent power flow (kVA) | Float |  | kVA | kVA
5520 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVAB | From end phase B apparent power flow (kVA) | Float |  | kVA | kVA
5521 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVAC | From end phase C apparent power flow (kVA) | Float |  | kVA | kVA
5522 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVARA | Side 2 phase A real power flow (kW). | Float
5523 | DNOM Component | Load | LOAD | input | ADDRESS.NOAPPSTR | Load address. | String
5524 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVARB | Side 2 phase B real power flow (kW). | Float
5525 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKVARC | Side 2 phase C real power flow (kW). | Float
5526 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKWA | Side 1 phase A real power flow (kW). | Float
5527 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKWB | Side 1 phase B real power flow (kW). | Float
5528 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEKWC | Side 1 phase C real power flow (kW). | Float
5529 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEPFA | From node phase A power factor | Float
5530 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEPFB | From node phase B power factor | Float
5531 | Virtual Object | Line and Series | LNSERIES | output | FROMNODEPFC | From node phase C power factor | Float
5532 | Virtual Object | Line and Series | LNSERIES | input | KVLLNOM | Operating voltage (in kV, line to line voltage for three phase and line to ground to single phase) | Float
5533 | Virtual Object | Line and Series | LNSERIES |  | TONODEKVAA | To end phase A apparent power flow (kVA) | Float |  | kVA | kVA
5534 | Virtual Object | Line and Series | LNSERIES |  | TONODEKVAB | To end phase B apparent power flow (kVA) | Float |  | kVA | kVA
5535 | Virtual Object | Line and Series | LNSERIES |  | TONODEKVAC | To end phase C apparent power flow (kVA) | Float |  | kVA | kVA
5536 | Virtual Object | Line and Series | LNSERIES | output | ToNODEKVARA | Side 2 phase A reactive power flow (kVAR). | Float
5537 | Virtual Object | Line and Series | LNSERIES | output | ToNODEKVARB | Side 2 phase B reactive power flow (kVAR). | Float
5538 | Virtual Object | Line and Series | LNSERIES | output | ToNODEKVARC | Side 2 phase C reactive power flow (kVAR). | Float
5539 | Virtual Object | Line and Series | LNSERIES | output | TONODEKWA | Side 1 phase A reactive power flow (kVAR). | Float
5540 | Virtual Object | Line and Series | LNSERIES | output | TONODEKWB | Side 1 phase B reactive power flow (kVAR). | Float
5541 | Virtual Object | Line and Series | LNSERIES | output | TONODEKWC | Side 1 phase C reactive power flow (kVAR). | Float
5542 | Virtual Object | Line and Series | LNSERIES | output | TONODEPFA | To node phase A power factor | Float
5543 | Virtual Object | Line and Series | LNSERIES | output | TONODEPFB | To node phase B power factor | Float
5544 | Virtual Object | Line and Series | LNSERIES | output | TONODEPFC | To node phase C power factor | Float
5545 | DNOM Component | Load | LOAD | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
5546 | DNOM Component | Load | LOAD | output | AMPANDANGLEA | Phase A current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
5547 | DNOM Component | Load | LOAD | output | AMPANDANGLEB | Phase B current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
5548 | DNOM Component | Load | LOAD | output | AMPANDANGLEC | Phase current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
5549 | DNOM Component | Load | LOAD | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5550 | DNOM Component | Load | LOAD |  | BLAFLAGS | BLA flags | Integer
5551 | DNOM Component | Load | LOAD | output | COLDLOADMULT | Load cold start multiplier. | Float | DPF | #N/A | #N/A
5552 | DNOM Component | Load | LOAD | output | COLDLOADMULTA | Load cold start multiplier phase A. | Float | DPF | #N/A | #N/A
5553 | DNOM Component | Load | LOAD | output | COLDLOADMULTB | Load cold start multiplier phase B. | Float | DPF | #N/A | #N/A
5554 | DNOM Component | Load | LOAD | output | COLDLOADMULTC | Load cold start multiplier phase C. | Float | DPF | #N/A | #N/A
5555 | DNOM Component | Load | LOAD | input | CONSTRUCTPHASES | Constructed Phases | String
5556 | DNOM Component | Load | LOAD |  | CRITICALCUSTNUM | Number of critical customers | Integer
5557 | DNOM Component | Load | LOAD | input | CUSTOMERCOUNT | Customer count. | Integer
5558 | DNOM Component | Load | LOAD |  | CUSTOMERDRRATIO | Ration of customers with DER | String
5559 | DNOM Component | Load | LOAD |  | CUSTOMERGENRATING | Customer generation rating | String
5560 | DNOM Component | Load | LOAD |  | CUSTOMERGENTYPE | Customer generation type | String
5561 | DNOM Component | Load | LOAD |  | CUSTOMERLOADTYPE | Customer load type | String
5562 | DNOM Component | Load | LOAD | input | DISTTFTABNAME | The DNOM table name of the distribution transformer of the load. | String
5563 | DNOM Component | Load | LOAD | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
5564 | DNOM Component | Load | LOAD | input | DNOMTABNAME | The DNOM table name of the load. | String
5565 | DNOM Component | Load | LOAD | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
5566 | DNOM Component | Load | LOAD | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
5567 | DNOM Component | Load | LOAD |  | DRRATIO | Demand response component of the load (in percent) | Integer
5568 | DNOM Component | Load | LOAD | input | DYNFEEDERNAME | Dynamic (currently energizing) feeder name. | String
5569 | DNOM Component | Load | LOAD | input | DYNSTATIONNAME | Dynamic (currently energizing) station name. | String
5570 | DNOM Component | Load | LOAD | input | FEEDERNAME | Nominal feeder name. | String
5571 | DNOM Component | Load | LOAD | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
5572 | DNOM Component | Load | LOAD |  | GENRATING | Nameplate kVA rating of the generation component of the load | Integer |  | kVA | kVA
5573 | DNOM Component | Load | LOAD |  | GENTYPE | User defined enumeration type for generation component | Integer
5574 | DNOM Component | Load | LOAD | input | GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
5575 | DNOM Component | Load | LOAD | input | HASMANUALENTRY | If one or some fields of load has(have) value override. | Boolean
5576 | DNOM Component | Load | LOAD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
5577 | DNOM Component | Load | LOAD |  | IFLOWA | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
5578 | DNOM Component | Load | LOAD | output | LDCAT.LDCATSCHEDSECVOLTNAME | Associated secondary voltage drop schedule name | String
5579 | DNOM Component | Load | LOAD |  | IFLOWB | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
5580 | DNOM Component | Load | LOAD |  | IFLOWC | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
5581 | DNOM Component | Load | LOAD | input | ISDYNFEEDERLOOPED | Flag indicating if Dynamic Feeder is Looped | Boolean
5582 | DNOM Component | Load | LOAD | output | KVAR3PH | Total reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5583 | DNOM Component | Load | LOAD |  | KVAR3PHDER | Associated DER apparent power phase ABC | String
5584 | DNOM Component | Load | LOAD | input | LOADCAT.ACCURACY | Load data accuracy (percent – used in determining the allocated loads) | Float |  |  |  | LOADCAT
5585 | DNOM Component | Load | LOAD | input | LOADCAT.BILLSCH | Associated billing schedule | String |  |  |  | LOADCAT
5586 | DNOM Component | Load | LOAD | input | LOADCAT.ECOSTINT | Value of uninterrupted service | Float |  | $/kW | $/kW | LOADCAT
5587 | DNOM Component | Load | LOAD | input | LOADCAT.ENDTM | Subinterval end times | Float |  | Hours | Hours | LOADCAT
5588 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALA | A flag indicating the manual load to voltage coefficient A | Boolean |  |  |  | LOADCAT
5589 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALB | A flag indicating the manual load to voltage coefficient C | Boolean |  |  |  | LOADCAT
5590 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALC | A flag indicating the manual load to voltage coefficient E | Boolean |  |  |  | LOADCAT
5591 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALD | A flag indicating the manual load to voltage coefficient B | Boolean |  |  |  | LOADCAT
5592 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALE | A flag indicating the manual load to voltage coefficient D | Boolean |  |  |  | LOADCAT
5593 | DNOM Component | Load | LOAD | input | LOADCAT.HASLOADVOLTMANUALF | A flag indicating the manual load to voltage coefficient F | Boolean |  |  |  | LOADCAT
5594 | DNOM Component | Load | LOAD | input | LOADCAT.ID | Unique and persistent ID | String |  |  |  | DNMOBJ
5595 | DNOM Component | Load | LOAD | input | LOADCAT.INDEXINT | Array of sub-interval's major interval indices | String |  |  |  | LOADCAT
5596 | DNOM Component | Load | LOAD | input | LOADCAT.INTNAME | The name of each major study interval | String |  |  |  | LOADCAT
5597 | DNOM Component | Load | LOAD | input | LOADCAT.LIMCOST | Voltage limit violation cost | Float |  | $/p.u. V | $/p.u. V | LOADCAT
5598 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALAA | Manual load to voltage coefficient A | Boolean |  |  |  | LOADCAT
5599 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALBB | Manual load to voltage coefficient C | Boolean |  |  |  | LOADCAT
5600 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALCC | Manual load to voltage coefficient E | Boolean |  |  |  | LOADCAT
5601 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALDD | Manual load to voltage coefficient B | Boolean |  |  |  | LOADCAT
5602 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALEE | Manual load to voltage coefficient D | Boolean |  |  |  | LOADCAT
5603 | DNOM Component | Load | LOAD | input | LOADCAT.LOADVOLTMANUALFF | Manual load to voltage coefficient F | Boolean |  |  |  | LOADCAT
5604 | DNOM Component | Load | LOAD | input | LOADCAT.NAME | Name of associated load category. | String
5605 | DNOM Component | Load | LOAD | input | LOADCAT.NMDAYINT | The number of daily study mode historical load data major intervals (for use by study DPF) | Integer |  |  |  | LOADCAT
5606 | DNOM Component | Load | LOAD | input | LOADCAT.NMSUBINT | The number of subintervals for the study interval (time intervals do not have to be consecutive, interval may cover 9–11 AM and 3–5 PM) | Integer |  |  |  | LOADCAT
5607 | DNOM Component | Load | LOAD | input | LOADCAT.NUMLDSCH | The number of associated load schedules | Integer |  |  |  | LOADCAT
5608 | DNOM Component | Load | LOAD | input | LOADCAT.OPTVEMGHIGH | Optimization emergency high voltage limit | Integer |  |  |  | LOADCAT
5609 | DNOM Component | Load | LOAD | input | LOADCAT.OPTVEMGLOW | Optimization emergency low voltage limit | Integer |  |  |  | LOADCAT
5610 | DNOM Component | Load | LOAD | input | LOADCAT.OPTVNRMHIGH | Optimization normal high voltage limit | Integer |  |  |  | LOADCAT
5611 | DNOM Component | Load | LOAD | input | LOADCAT.OPTVNRMLOW | Optimization normal low voltage limit | Integer |  |  |  | LOADCAT
5612 | DNOM Component | Load | LOAD | input | LOADCAT.PCOSTINT | Value of uninterrupted service | Float |  | $/kW | $/kW | LOADCAT
5613 | DNOM Component | Load | LOAD | input | LOADCAT.PEAKLOAD | Flag indicating the load P and Q nominal values represent peak values (true = peak) | Boolean |  |  |  | LOADCAT
5614 | DNOM Component | Load | LOAD | input | LOADCAT.REACTSCH | Flag indicating the reactive power schedule is given (true = reactive power schedule is given, false = power factor schedule is given) | Boolean |  |  |  | LOADCAT
5615 | DNOM Component | Load | LOAD | input | LOADCAT.STARTTM | Subinterval start times | Float |  | Hours | Hours | LOADCAT
5616 | DNOM Component | Load | LOAD | input | LOADCAT.VEMGHIGH | Emergency high voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5617 | DNOM Component | Load | LOAD | input | LOADCAT.VEMGLOW | Emergency low voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5618 | DNOM Component | Load | LOAD | input | LOADCAT.VIMBAL | Voltage imbalance limit for three-phase loads (percent) | Float |  |  |  | LOADCAT
5619 | DNOM Component | Load | LOAD | input | LOADCAT.VNRMHIGH | Normal high voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5620 | DNOM Component | Load | LOAD | input | LOADCAT.VNRMLOW | Normal low voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5621 | DNOM Component | Load | LOAD | input | LOADCAT.VOLTAGEBASE | Voltage base value | Float |  |  |  | LOADCAT
5622 | DNOM Component | Load | LOAD | input | LOADCAT.VOLTUNIT | Enumerated units flag for the six voltage limits. The enumeration has the following values: 1 = per unit, 2 = Voltage on a configurable voltage base. | Boolean |  |  |  | LOADCAT
5623 | DNOM Component | Load | LOAD | input | LOADCAT.VSTBHIGH | Load stability high voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5624 | DNOM Component | Load | LOAD | input | LOADCAT.VSTBLOW | Load stability low voltage limit (per unit or configurable voltage base) | Float |  |  |  | LOADCAT
5625 | DNOM Component | Load | LOAD | input | LOADCAT.VUBFCOST | Voltage imbalance limit violation cost | Float |  | $/p.u. V | $/p.u. V | LOADCAT
5626 | DNOM Component | Load | LOAD |  | KVAR3PHNATIVE | Native load reactive power phase ABC | String
5627 | DNOM Component | Load | LOAD |  | KVARADER | Associated DER apparent power phase A | String
5628 | DNOM Component | Load | LOAD |  | KVARANATIVE | Native load reactive power phase A | String
5629 | DNOM Component | Load | LOAD |  | KVARBDER | Associated DER apparent power phase B | String
5630 | DNOM Component | Load | LOAD |  | KVARBNATIVE | Native load reactive power phase B | String
5631 | DNOM Component | Load | LOAD |  | KVARCDER | Associated DER apparent power phase C | String
5632 | DNOM Component | Load | LOAD |  | KVARCNATIVE | Native load reactive power phase C | String
5633 | DNOM Component | Load | LOAD | output | KW3PH | Total real power flow (kW). | Float | DPF | kW | kW
5634 | DNOM Component | Load | LOAD |  | KW3PHDER | Associated DER active power phase ABC | String
5635 | DNOM Component | Load | LOAD |  | KW3PHNATIVE | Native load real power phase ABC | String
5636 | DNOM Component | Load | LOAD |  | KWADER | Associated DER active power phase A | String
5637 | DNOM Component | Load | LOAD |  | KWANATIVE | Native load real power phase A | String
5638 | DNOM Component | Load | LOAD |  | KWBDER | Associated DER active power phase B | String
5639 | DNOM Component | Load | LOAD |  | KWBNATIVE | Native load real power phase B | String
5640 | DNOM Component | Load | LOAD |  | KWCDER | Associated DER active power phase C | String
5641 | DNOM Component | Load | LOAD |  | KWCNATIVE | Native load real power phase C | String
5642 | DNOM Component | Load | LOAD | output | LDSCHEDDISTTFLOADPERCENT | Associated distribution transformer loading (using manually overrided capacity) | Float |  | % | %
5643 | DNOM Component | Load | LOAD | output | LDSCHEDDISTTFLOADRATINGPERCENT | Associated distribution transformer loading (using transformer rating capacity) | Float |  | % | %
5644 | DNOM Component | Load | LOAD | output | LDSCHEDSECVOLTDROP | Associated distribution transformer secondary voltage drop | Float |  | % | %
5645 | DNOM Component | Load | LOAD |  | LDSCHEDSECVOLTNAME | Secondary voltage drop load schedule name | Float
5646 | DNOM Component | Load | LOAD | input | LOADCAT | Pointer to the associated load category | String
5647 | DNOM Component | Load | LOAD | input | LOADHASGEN | Indicates whether the load is with generation | Boolean
5648 | DNOM Component | Load | LOAD | input | LOADHASMAN | Manual entry enable flag | Boolean | DPF
5649 | DNOM Component | Load | LOAD | output | LOADHASVHIGHLMTMANENABLE | Whether the load has high voltage limit. | Boolean | DPF | #N/A | #N/A
5650 | DNOM Component | Load | LOAD | output | LOADHASVLOWLMTMANENABLE | Whether the load has low voltage limit. | Boolean | DPF | #N/A | #N/A
5651 | DNOM Component | Load | LOAD |  | LOADHASVOPTHIGHLMTMANENABLE | Load has manually entered optimization high voltage limit. | Boolean
5652 | DNOM Component | Load | LOAD |  | LOADHASVOPTLOWLMTMANENABLE | Load has manually entered optimization low voltage limit. | Boolean
5653 | DNOM Component | Load | LOAD | output | LOADIMBALVOLTVALUE | Voltage Imbalance | String | DPF | #N/A | #N/A
5654 | DNOM Component | Load | LOAD | output | LOADKVARA | Phase A reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5655 | DNOM Component | Load | LOAD | output | LOADKVARB | Phase B reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5656 | DNOM Component | Load | LOAD | output | LOADKVARC | Phase C reactive power flow (kVAR). | Float | DPF | kVAR | kVAR
5657 | DNOM Component | Load | LOAD | output | LOADKWA | Phase A real power flow (kW). | Float | DPF | kW | kW
5658 | DNOM Component | Load | LOAD | output | LOADKWB | Phase B real power flow (kW). | Float | DPF | kW | kW
5659 | DNOM Component | Load | LOAD | output | LOADKWC | Phase C real power flow (kW). | Float | DPF | kW | kW
5660 | DNOM Component | Load | LOAD | input | LOADMANPA | Phase A or AB (if delta connected) nominal load (kW) | Float | DPF
5661 | DNOM Component | Load | LOAD | input | LOADMANPB | Phase B or BC (if delta connected) nominal load (kW) | Float | DPF
5662 | DNOM Component | Load | LOAD | input | LOADMANPC | Phase C or CA (if delta connected) nominal load (kW) | Float | DPF
5663 | DNOM Component | Load | LOAD | input | LOADMANQA | Phase A or AB (if delta connected) nominal load (kVAR) | Float | DPF
5664 | DNOM Component | Load | LOAD | input | LOADMANQB | Phase B or BC (if delta connected) nominal load (kVAR) | Float | DPF
5665 | DNOM Component | Load | LOAD | input | LOADMANQC | Phase C or CA (if delta connected) nominal load (kVAR) | Float | DPF
5666 | DNOM Component | Load | LOAD |  | LOADNUMBERDRCUSTOMERS | Number of customers with DER | String
5667 | DNOM Component | Load | LOAD |  | LOADNUMBERGENCUSTOMERS | Number of customers with generation | String
5668 | DNOM Component | Load | LOAD | input | LOADOPTVLIMHIGHEMERG | Optimization Emergency high voltage limit. | Float
5669 | DNOM Component | Load | LOAD | input | LOADOPTVLIMHIGHNORM | Optimization Normal high voltage limit. | Float
5670 | DNOM Component | Load | LOAD | input | LOADOPTVLIMLOWEMERG | Optimization Emergency low voltage limit. | Float
5671 | DNOM Component | Load | LOAD | input | LOADOPTVLIMLOWNORM | Optimization Normal low voltage limit. | Float
5672 | DNOM Component | Load | LOAD | input | LOADOPTVLIMMANHIGH | Manually entered optimization high voltage limit. | Float
5673 | DNOM Component | Load | LOAD | input | LOADOPTVLIMMANLOW | Manually entered optimization low voltage limit. | Float
5674 | DNOM Component | Load | LOAD | output | LOADORBUSHASVOLTIMBALVIOLATION | Whether the load has voltage imbalance violation. | Boolean | DPF | #N/A | #N/A
5675 | DNOM Component | Load | LOAD | output | LOADOUTAGELENGTH | Load last outage length. | String | DPF | #N/A | #N/A
5676 | DNOM Component | Load | LOAD | output | LOADOUTAGETIME | Last recorded outage time (for cold load pick-up calculations). | String | NTP | #N/A | #N/A
5677 | DNOM Component | Load | LOAD | output | LOADPF | Power Factor | Float | DPF | #N/A | #N/A
5678 | DNOM Component | Load | LOAD |  | LOADPFNOM | Total nominal power factor of the load | Float
5679 | DNOM Component | Load | LOAD |  | LOADPFNOMA | Phase A or AB (if delta connected) nominal power factor of the load | Float
5680 | DNOM Component | Load | LOAD |  | LOADPFNOMB | Phase B or BC (if delta connected) nominal power factor of the load | Float
5681 | DNOM Component | Load | LOAD |  | LOADPFNOMC | Phase C or CA (if delta connected) nominal power factor of the load | Float
5682 | DNOM Component | Load | LOAD | input | LOADPNORM | Total nominal power of the load. | Float
5683 | DNOM Component | Load | LOAD | input | LOADPNORMA | Phase A or AB (if delta connected) nominal power of the load. | Float
5684 | DNOM Component | Load | LOAD | input | LOADTF.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
5685 | DNOM Component | Load | LOAD | input | LOADTF.DNOMX | X coordinate of the object | Float |  |  |  | DNMOBJ
5686 | DNOM Component | Load | LOAD | input | LOADTF.DNOMY | Y coordinate of the object | Float |  |  |  | DNMOBJ
5687 | DNOM Component | Load | LOAD | input | LOADTF.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
5688 | DNOM Component | Load | LOAD | input | LOADTF.ID | ID of the object | String |  |  |  | DNMOBJ
5689 | DNOM Component | Load | LOAD | input | LOADTF.NAME | Name of the object | String |  |  |  | DNMOBJ
5690 | DNOM Component | Load | LOAD | input | LOADTF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5691 | DNOM Component | Load | LOAD | input | LOADTF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5692 | DNOM Component | Load | LOAD | input | LOADTF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5693 | DNOM Component | Load | LOAD | input | LOADPNORMB | Phase B or BC (if delta connected) nominal power of the load. | Float
5694 | DNOM Component | Load | LOAD | input | LOADPNORMC | Phase C or CA (if delta connected) nominal power of the load. | Float
5695 | DNOM Component | Load | LOAD | output | LOADPQIHIGH | PQI high voltage index. | Float | DPF | #N/A | #N/A
5696 | DNOM Component | Load | LOAD | output | LOADPQIIMBALANCE | PQI imbalance voltage index for three-phase loads. | Float | DPF | #N/A | #N/A
5697 | DNOM Component | Load | LOAD | output | LOADPQILOW | PQI low voltage index | Float | DPF | #N/A | #N/A
5698 | DNOM Component | Load | LOAD | input | LOADPRIORITY | Load priority | Boolean
5699 | DNOM Component | Load | LOAD | output | LOADPRIORITY | Load priority | Integer
5700 | DNOM Component | Load | LOAD | input | LOADQNORM | Total nominal reactive power of the load. | Float
5701 | DNOM Component | Load | LOAD | input | LOADQNORMA | Phase A or AB (if delta connected) nominal reactive power of the load. | Float
5702 | DNOM Component | Load | LOAD | input | LOADQNORMB | Phase B or BC (if delta connected) nominal reactive power of the load. | Float
5703 | DNOM Component | Load | LOAD | input | LOADQNORMC | Phase C or CA (if delta connected) nominal reactive power of the load. | Float
5704 | DNOM Component | Load | LOAD | output | LOADRESTORETIME | Last recorded restoration time (for cold load pick-up calculations). | String | NTP | #N/A | #N/A
5705 | DNOM Component | Load | LOAD | output | LOADSOURCE | Load value source (Dynamic Schedule, Telemetered, Manually Replaced, AMI Fixed, AMI Scaled, or Static Schedule) | String
5706 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN1 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5707 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN2 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5708 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN3 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5709 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN4 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5710 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN5 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5711 | DNOM Component | Load | LOAD | output | LOADSTUDYBIN6 | Real time DPF delta load factor (difference in allocated and estimated load for a given day type and time period). | Float | DPF | #N/A | #N/A
5712 | DNOM Component | Load | LOAD | input | LOADTF | Pointer to secondary transformer | String
5713 | DNOM Component | Load | LOAD | input | LOADTFNAME | Connected transformer ID. | String
5714 | DNOM Component | Load | LOAD | input | LOADTFNAME2 | Connected transformer ID(Special version to account for multiple transformers in a bank). | String
5715 | DNOM Component | Load | LOAD |  | LOADTFNAMEFIRST | First connected transformer ID (Special version to account for multiple transformers in a bank) | Float
5716 | DNOM Component | Load | LOAD | output | LOADTFVOLTA | Phase A Voltage magnitude of connected distribution transformer | Float | DPF | Volt | Volt
5717 | DNOM Component | Load | LOAD | output | LOADTFVOLTB | Phase B Voltage magnitude of connected distribution transformer | Float | DPF | Volt | Volt
5718 | DNOM Component | Load | LOAD | output | LOADTFVOLTC | Phase C Voltage magnitude of connected distribution transformer | Float | DPF | Volt | Volt
5719 | DNOM Component | Load | LOAD | input | LOADVLIMHIGHEMERG | High emergency voltage limit (configurable voltage base). | Float
5720 | DNOM Component | Load | LOAD | input | LOADVLIMHIGHNORM | High normal voltage limit (configurable voltage base). | Float
5721 | DNOM Component | Load | LOAD | input | LOADVLIMHIGHSTAB | Stability voltage high limit | Float
5722 | DNOM Component | Load | LOAD | input | LOADVLIMIMBALANCE | Voltage imbalance limit | Float
5723 | DNOM Component | Load | LOAD | input | LOADVLIMLOWEMERG | Low normal voltage limit (configurable voltage base). | Float
5724 | DNOM Component | Load | LOAD | input | LOADVLIMLOWNORM | Low emergency voltage limit (configurable voltage base). | Float
5725 | DNOM Component | Load | LOAD |  | LOADVLIMLOWSTAB | Stability voltage low limit | Float
5726 | DNOM Component | Load | LOAD | input | LOADVLMTMANHIGH | High voltage limit override. | Float
5727 | DNOM Component | Load | LOAD | input | LOADVLMTMANLOW | Low voltage limit override. | Float
5728 | DNOM Component | Load | LOAD | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
5729 | DNOM Component | Load | LOAD | output | MANENTRYLOAD | Whether the load has manual entry. | Boolean | DPF | #N/A | #N/A
5730 | DNOM Component | Load | LOAD | input | PRIMNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
5731 | DNOM Component | Load | LOAD | input | PRIMNODE.DNOMX | X coordinate of the object | Float |  |  |  | DNMOBJ
5732 | DNOM Component | Load | LOAD | input | PRIMNODE.DNOMY | Y coordinate of the object | Float |  |  |  | DNMOBJ
5733 | DNOM Component | Load | LOAD | input | PRIMNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
5734 | DNOM Component | Load | LOAD | input | PRIMNODE.ID | ID of the object | String |  |  |  | DNMOBJ
5735 | DNOM Component | Load | LOAD | input | PRIMNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5736 | DNOM Component | Load | LOAD | input | PRIMNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5737 | DNOM Component | Load | LOAD | input | PRIMNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5738 | DNOM Component | Load | LOAD | input | PRIMNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
5739 | DNOM Component | Load | LOAD | input | NAME | Object name | String |  |  |  | DNMOBJ
5740 | DNOM Component | Load | LOAD | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5741 | DNOM Component | Load | LOAD | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5742 | DNOM Component | Load | LOAD |  | NONCONFORMINGLOAD | Flag indicating a non-conforming load | String
5743 | DNOM Component | Load | LOAD | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5744 | DNOM Component | Load | LOAD | input | NUMCUST | Customer count. | Integer
5745 | DNOM Component | Load | LOAD |  | NUMDRCUSTOMER | The number of customers participating in demand response program | Integer
5746 | DNOM Component | Load | LOAD | input | SERVCNTR.NAME | Service center name. | String
5747 | DNOM Component | Load | LOAD |  | NUMGENCUSTOMER | The number of customers that have generation | Integer
5748 | DNOM Component | Load | LOAD | input | NUMREGDT | The number of regular day types | Integer
5749 | DNOM Component | Load | LOAD | input | NUMSTBIN | The total number of historical data bins for study mode. | Integer
5750 | DNOM Component | Load | LOAD | output | PFCOMPTIME | Latest power flow solution time. | String | DPF | #N/A | #N/A
5751 | DNOM Component | Load | LOAD | input | PNOMA | Nominal phase A real power demand (kW). | Float
5752 | DNOM Component | Load | LOAD | input | PNOMB | Nominal phase B real power demand (kW). | Float
5753 | DNOM Component | Load | LOAD | input | PNOMC | Nominal phase C real power demand (kW). | Float
5754 | DNOM Component | Load | LOAD |  | PQFLOWA | Phase A output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
5755 | DNOM Component | Load | LOAD |  | PQFLOWB | Phase B output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
5756 | DNOM Component | Load | LOAD |  | PQFLOWC | Phase C output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
5757 | DNOM Component | Load | LOAD | input | PRIMCONN | Composite flag (mask). | Integer
5758 | DNOM Component | Load | LOAD | input | PRIMMETLOAD | Flag indicating load is a primary meter load (true = primary). | Boolean
5759 | DNOM Component | Load | LOAD | input | PRIMNODE | Pointer to the primary node | String
5760 | DNOM Component | Load | LOAD | output | PRMETERLOADAMPA | Phase A current. | Float | DPF | Amps | Amps
5761 | DNOM Component | Load | LOAD | output | PRMETERLOADAMPB | Phase B current. | Float | DPF | Amps | Amps
5762 | DNOM Component | Load | LOAD | output | PRMETERLOADAMPC | Phase C current. | Float | DPF | Amps | Amps
5763 | DNOM Component | Load | LOAD | input | PRMETERLOADKVA | Total connected load value (kVA). | Float
5764 | DNOM Component | Load | LOAD | input | QNOMA | Nominal phase A reactive power demand (kW). | Float
5765 | DNOM Component | Load | LOAD | input | QNOMB | Nominal phase B reactive power demand (kW). | Float
5766 | DNOM Component | Load | LOAD | input | QNOMC | Nominal phase C reactive power demand (kW). | Float
5767 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANA | Phase A Voltage with service drop | Float | DPF | Volt | Volt
5768 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANALG | Phase A LG Voltage with service drop | Float | DPF | Volt | Volt
5769 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANALL | Phase A LL Voltage with service drop | Float | DPF | Volt | Volt
5770 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANB | Phase B Voltage with service drop | Float | DPF | Volt | Volt
5771 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANBLG | Phase B LG Voltage with service drop | Float | DPF | Volt | Volt
5772 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANBLL | Phase B LL Voltage with service drop | Float | DPF | Volt | Volt
5773 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANC | Phase C Voltage with service drop | Float | DPF | Volt | Volt
5774 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANCLG | Phase C LG Voltage with service drop | Float | DPF | Volt | Volt
5775 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEANCLL | Phase C LL Voltage with service drop | Float | DPF | Volt | Volt
5776 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEOPA | From end phase A voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
5777 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEOPB | From end phase B voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
5778 | DNOM Component | Load | LOAD |  | SERVICEVOLTANDANGLEOPC | From end phase C voltage (magnitude on configurable voltage base and angle) for operator pop-up. | Float
5779 | DNOM Component | Load | LOAD | input | SHUNTCONNECTION | Connection type (Delta, Grounded Wye, or Ungrounded Wye) | String
5780 | DNOM Component | Load | LOAD | input | SHUNTPHASING | Load phasing information. | String
5781 | DNOM Component | Load | LOAD | input | STATIONNAME | Nominal station name. | String
5782 | DNOM Component | Load | LOAD | input | STDELTAC | The load delta iteration counter | Integer
5783 | DNOM Component | Load | LOAD | input | STDELTAP | The values of the schedule correction factors for power. | String
5784 | DNOM Component | Load | LOAD | input | STDELTAQ | The values of the schedule correction factors for reactive power. | String
5785 | DNOM Component | Load | LOAD | input | SUPPLIER | Energy supplier. | Integer
5786 | DNOM Component | Load | LOAD | output | SUSPECTLDA | Phase A voltage information if the load DPF result is suspect. | Float | DPF | #N/A | #N/A
5787 | DNOM Component | Load | LOAD | output | SUSPECTLDB | Phase B voltage information if the load DPF result is suspect. | Float | DPF | #N/A | #N/A
5788 | DNOM Component | Load | LOAD | output | SUSPECTLDC | Phase C voltage information if the load DPF result is suspect. | Float | DPF | #N/A | #N/A
5789 | DNOM Component | Load | LOAD | output | SUSPECTLOAD | Whether the load is suspect. | Boolean | DPF | #N/A | #N/A
5790 | DNOM Component | Load | LOAD |  | TYPE | Type of the load | Integer
5791 | DNOM Component | Load | LOAD | output | VOLTANDANGLEANA | Load phase A voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
5792 | DNOM Component | Load | LOAD | output | VOLTANDANGLEANB | Load phase B voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
5793 | DNOM Component | Load | LOAD | output | VOLTANDANGLEANC | Load phase C voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
5794 | DNOM Component | Load | LOAD | output | VOLTANDANGLEOPA | Phase A voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5795 | DNOM Component | Load | LOAD | output | VOLTANDANGLEOPB | Phase B voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5796 | DNOM Component | Load | LOAD | output | VOLTANDANGLEOPC | Phase C voltage (magnitude on configurable voltage base and no angle). | Float |  | Volt | Volt
5797 | DNOM Component | Load | LOAD | input | WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
5798 | DNOM Component | Load | LOAD | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
5799 | DNOM Component | Load | LOAD | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
5800 |  | Load | LOAD | output | LOADMANVOLTMEASVALUE | The SCADA voltage measurement value, if available | Float
5801 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | CurrentInfo_MVAR | Current reactive power (calculated) | Float |  | MVAR | MVAR
5802 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | CurrentInfo_MW | Current real power (calculated) | Float |  | MW | MW
5803 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | CurrentInfo_VCalc | Current voltage (calculated) | Float |  | V | V
5804 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | CurrentInfo_VMeas | Current voltage (measured) | Float |  | V | V
5805 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ForecastInfo_MVAR | Forecast reactive power | Float |  | MVAR | MVAR
5806 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ForecastInfo_MW | Forecast real power | Float |  | MW | MW
5807 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ForecastInfo_VCalc | Forecast voltage | Float
5808 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ForecastProblemFormulation | Forecast problem formulation ID | Integer
5809 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ForecastState | State of forecast solution: None = 0, Pending = 1, In Progress = 2, Complete = 3, Complete, No Plan = 4, (station level only) Failed = 5, Locked = 6 (station level only) EventTriggerWait = 7 (waiting for event trigger delay) Disabled = 8 (LVM is disabled for station in DNAF System Configuration) | Integer
5810 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplCurrInfo_MVAR | Implementation current reactive power (measured) | Float |  | MVAR | MVAR
5811 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplCurrInfo_MW | Implementation current real power (measured) | Float |  | MW | MW
5812 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplCurrInfo_VMeas | Implementation current voltage (measured) | Float |  | V | V
5813 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplementedProbForm | Inmplemented problem formulation ID | Integer
5814 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplementState | State of implementation: None = 0, InProgress = 1, Complete = 2, Failed = 3, Stopped = 4 | Integer
5815 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplStartInfo_MVAR | Implementation initial reactive power | Float |  | MVAR | MVAR
5816 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplStartInfo_MW | Implementation initial real power | Float |  | MW | MW
5817 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplStartInfo_VMeas | Implementation initial voltage | Float |  | V | V
5818 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplTargetInfo_MVAR | Implementation target reactive power | Float |  | MVAR | MVAR
5819 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplTargetInfo_MW | Implementation target real power | Float |  | MW | MW
5820 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplTargetInfo_VMeas | Implementation targer voltage | Float |  | V | V
5821 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ImplTrend | Implementation trend time-series data | String
5822 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | MaxReactiveROC | Maximum reactive power throttling | Float |  | MVAR | MVAR
5823 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | MaxRealROC | Maximum real power throttling | Float |  | MW | MW
5824 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | MinReactiveROC | Minimum reactive power throttling | Float |  | MVAR | MVAR
5825 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | MinRealROC | Minimum real power throttling | Float |  | MW | MW
5826 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | Name | Name of the area | String
5827 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | ProfileName | Name of the selected problem formulation profile | String
5828 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | StationNames | Names of stations in area | String
5829 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | Trend | Current trend time-series data | String
5830 | LVM System Monitor Data Store | LVM System Monitor Area | LSMAREA | output | Type | Type of the area: System = 0 Optimization = 1 Division = 2 | Integer
5831 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ActualVoltReduction | Actual voltage reduction | Float |  | V | V
5832 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | Division | The associated division name | String
5833 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | EligibleDevices | The number of eligible devices | Integer
5834 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ExcludedDevices | The number of excluded devices | Integer
5835 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastCriticalConstraintActualValue | Actual value of the critical constraint | Float
5836 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastCriticalConstraintID | ID of the critical constraint from LVM solution | String
5837 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastCriticalConstraintLimitValue | Limit value of the critical constraint | Float
5838 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastCriticalConstraintPenaltyValue | Penalty value of the critical constraint | Float
5839 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastCriticalConstraintType | Limit type represented by the critical constraint | String
5840 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastRealPowerReduction | Forecasted real power reduction | Float |  | MW | MW
5841 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastSteps | The number of steps in forecast plan | Integer
5842 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ForecastVoltReduction | Forecasted voltage reduction | Float |  | V | V
5843 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ImplementedProbForm | ID of the implemented problem formulation | Integer
5844 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ImplementedProblemFormulationName | The name of the implemented problem formulation | String
5845 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ImplementState | Implementation state (from Plan Manager) | Integer
5846 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | IneligibleDevices | The number of ineligible devices | Integer
5847 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | IsLocked | Is station problem formulation locked? | Boolean
5848 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | IsMeasuredPower | True if measured power is available (if not MeasValues = CalcValues) | Boolean
5849 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | IsMeasuredVoltage | True if measured voltage is available (if not MeasValues = CalcValues | Boolean
5850 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | LockedFeeders | The number of feeders with locked problem formulations | Integer
5851 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | LockedTrans | The number of transformers with locked problem formulations | Integer
5852 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | Name | Station name | String
5853 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | NumFeeders | The number of feeders in the station | Integer
5854 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | NumFeeders | The number of feeders in the station | Integer
5855 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | NumTrans | The number of station TF banks in the station | Integer
5856 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | NumTrans | The number of station TF banks in the station | Integer
5857 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | PlanSolved | Date and time when the plan was solved | String
5858 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | PlanSolvedTimeValue | Date and time when the plan was solved | String
5859 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | PreImplementedProbForm | ID of the problem formulation that was used before the implementation | Integer
5860 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | PreImplementedProbFormName | The name of the problem formulation that was used before the implementation | String
5861 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ProblemFormulation | Problem formulation ID | Integer
5862 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ProblemFormulationName | Problem formulation name | String
5863 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | ProfileName | The name of the forecasted profile | String
5864 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | RetriggerCount | The number of step implementation attempts performed | Integer
5865 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | State | State of forecast solution | Integer
5866 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | StepsFailed | Number of failed implementation steps | Integer
5867 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | StepsImplemented | Number of successfully implemented steps | Integer
5868 | LVM System Monitor Data Store | LVM System Monitor Station | LSMSTATION | output | StepsNotImplemented | Number of steps that failed to implement | Integer
5869 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | CurrentForecastAreaName | Name of the area for which the forecast is being performed | String
5870 | DNOM Component | Measurement | MEAS | input | DNOMOBJ.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
5871 | DNOM Component | Measurement | MEAS | input | DNOMOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
5872 | DNOM Component | Measurement | MEAS | input | DNOMOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
5873 | DNOM Component | Measurement | MEAS | input | DNOMOBJ.ID | Object unique ID | String |  |  |  | DNMOBJ
5874 | DNOM Component | Measurement | MEAS | input | DNOMOBJ.NAME | Object name | String |  |  |  | DNMOBJ
5875 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ForecastPeriod | Forecast period in minutes | Float
5876 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ImplementationComplete | Time most recent implementation completed | String
5877 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ImplementationID | ID for most recent implementation | String
5878 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ImplementationStarted | Time most recent implementation started | String
5879 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ImplementationStopped | Specifies whether implementation was stopped for an area | Boolean
5880 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | MaxPlanAge | Maximum plan age in minutes | Float
5881 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | MaxTrendAge | Maximum trend age in minutes | Float
5882 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | MaxVoltageLimit | Maximum voltage limit | Float | V | V
5883 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | MinVoltageLimit | Minimum voltage limit | Float | V | V
5884 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | Name | Name of the system element (for example, System) | String
5885 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | OtherInstanceImplementing | Specifies whether another instance of the LVM System Monitor is currently implementing plans. Use to prioritize implementation over forecasting by pausing the forecasting by the LVM System Monitor Read-Only when plans are implemented by the LVM System Monitor. | String
5886 | LVM System Monitor Data Store | LVM System Monitor System | LSMSYSTEM | output | ServerConnected | True when forecast server is connected | Boolean
5887 | DNOM Component | Measurement | MEAS |  | _KEY | The unique identifier of the measurement | String
5888 | DNOM Component | Measurement | MEAS |  | ANALOGMEASDEV | Analog measurement device | String
5889 | DNOM Component | Measurement | MEAS |  | AREANAME | Area name - only for area load measurements (MW) | String
5890 | DNOM Component | Measurement | MEAS |  | DATASOURCEFEED | SCADA datasource feed. 0 = Telemetered (coming from RTU) 1 = Manual (Local) | Integer
5891 | DNOM Component | Measurement | MEAS |  | DEFQUALITY | Default quality | Integer
5892 | DNOM Component | Measurement | MEAS |  | DEFVALUE | Analog measurement default value | Integer
5893 | DNOM Component | Measurement | MEAS |  | DNAFTRIG | Flag indicating that DNAF should consider this measurement when performing a rate of change trigger check (such as feeder head amps or voltage measurements) | Boolean
5894 | DNOM Component | Measurement | MEAS |  | DNOMID | DNOM ID | String
5895 | DNOM Component | Measurement | MEAS | input | DNOMOBJ | Pointer to the component associated with the measurement | String
5896 | DNOM Component | Measurement | MEAS | input | HASMEASNAMEFOROBJECT | Has measurement name for object? | Boolean
5897 | DNOM Component | Measurement | MEAS | input | ID | Object unique ID | String |  |  |  | DNMOBJ
5898 | DNOM Component | Measurement | MEAS |  | iMeasurementTypeId | Converter - Measurement type (flow, status, other). | Integer
5899 | DNOM Component | Measurement | MEAS |  | iPhase | The phase the measurement is on (A, B, C, or three-phase) | Integer
5900 | DNOM Component | Measurement | MEAS |  | ISANALOG | Flag indicating whether the measurement is an analog or a status measurement (true = analog, false = status) | Boolean
5901 | DNOM Component | Measurement | MEAS |  | ISCOMPMEAS | If True, the measurement is shown in the Measurement Comparison Data grid tabular display (flow and voltage analogs) | Boolean
5902 | DNOM Component | Measurement | MEAS |  | ISSECVOLTMEAS | Specifies whether the measurement is a secondary voltage measurement | Boolean
5903 | DNOM Component | Measurement | MEAS |  | ISSTATMS | A flag indicating that the measurement is associated with the station and not a specific node or component | Boolean
5904 | DNOM Component | Measurement | MEAS |  | iTerminalId | Converter - Terminal ID (from-0/to-1/tertiary-2) the measurement is on | Integer
5905 | DNOM Component | Measurement | MEAS |  | iUnits | Measurement units for current, voltage, power, and other measurements Base = 0, Kilo = 1, Mega = 2 PerUnit = 3 | Integer
5906 | DNOM Component | Measurement | MEAS |  | MBITMASK | Bitmask field for measurements. (bit 0 - normal status value, 1 - current status value, 2 - last status value, 3 - invert value, 4 - BLA obtained, 5 - DDNOM multi state measurement, the combination of SDIS and XDIS is hard coded, 6 - scada multi state measurement, the combination with XDIS = true is defined in config file, 7 - not used now, 8 - has effective device set, 9 - extended current status value, 10 - extended last status value, 11 - extended invert value, 12 - extended BLA obtained, 13 - multi state false value 01, 14 - multi state false value 11, 15 - Not used now, 16 - multichange normal status value, 17 - multichange current status value, 18 - multichange last status value, 19 - multichange invert value, 20 - multi state True value 01, 21 - multi state True value 11, 23 - Meas DNAF flag, 24 - Possible interface voltage measurement, 25 - analogue and status measurement initialized, 26 - Not used now, 27 - Indicates this is a Group Multi-Phase Measurement for a device that has individual phase measurements for the same function. | Integer
5907 | DNOM Component | Measurement | MEAS |  | MEASBASE | Voltage measurement base value | Integer
5908 | DNOM Component | Measurement | MEAS | input | MEASCHECKTIMESTAMPE | Measurement check time stamp | String
5909 | DNOM Component | Measurement | MEAS |  | MEASCLAS | Measurement classification (analog, status, set point, or control point) | Integer
5910 | DNOM Component | Measurement | MEAS |  | MEASCOMPID | ID of the measurement | String
5911 | DNOM Component | Measurement | MEAS |  | MEASCOMPNAME | Name of the measurement | String
5912 | DNOM Component | Measurement | MEAS |  | MEASCOMPPFPERC | Difference between the SCADA-measured and DPF-calculated values, in percentage. | String
5913 | DNOM Component | Measurement | MEAS |  | MEASCOMPPFVALUE | Measurement distribution power flow calculated value | String
5914 | DNOM Component | Measurement | MEAS |  | MEASCOMPSUBTYPE | DNOM object type of the device that the measurement is associated with (for example, dmsPowerTf). | String
5915 | DNOM Component | Measurement | MEAS |  | MEASCOMPTYPE | DNOM record name of the device that the measurement is associated with (for example, TF). | String
5916 | DNOM Component | Measurement | MEAS |  | MEASCOMPTYPESTRING | Type of the component the measurement is associated with | String
5917 | DNOM Component | Measurement | MEAS |  | MEASDNAFFLAG | A flag indicating if the analog measurement is used in DNAF applications | Boolean
5918 | DNOM Component | Measurement | MEAS |  | MEASEVALUATED | Measurement evaluated | String
5919 | DNOM Component | Measurement | MEAS |  | MEASFLIPANALOG | Measurement flip analog | String
5920 | DNOM Component | Measurement | MEAS |  | MEASMANVALIDITY | Manual value of the SCADA quality measurement | String
5921 | DNOM Component | Measurement | MEAS |  | MEASMANVALUE | Manual measurement value (for Study mode) | Float
5922 | DNOM Component | Measurement | MEAS |  | MEASMDIS | MDIS | String
5923 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECT | Composite ID of a SCADA Point of the device (typically, status, but could be analog or control). Note: This query applies to DNOM objects, such as SWT. | String
5924 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTDEVICE | Name of the device that the measurement is associated with. Note: This query applies to DNOM objects, such as SWT. | String
5925 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTDEVTYP | Type of the device that the measurement is associated with. Note: This query applies to DNOM objects, such as SWT. | String
5926 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTPHASEA | Composite ID of a SCADA Point of the Phase A status measurement that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5927 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTPHASEB | Composite ID of a SCADA Point of the Phase B status measurement that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5928 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTPHASEC | Composite ID of a SCADA Point of the Phase C status measurement that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5929 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTPHASEN | Composite ID of a SCADA Point of the neutral phase status measurement that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5930 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTPOINT | Name of a SCADA Point that is associated with the device, such as STTS or DAST name for object, point. Note: This query applies to DNOM objects, such as SWT. | String
5931 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTSTATE | Composite ID of the SCADA Point that represents the state of the device. Note: This query applies to DNOM objects, such as SWT. | String
5932 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTSTRING | Composite ID of a SCADA Point that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5933 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTSUBSTN | Name of the station that the measurement is associated with. Note: This query applies to DNOM objects, such as SWT. | String
5934 | DNOM Component | Measurement | MEAS |  | MEASNAMEFOROBJECTSWO | Composite ID of a SCADA Point that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5935 | DNOM Component | Measurement | MEAS |  | MEASNAMEFORSWITCH | Composite ID of a SCADA Point that is associated with the device. Note: This query applies to DNOM objects, such as SWT. | String
5936 | DNOM Component | Measurement | MEAS |  | MEASPHASE | Measured phases | String
5937 | DNOM Component | Measurement | MEAS |  | MEASQUALITYFORFLTIND | Measurement quality for the fault indicator | String
5938 | DNOM Component | Measurement | MEAS |  | MEASQUALITYFORSWITCH | Measurement quality for switch | String
5939 | DNOM Component | Measurement | MEAS |  | MEASSCADAQUALITY | SCADA quality measurement | String
5940 | DNOM Component | Measurement | MEAS |  | MEASSCALEFACT | Bus Load Allocation scaling factor for the measurement. This is the value to which the scheduled nominal loads for a measurement island were scaled by BLA to match the target measured flow values from SCADA. | Boolean
5941 | DNOM Component | Measurement | MEAS |  | MEASSDIS | SDIS | String
5942 | DNOM Component | Measurement | MEAS | input | NODE.AREAID | Index in the station permission area list | Integer |  |  |  | DNMOBJ
5943 | DNOM Component | Measurement | MEAS | input | NODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
5944 | DNOM Component | Measurement | MEAS | input | NODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
5945 | DNOM Component | Measurement | MEAS | input | NODE.FROME | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
5946 | DNOM Component | Measurement | MEAS | input | NODE.ID | ID of the node | String |  |  |  | DNMOBJ
5947 | DNOM Component | Measurement | MEAS | input | NODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5948 | DNOM Component | Measurement | MEAS | input | NODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
5949 | DNOM Component | Measurement | MEAS | input | NODE.NTPFL | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
5950 | DNOM Component | Measurement | MEAS | input | NODE.VOLTC | Node mask | Integer |  |  |  | NODE
5951 | DNOM Component | Measurement | MEAS |  | MEASSIMONLY | A flag indicating the simulator only measurement | Boolean
5952 | DNOM Component | Measurement | MEAS |  | MEASSTATIONFOROBJECT | Name of the station that the measurement is associated with. Note: This query applies to DNOM objects, such as SWT. | String
5953 | DNOM Component | Measurement | MEAS |  | MEASSTNNAME | Name of the station that the measurement is associated with | String
5954 | DNOM Component | Measurement | MEAS |  | MEASSUBNAME | Substation the measurement belongs to | String
5955 | DNOM Component | Measurement | MEAS |  | MEASTERMINALID | ID of the measurement terminal (From Side of To Side) | String
5956 | DNOM Component | Measurement | MEAS |  | MEASTIME | Time of the measurement | String
5957 | DNOM Component | Measurement | MEAS |  | MEASTYPE | Type of the measurement | String
5958 | DNOM Component | Measurement | MEAS |  | MEASSTATUSNAMES | The list of measurement statuses. | String
5959 | DNOM Component | Measurement | MEAS |  | GROUPCTRLSTATUS | The last group control execution status (0 = No permission, 1 = Control status unknown, 2 = Already in requested state, 3 = Pending, 4 = Succeeded, or 5 = Failed) | String
5960 | DNOM Component | Measurement | MEAS |  | GROUPCTRLTIME | The last group control execution time | DateTime
5961 | DNOM Component | Measurement | MEAS |  | MEASUNITS | Measurement unit metric prefix (e.g., Mega) | String
5962 | DNOM Component | Measurement | MEAS |  | MEASUSEMANVALIDITY | A flag indicating that the manual SCADA quality measurement is used | Boolean
5963 | DNOM Component | Measurement | MEAS |  | MEASUSEMANVALUE | A flag indicating that the manual measurement is used | Boolean
5964 | DNOM Component | Measurement | MEAS |  | MEASVALIDITY | Validity of the measurement | String
5965 | DNOM Component | Measurement | MEAS |  | MEASVALUE | Measurement value | String
5966 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.ANMGTYPE | Analog measurement group type (based on measurements that form the group) | Enumeration |  |  |  | AMSGRP
5967 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.AREAID | Index in the station permission area list | Integer |  |  |  | DNMOBJ
5968 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
5969 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
5970 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.ID | ID of the node | String |  |  |  | DNMOBJ
5971 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.NUMMEAS | The number of measurements in the group | Integer |  |  |  | AMSGRP
5972 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.TELLOAD | A flag indicating telemetered loading | Boolean |  |  |  | AMSGRP
5973 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP.THRPHALL | Flag indicating that only three-phase measurements are present | Boolean |  |  |  | AMSGRP
5974 | DNOM Component | Measurement | MEAS |  | MEASVAUEFORSWITCH | Measurement name for switch | String
5975 | DNOM Component | Measurement | MEAS |  | MEASVOLT | Measured voltage expressed as a 120V base value | Float
5976 | DNOM Component | Measurement | MEAS |  | MEASVOLTAGEFLAG | This flag indicates whether an analog voltage measurement is considered a trigger for advanced DNAF applications | Boolean
5977 | DNOM Component | Measurement | MEAS |  | MEASVOLTBASE | Voltage base that is used (e.g., 120V LG) | Float
5978 | DNOM Component | Measurement | MEAS |  | MEASVOLTCONNECTTYPE | Voltage measurement type (line to line, or line to ground) | String
5979 | DNOM Component | Measurement | MEAS |  | MEASXDIS | XDIS | String
5980 | DNOM Component | Measurement | MEAS | input | NAME | Object name | String |  |  |  | DNMOBJ
5981 | DNOM Component | Measurement | MEAS | input | NODE | Pointer to the node associated with the measurement | String
5982 | DNOM Component | Measurement | MEAS |  | NOTINIT | Flag indicating that the associated object (component or node) is initially unset from the Converter (model file) | Boolean
5983 | DNOM Component | Measurement | MEAS |  | OPERATETIME | Measurement operate time | Integer
5984 | DNOM Component | Measurement | MEAS |  | SIMONLY | A flag indicating a simulated measurement | Boolean
5985 | DNOM Component | Measurement | MEAS |  | SITENAME | Name of the site | String
5986 | DNOM Component | Measurement | MEAS |  | STDDEV | Measurement standard deviation | Integer
5987 | DNOM Component | Measurement | MEAS |  | SWOMEASUREMENTINFO | Switching Order measurement info | String
5988 | DNOM Component | Measurement | MEAS |  | TIMEOUT | Measurement timeout | Integer
5989 | DNOM Component | Measurement | MEAS | input | UPMEAS1 | - | - |  |  |  | Commented out
5990 | DNOM Component | Measurement | MEAS | input | UPMEAS2 | - | - |  |  |  | Commented out
5991 | DNOM Component | Measurement | MEAS |  | WAITTIME | Measurement wait time | Integer
5992 | DNAF Object | Measurement Island | MEASIL | input | ANMEASGP | Array of bounding measurement analog groups | String
5993 | DNAF Object | Measurement Island | MEASIL |  | MEASALLC | The type of measurements to use for the load allocation | Enumeration
5994 | DNAF Object | Measurement Island | MEASIL |  | MEASKVAA | Phase A equivalent kVA measurement | Integer
5995 | DNAF Object | Measurement Island | MEASIL |  | MEASKVAB | Phase B equivalent kVA measurement | Integer
5996 | DNAF Object | Measurement Island | MEASIL |  | MEASKVAC | Phase C equivalent kVA measurement | Integer
5997 | DNAF Object | Measurement Island | MEASIL |  | MEASKVRA | Phase A equivalent kVAR measurement | Integer
5998 | DNAF Object | Measurement Island | MEASIL |  | MEASKVRB | Phase B equivalent kVAR measurement | Integer
5999 | DNAF Object | Measurement Island | MEASIL |  | MEASKVRC | Phase C equivalent kVAR measurement | Integer
6000 | DNAF Object | Measurement Island | MEASIL |  | MEASKWA | Phase A equivalent kW measurement | Integer
6001 | DNAF Object | Measurement Island | MEASIL |  | MEASKWB | Phase B equivalent kW measurement | Integer
6002 | DNAF Object | Measurement Island | MEASIL |  | MEASKWC | Phase C equivalent kW measurement | Integer
6003 | DNAF Object | Measurement Island | MEASIL |  | MISMATA | The total phase A mismatch - to be allocated in load scaling algorithm | Integer
6004 | DNAF Object | Measurement Island | MEASIL |  | MISMATAQ | The total phase A reactive mismatch - to be allocated in load scaling algorithm | Integer
6005 | DNAF Object | Measurement Island | MEASIL |  | MISMATB | The total phase B mismatch - to be allocated in load scaling algorithm | Integer
6006 | DNAF Object | Measurement Island | MEASIL |  | MISMATBQ | The total phase B reactive mismatch - to be allocated in load scaling algorithm | Integer
6007 | DNAF Object | Measurement Island | MEASIL |  | MISMATC | The total phase C mismatch - to be allocated in load scaling algorithm | Integer
6008 | DNAF Object | Measurement Island | MEASIL |  | MISMATCQ | The total phase C reactive mismatch - to be allocated in load scaling algorithm | Integer
6009 | DNAF Object | Measurement Island | MEASIL |  | NUBLAMIT | The number of BLA iterations | Integer
6010 | DNAF Object | Measurement Island | MEASIL |  | NUMMEAS | The number of measurements that bound the island | Integer
6011 | DNAF Object | Measurement Island | MEASIL |  | PHAFLOW | Array of phase A DPF flows (P or S) | Integer
6012 | DNAF Object | Measurement Island | MEASIL |  | PHAIFLOW | Array of actual calculated phase A DPF current flows | Integer
6013 | DNAF Object | Measurement Island | MEASIL |  | PHAQFLOW | Array of BLA adjusted phase A DPF flows (Q) | Integer
6014 | DNAF Object | Measurement Island | MEASIL |  | PHAQFLWA | Array of actual calculated phase A DPF flows (including VAR flows) (Q) | Integer
6015 | DNAF Object | Measurement Island | MEASIL |  | PHBFLOW | Array of phase B DPF flows (P or S) | Integer
6016 | DNAF Object | Measurement Island | MEASIL |  | PHBIFLOW | Array of actual calculated phase B DPF current flows | Integer
6017 | DNAF Object | Measurement Island | MEASIL |  | PHBQFLOW | Array of BLA adjusted phase B DPF flows (Q) | Integer
6018 | DNAF Object | Measurement Island | MEASIL |  | PHBQFLWA | Array of actual calculated phase B DPF flows (including VAR flows) (Q) | Integer
6019 | DNAF Object | Measurement Island | MEASIL |  | PHCFLOW | Array of phase C DPF flows (P or S) | Integer
6020 | DNAF Object | Measurement Island | MEASIL |  | PHCIFLOW | Array of actual calculated phase C DPF current flows | Integer
6021 | DNAF Object | Measurement Island | MEASIL |  | PHCQFLOW | Array of BLA adjusted phase c DPF flows (Q) | Integer
6022 | DNAF Object | Measurement Island | MEASIL |  | PHCQFLWA | Array of actual calculated phase C DPF flows (including VAR flows) (Q) | Integer
6023 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | CAPVARA | Phase A capacitive kVAR | Integer
6024 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | CAPVARB | Phase B capacitive kVAR | Integer
6025 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | CAPVARC | Phase C capacitive kVAR | Integer
6026 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWA | DPF flow of phase A | Integer
6027 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWAQ | Phase A reactive power calculated | Integer
6028 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWB | DPF flow of phase B | Integer
6029 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWBQ | Phase B reactive power calculated | Integer
6030 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWC | DPF flow of phase C | Integer
6031 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | DPFFLOWCQ | Phase C reactive power calculated | Integer
6032 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESVARA | Phase A energy resource kVAR | Integer
6033 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESVARB | Phase B energy resource kVAR | Integer
6034 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESVARC | Phase C energy resource kVAR | Integer
6035 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESWATTA | Phase A energy resource kW | Integer
6036 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESWATTB | Phase B energy resource kW | Integer
6037 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ENERGYRESWATTC | Phase C energy resource kW | Integer
6038 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERVARA | Phase A generator/DER kVAR | Integer |  | kVAR | kVAR
6039 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERVARB | Phase B generator/DER kVAR | Integer |  | kVAR | kVAR
6040 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERVARC | Phase C generator/DER kVAR | Integer |  | kVAR | kVAR
6041 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERWATTA | Phase A generator/DER kW | Integer |  | kW | kW
6042 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERWATTB | Phase B generator/DER kW | Integer |  | kW | kW
6043 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENDERWATTC | Phase C generator/DER kW | Integer |  | kW | kW
6044 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENVARA | Phase A generator kVAR | Integer |  | kVAR | kVAR
6045 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENVARB | Phase B generator kVAR | Integer |  | kVAR | kVAR
6046 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENVARC | Phase C generator kVAR | Integer |  | kVAR | kVAR
6047 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENWATTA | Phase A generator kW | Integer |  | kW | kW
6048 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENWATTB | Phase B generator kW | Integer |  | kW | kW
6049 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | GENWATTC | Phase C generator kW | Integer |  | kW | kW
6050 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | ITINDEX | Iteration index | Integer
6051 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVANETA | Load allocation measurement phase A | String
6052 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVANETB | Load allocation measurement phase B | String
6053 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVANETC | Load allocation measurement phase C | String
6054 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVARNETA | Phase A reactive power target kVAR | Integer
6055 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVARNETB | Phase B reactive power target kVAR | Integer
6056 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KVARNETC | Phase C reactive power target kVAR | Integer
6057 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KWNETA | Phase A real power target kW | Integer
6058 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KWNETB | Phase B real power target kW | Integer
6059 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | KWNETC | Phase C real power target kW | Integer
6060 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | MEASILINDEX | Measurement island index | String
6061 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | MEASILNAME | Measurement island name | String
6062 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | MISMATA | The total phase A mismatch - to be allocated in load scaling algorithm | Integer
6063 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | MISMATB | The total phase B mismatch - to be allocated in load scaling algorithm | Integer
6064 | DNAF Object | Measurement Island Iteration Item | MEASILITE |  | MISMATC | The total phase C mismatch - to be allocated in load scaling algorithm | Integer
6065 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILAHASLOAD | A flag indicating that phase A of the measurement island has load | Boolean
6066 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILAVA | VA direction of phase A for one measurement island | String
6067 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILAVAR | Reactive power flow direction of phase A for one measurement island | String
6068 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILAW | Real power flow direction of phase A for one measurement island | String
6069 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILBHASLOAD | A flag indicating that phase B of the measurement island has load | Boolean
6070 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILBRID | Measurement island branch ID | String
6071 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILBRNAME | Measurement island branch name. | String
6072 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILBVA | VA direction of phase B for one measurement island | String
6073 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILBVAR | Reactive power flow direction of phase A for one measurement island | String
6074 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILBW | Real power flow direction of phase B for one measurement island | String
6075 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILCHASLOAD | A flag indicating that phase C of the measurement island has load | Boolean
6076 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILCVA | VA direction of phase C for one measurement island | String
6077 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILCVAR | Reactive power flow direction of phase A for one measurement island | String
6078 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILCW | Real power flow direction of phase C for one measurement island | String
6079 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILERRCNT | Measurement island error count | Integer
6080 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILERRCNTPERBLA | Measurement island error count per BLA | Integer
6081 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILFDNAME | Measurement island feeder name. | String
6082 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILINDEX | Measurement island index. | String
6083 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILNAME | Measurement island name. | String
6084 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILNETRES | Measurement island net validation status. | String
6085 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILNOMRES | Measurement island nominal validation status. | String
6086 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILOADALLOCTYPE | Load Allocation type for one measurement island | String
6087 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASILSHOWABLE | If measurement island result has load flag or branch name or feeder head name. | Boolean
6088 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASILSHOWABLEONLYLOADS |  | Boolean
6089 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILSTNNAME | Measurement island station name. | String
6090 | DNAF Object | Measurement Island Result | MEASILRES | input | MEASILTYPE | Meausrement Island Type. | String
6091 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_3PH_PF_COMP | Three phase power factor | Float
6092 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAA_COMP | Phase A computed apparent power | Float |  | kVA | kVA
6093 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAA_MISM | Phase A apparent power mismatch % | Float |  | kVA | kVA
6094 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAABC_COMP | Total computed apparent power | Float |  | kVA | kVA
6095 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAABC_MISM | Total reactive power mismatch % | Float
6096 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAB_COMP | Phase B computed apparent power | Float |  | kVA | kVA
6097 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAB_MISM | Phase B apparent power mismatch % | Float |  | kVA | kVA
6098 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAC_COMP | Phase C computed apparent power | Float |  | kVA | kVA
6099 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVAC_MISM | Phase C apparent power mismatch % | Float |  | kVA | kVA
6100 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARA_COMP | Phase A computed reactive power | Float |  | kVAR | kVAR
6101 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARA_COMP_DIR | Phase A computed reactive power | Float |  | kVAR | kVAR
6102 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARA_MISM | Phase A reactive power mismatch % | Float |  | kVAR | kVAR
6103 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARABC_COMP_DIR | Total computed reactive power | Float |  | kVAR | kVAR
6104 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARABC_MISM | Total apparent power mismatch % | Float
6105 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARB_COMP | Phase B computed reactive power | Float |  | kVAR | kVAR
6106 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARB_COMP_DIR | Phase B computed reactive power | Float |  | kVAR | kVAR
6107 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARB_MISM | Phase B reactive power mismatch % | Float |  | kVAR | kVAR
6108 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARC_COMP | Phase C computed reactive power | Float |  | kVAR | kVAR
6109 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARC_COMP_DIR | Phase C computed reactive power | Float |  | kVAR | kVAR
6110 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KVARC_MISM | Phase C reactive power mismatch % | Float |  | kVAR | kVAR
6111 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWA_COMP | Phase A computed real power | Float |  | kW | kW
6112 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWA_COMP_DIR | Phase A computed real power | Float |  | kW | kW
6113 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWA_MISM | Phase A real power mismatch % | Float |  | kW | kW
6114 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWABC_COMP_DIR | Total computed real power | Float |  | kW | kW
6115 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWABC_MISM | Total real power mismatch % | Float
6116 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWB_COMP | Phase B computed real power | Float |  | kW | kW
6117 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWB_COMP_DIR | Phase B computed real power | Float |  | kW | kW
6118 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWB_MISM | Phase B real power mismatch % | Float |  | kW | kW
6119 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWC_COMP | Phase C computed real power | Float |  | kW | kW
6120 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWC_COMP_DIR | Phase C computed real power | Float |  | kW | kW
6121 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLAND_KWC_MISM | Phase C real power mismatch % | Float |  | kW | kW
6122 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDCONVERGECHECKMETHOD | Convergence check method for the measurement island | String
6123 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDCONVERGEP | Real power convergence result for one measurement island | Float
6124 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDCONVERGEPQ | Apparent power convergence result for one measurement island | Float
6125 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDCONVERGEQ | Reactive power convergence result for one measurement island | Float
6126 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDKVARTOTAL | Total reactive power | Float
6127 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVARTOTALA | Total phase A reactive power | Float |  | kVAR | kVAR
6128 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVARTOTALB | Total phase B reactive power | Float |  | kVAR | kVAR
6129 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVARTOTALC | Total phase C reactive power | Float |  | kVAR | kVAR
6130 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVATOTAL | Total apparent power for the measurement island | Float |  | kVA | kVA
6131 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVATOTALA | Total phase A apparent power | Float |  | kVA | kVA
6132 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVATOTALB | Total phase B apparent power | Float |  | kVA | kVA
6133 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKVATOTALC | Total phase C apparent power | Float |  | kVA | kVA
6134 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDKWTOTAL | Total real power | Float
6135 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKWTOTALA | Total phase A real power | Float |  | kW | kW
6136 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKWTOTALB | Total phase B real power | Float |  | kW | kW
6137 | DNAF Object | Measurement Island Result | MEASILRES |  | MEASLANDKWTOTALC | Total phase C real power | Float |  | kW | kW
6138 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDMISMATCH3PH | Mismatch values for measurement island | Float
6139 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDOPENWYEDELTALOADS | Number of open wye-delta loads. | Integer
6140 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDPHABCLOADS | Number of balanced three-phase loads. | Integer
6141 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDPHALOADS | Number of phase A loads. | Integer
6142 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDPHBLOADS | Number of phase B loads. | Integer
6143 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDPHCLOADS | Number of phase C loads. | Integer
6144 | DNAF Object | Measurement Island Result | MEASILRES | output | MEASLANDPHN3LOADS | Number of non three-phase loads | Integer
6145 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHACTP | Net island high measured downstream KW | Float
6146 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHACTQ | Net island high measured downstream KVAR | Float
6147 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHACTS | Net island high measured downstream KVA | Float
6148 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHMEASP | Net island high measured upstream KW | Float
6149 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHMEASQ | Net island high measured upstream KVAR | Float
6150 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDHIGHMEASS | Net island high measured upstream KVA | Float
6151 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHACTP | Net island low measured downstream KW | Float
6152 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHACTQ | Net island low measured downstream KVAR | Float
6153 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHACTS | Net island low measured downstream KVA | Float
6154 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHMEASP | Net island low measured upstream KW | Float
6155 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHMEASQ | Net island low measured upstream KVAR | Float
6156 | DNAF Object | Measurement Island Result | MEASILRES | output | NETLANDLOWHMEASS | Net island low measured upstream KVA | Float
6157 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHACTP | Nominal island high actual KW | Float
6158 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHACTQ | Nominal island high actual KVAR | Float
6159 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHACTS | Nominal island high actual KVA | Float
6160 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHMEASP | Nominal island high measured KW | Float
6161 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHMEASQ | Nominal island high measured KVAR | Float
6162 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDHIGHMEASS | Nominal island high measured KVA | Float
6163 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHACTP | Nominal island low actual KW | Float
6164 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHACTQ | Nominal island low actual KVAR | Float
6165 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHACTS | Nominal island low actual KVA | Float
6166 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHMEASP | Nominal island low measured KW | Float
6167 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHMEASQ | Nominal island low measured KVAR | Float
6168 | DNAF Object | Measurement Island Result | MEASILRES | output | NOMILANDLOWHMEASS | Nominal island low measured KVA | Float
6169 | DNAF Object | Measurement Island Result | MEASILRES | output | NUMBLAINCONSIST | The number of devices which have a potential inconsistency issue. | Integer
6170 | DNOM Component | Meter Measurement | METERMEAS |  | AMP_A | Phase A current | Float |  | Amps | Amps
6171 | DNOM Component | Meter Measurement | METERMEAS |  | AMP_B | Phase B current | Float |  | Amps | Amps
6172 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
6173 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.BLAFLAGS | BLA flags | Integer |  |  |  | LOAD
6174 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.CRITICALCUSTNUM | Number of critical customers | Integer |  |  |  | LOAD
6175 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6176 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6177 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.DRRATIO | Demand response component of the load (in percent) | Integer |  |  |  | LOAD
6178 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
6179 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.GENRATING | Nameplate kVA rating of the generation component of the load | Integer |  |  |  | LOAD
6180 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.GENTYPE | User defined enumeration type for generation component | Integer |  |  |  | LOAD
6181 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
6182 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.ID | Object unique ID | String |  |  |  | DNMOBJ
6183 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NAME | Object name | String |  |  |  | DNMOBJ
6184 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
6185 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
6186 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
6187 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NUMCUST | Customer count. | Integer |  |  |  | LOAD
6188 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NUMDRCUSTOMER | The number of customers participating in demand response program | Integer |  |  |  | LOAD
6189 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NUMGENCUSTOMER | The number of customers that have generation | Integer |  |  |  | LOAD
6190 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NUMREGDT | The number of regular day types | Integer |  |  |  | LOAD
6191 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.NUMSTBIN | The total number of historical data bins for study mode. | Integer |  |  |  | LOAD
6192 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.PNOMA | Nominal phase A real power demand | Float |  | kW | kW | LOAD
6193 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.PNOMB | Nominal phase B real power demand | Float |  | kW | kW | LOAD
6194 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.PNOMC | Nominal phase C real power demand | Float |  | kW | kW | LOAD
6195 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.PRIMCONN | Composite flag (mask) | Integer |  |  |  | LOAD
6196 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.QNOMA | Nominal phase A reactive power demand | Float |  | kW | kW | LOAD
6197 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.QNOMB | Nominal phase B reactive power demand | Float |  | kW | kW | LOAD
6198 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.QNOMC | Nominal phase C reactive power demand | Float |  | kW | kW | LOAD
6199 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.STDELTAC | The load delta iteration counter | Integer |  |  |  | LOAD
6200 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.STDELTAP | The values of the schedule correction factors for power. | String |  |  |  | LOAD
6201 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.STDELTAQ | The values of the schedule correction factors for reactive power. | String |  |  |  | LOAD
6202 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.SUPPLIER | Energy supplier | Integer |  |  |  | LOAD
6203 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.TYPE | Type of the load | Integer |  |  |  | LOAD
6204 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD.WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
6205 | DNOM Component | Meter Measurement | METERMEAS |  | AMP_C | Phase C current | Float |  | Amps | Amps
6206 | DNOM Component | Meter Measurement | METERMEAS |  | DYNFEEDER | Dynamic feeder | String
6207 | DNOM Component | Meter Measurement | METERMEAS |  | DYNSTATION | Dynamic substation | String
6208 | DNOM Component | Meter Measurement | METERMEAS |  | LCOMMTIME | Last communication time | Enumeration
6209 | DNOM Component | Meter Measurement | METERMEAS | input | LOAD | Pointer to the load | String
6210 | DNOM Component | Meter Measurement | METERMEAS |  | LOADDTFID | ID of the load distribution transformer | String
6211 | DNOM Component | Meter Measurement | METERMEAS |  | LOADID | Load ID | String
6212 | DNOM Component | Meter Measurement | METERMEAS |  | LOADPROFILEENABLED | A flag indicating that the load profile is enabled | Boolean
6213 | DNOM Component | Meter Measurement | METERMEAS |  | MEASDEVTYPE | Device type of the meter | Integer
6214 | DNOM Component | Meter Measurement | METERMEAS |  | METERID | Meter ID | String
6215 | DNOM Component | Meter Measurement | METERMEAS |  | NORMSTATION | Nominal substation | String
6216 | DNOM Component | Meter Measurement | METERMEAS |  | VAR_A | Phase A reactive power | Float |  | VAR | VAR
6217 | DNOM Component | Meter Measurement | METERMEAS |  | VAR_B | Phase B reactive power | Float |  | VAR | VAR
6218 | DNOM Component | Meter Measurement | METERMEAS |  | VAR_C | Phase C reactive power | Float |  | VAR | VAR
6219 | DNOM Component | Meter Measurement | METERMEAS |  | VARA | Phase A reactive power measurement | Float |  | VAR | VAR
6220 | DNOM Component | Meter Measurement | METERMEAS |  | VARB | Phase B reactive power measurement | Float |  | VAR | VAR
6221 | DNOM Component | Meter Measurement | METERMEAS |  | VARC | Phase C reactive power measurement | Float |  | VAR | VAR
6222 | DNOM Component | Meter Measurement | METERMEAS |  | VOLT_A | Phase A voltage | Float |  | Volts | Volts
6223 | DNOM Component | Meter Measurement | METERMEAS |  | VOLT_B | Phase B voltage | Float |  | Volts | Volts
6224 | DNOM Component | Meter Measurement | METERMEAS |  | VOLT_C | Phase C voltage | Float |  | Volts | Volts
6225 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTA | Phase A voltage measurement | Float |  | Volt, p.u | Volt, p.u
6226 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTB | Phase B voltage measurement | Float |  | Volt, p.u | Volt, p.u
6227 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTC | Phase C voltage measurement | Float |  | Volt, p.u | Volt, p.u
6228 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFA | Difference between the measured and calculated voltage at phase A | Float |  | % | %
6229 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFAEX | Specifies whether the difference between the measured and calculated voltage at phase B exceed the threshold specified by the Maximum Voltage Mismatch at Load Point (%) parameter in DCE | Boolean
6230 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFB | Difference between the measured and calculated voltage at phase B | Float |  | % | %
6231 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFBEX | Specifies whether the difference between the measured and calculated voltage at phase B exceed the threshold specified by the Maximum Voltage Mismatch at Load Point (%) parameter in DCE | Boolean
6232 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFC | Difference between the measured and calculated voltage at phase C | Float |  | % | %
6233 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTDIFFCEX | Specifies whether the difference between the measured and calculated voltage at phase B exceed the threshold specified by the Maximum Voltage Mismatch at Load Point (%) parameter in DCE | Boolean
6234 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTEVENTTYPE | Voltage event type | Integer
6235 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTEXCEPTIONSTATE | Voltage exception state | String
6236 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTHIGHLIM | High voltage limit | Float
6237 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTLOADA | Phase A DPF-calculated voltage | Float |  | p.u | p.u
6238 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTLOADB | Phase B DPF-calculated voltage | Float |  | p.u | p.u
6239 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTLOADC | Phase C DPF-calculated voltage | Float |  | p.u | p.u
6240 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTLOWLIM | Low voltage limit | Float
6241 | DNOM Component | Meter Measurement | METERMEAS |  | VOLTPROFILEENABLED | A flag indicating that the voltage profile is enabled | Boolean
6242 | DNOM Component | Meter Measurement | METERMEAS |  | WATT_A | Phase A real power | Float |  | Watts | Watts
6243 | DNOM Component | Meter Measurement | METERMEAS |  | WATT_B | Phase B real power | Float |  | Watts | Watts
6244 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
6245 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
6246 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
6247 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6248 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6249 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.ENUMTYPE | Manhole Type 1 = standard, 2 = others | Integer |  |  |  | MHOLE
6250 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
6251 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.ID | ID of the object | String |  |  |  | DNMOBJ
6252 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.NAME | Object name | String |  |  |  | DNMOBJ
6253 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
6254 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.NUMOBJ | The number of objects in the manhole | Integer |  |  |  | MHOLE
6255 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE.REFDRAW | Reference Drawing | String |  |  |  | MHOLE
6256 | DNOM Component | Manhole | MHOLE | input | ADDRESS.NOAPPSTR | Address of manhole | String
6257 | DNOM Component | Meter Measurement | METERMEAS |  | WATT_C | Phase C real power | Float |  | Watts | Watts
6258 | DNOM Component | Meter Measurement | METERMEAS |  | WATTA | Phase A real power measurement | Float |  | Watt | Watt
6259 | DNOM Component | Meter Measurement | METERMEAS |  | WATTB | Phase B real power measurement | Float |  | Watt | Watt
6260 | DNOM Component | Meter Measurement | METERMEAS |  | WATTC | Phase C real power measurement | Float |  | Watt | Watt
6261 | DNOM Component Placement | Manhole Label Placement | MHLBPL | input | MANHOLE | Pointer to the associated manhole | String
6262 | DNOM Component | Manhole | MHOLE | input | ALTERNATENAME | Alternate Name | String
6263 | DNOM Component | Manhole | MHOLE | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
6264 | DNOM Component | Manhole | MHOLE | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
6265 | DNOM Component | Manhole | MHOLE | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
6266 | DNOM Component | Manhole | MHOLE | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
6267 | DNOM Component | Manhole | MHOLE | input | DNOMTABNAME | The DNOM table name | String
6268 | DNOM Component | Manhole | MHOLE | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6269 | DNOM Component | Manhole | MHOLE | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6270 | DNOM Component | Manhole | MHOLE | input | ENUMTYPE | Manhole Type. 1 = standard, 2 = others | Integer
6271 | DNOM Component | Manhole | MHOLE | input | ID | Object unique ID | String |  |  |  | DNMOBJ
6272 | DNOM Component | Manhole | MHOLE | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
6273 | DNOM Component | Manhole | MHOLE | input | NAME | Object name | String |  |  |  | DNMOBJ
6274 | DNOM Component | Manhole | MHOLE | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
6275 | DNOM Component | Manhole | MHOLE | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
6276 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
6277 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
6278 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
6279 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6280 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6281 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.ENUMTYPE | Manhole Type 1 = standard, 2 = others | Integer |  |  |  | MHOLE
6282 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
6283 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.ID | ID of the object | String |  |  |  | DNMOBJ
6284 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.NAME | Object name | String |  |  |  | DNMOBJ
6285 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
6286 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.NUMOBJ | The number of objects in the manhole | Integer |  |  |  | MHOLE
6287 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE.REFDRAW | Reference Drawing | String |  |  |  | MHOLE
6288 | DNOM Component | Manhole | MHOLE | input | NUMOBJ | The number of objects in the manhole | Integer
6289 | DNOM Component | Manhole | MHOLE | input | REFDRAW | Reference Drawing | String
6290 | DNOM Component | Manhole | MHOLE | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
6291 | DNOM Component | Manhole | MHOLE | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
6292 | DNOM Component Placement | Manhole Placement | MHPLE | input | MANHOLE | Pointer to the associated manhole | String
6293 | DNOM Component | Non Application String | NDPFST |  | NOAPPSTR | Non DPF/NTP application string. Includes the address, second switch identifier, and other string attributes not needed for the NTP or DPF applications. | String
6294 | DNOM Component | Node | NODE |  | BUSID | ID of the bus | String
6295 | DNOM Component | Node | NODE |  | BUSNAME | Name of the bus | String
6296 | DNOM Component | Node | NODE |  | BUSVLIMHIGHEMERG | Emergency high voltage limit | Float
6297 | DNOM Component | Node | NODE |  | BUSVLIMHIGHNORM | Normal high voltage limit | Float
6298 | DNOM Component | Node | NODE |  | BUSVLIMLOWEMERG | Emergency low voltage limit | Float
6299 | DNOM Component | Node | NODE |  | BUSVLIMLOWNORM | Normal low voltage limit | Float
6300 | DNOM Component | Node | NODE |  | BUSVOPTEMRGHIGH | Emergency optimization high limit | Float
6301 | DNOM Component | Node | NODE |  | BUSVOPTEMRGLOW | Emergency optimization low limit | Float
6302 | DNOM Component | Node | NODE |  | BUSVOPTNORMHIGH | Normal optimization high limit | Float
6303 | DNOM Component | Node | NODE |  | BUSVOPTNORMLOW | Normal optimization low limit | Float
6304 | DNOM Component | Node | NODE |  | COMPPHASEA | Flag indicating whether phase A exists in the component | Boolean
6305 | DNOM Component | Node | NODE |  | COMPPHASEB | Flag indicating whether phase B exists in the component | Boolean
6306 | DNOM Component | Node | NODE |  | COMPPHASEC | Flag indicating whether phase C exists in the component | Boolean
6307 | DNOM Component | Node | NODE |  | COMPPHASEN | Indicates whether neutral is connected | Boolean
6308 | DNOM Component | Node | NODE | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6309 | DNOM Component | Node | NODE | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6310 | DNOM Component | Node | NODE | input | DYNFEEDERNAME | Dynamic (currently energizing) feeder name. | String
6311 | DNOM Component | Node | NODE | input | SWSECT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
6312 | DNOM Component | Node | NODE | input | SWSECT.BRCHLIMA | ID of branch with the lowest phase A limit | String |  |  |  | SWSECT
6313 | DNOM Component | Node | NODE | input | SWSECT.BRCHLIMB | ID of branch with the lowest phase B limit | String |  |  |  | SWSECT
6314 | DNOM Component | Node | NODE | input | SWSECT.BRCHLIMC | ID of branch with the lowest phase C limit | String |  |  |  | SWSECT
6315 | DNOM Component | Node | NODE | input | SWSECT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
6316 | DNOM Component | Node | NODE | input | SWSECT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
6317 | DNOM Component | Node | NODE | input | SWSECT.ID | Object unique ID | String |  |  |  | DNMOBJ
6318 | DNOM Component | Node | NODE | input | SWSECT.LOWLIMA | Lowest phase A branch flow limit value | Float |  | Amps | Amps | SWSECT
6319 | DNOM Component | Node | NODE | input | SWSECT.LOWLIMB | Lowest phase B branch flow limit value | Float |  | Amps | Amps | SWSECT
6320 | DNOM Component | Node | NODE | input | SWSECT.LOWLIMC | Lowest phase C branch flow limit value | Float |  | Amps | Amps | SWSECT
6321 | DNOM Component | Node | NODE | input | SWSECT.NAME | Object name | String |  |  |  | DNMOBJ
6322 | DNOM Component | Node | NODE | input | SWSECT.NTPFLAG | NTP flags(e.g. 1 = section is fully energized, 2 = partially energized, 4 = one or more temp grounds) | Integer |  |  |  | SWSECT
6323 | DNOM Component | Node | NODE | input | SWSECT.NUMCRCST | Number of critical customers. | Integer |  |  |  | SWSECT
6324 | DNOM Component | Node | NODE | input | SWSECT.NUMCUST3 | Number of three-phase customers | Integer |  |  |  | SWSECT
6325 | DNOM Component | Node | NODE | input | SWSECT.NUMCUSTA | Number of phase A customers | Integer |  |  |  | SWSECT
6326 | DNOM Component | Node | NODE | input | SWSECT.NUMCUSTB | Number of phase B customers | Integer |  |  |  | SWSECT
6327 | DNOM Component | Node | NODE | input | SWSECT.NUMCUSTC | Number of phase C customers | Integer |  |  |  | SWSECT
6328 | DNOM Component | Node | NODE | input | SWSECT.NUMTF3 | Number of three-phase distribution transformers | Integer |  |  |  | SWSECT
6329 | DNOM Component | Node | NODE | input | SWSECT.NUMTFA | Number of phase A distribution transformers | Integer |  |  |  | SWSECT
6330 | DNOM Component | Node | NODE | input | SWSECT.NUMTFB | Number of phase B distribution transformers | Integer |  |  |  | SWSECT
6331 | DNOM Component | Node | NODE | input | SWSECT.NUMTFC | Number of phase C distribution transformers | Integer |  |  |  | SWSECT
6332 | DNOM Component | Node | NODE | input | ID | Object unique ID | String |  |  |  | DNMOBJ
6333 | DNOM Component | Node | NODE | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
6334 | DNOM Component | Node | NODE | input | NAME | Object name | String |  |  |  | DNMOBJ
6335 | DNOM Component | Node | NODE |  | NODEENERGIZED | Phases that are energized | String
6336 | DNOM Component | Node | NODE |  | BRANCHDEENERGIZED | Phases that are de-energized | String
6337 | DNOM Component | Node | NODE | input | SWSECT | Pointer to the associated switchable section | String
6338 | DNOM Component | Node | NODE | input | VLTLEVEL.NOMVOLT | Voltage level (line to neutral) | Integer |  |  |  | VOLTLV
6339 | DNOM Component | Node | NODE |  | VANGLEA | Voltage angle of phase A | Integer |  | Radians | Radians
6340 | DNOM Component | Node | NODE |  | VANGLEB | Voltage angle of phase B | Integer |  | Radians | Radians
6341 | DNOM Component | Node | NODE |  | VANGLEC | Voltage angle of phase B | Integer |  | Radians | Radians
6342 | DNOM Component | Node | NODE |  | VANGLEN | Voltage angle of neutral | Integer |  | Radians | Radians
6343 | DNOM Component | Node | NODE | input | VLTLEVEL | Pointer to the voltage level determined in the converter | String
6344 | DNOM Component | Node | NODE |  | VMAGA | Voltage magnitude of phase A | Integer |  | p.u. | p.u.
6345 | DNOM Component | Node | NODE |  | VMAGB | Voltage magnitude of phase B | Integer |  | p.u. | p.u.
6346 | DNOM Component | Node | NODE |  | VMAGC | Voltage magnitude of phase B | Integer |  | p.u. | p.u.
6347 | DNOM Component | Node | NODE |  | VMAGN | Voltage magnitude of neutral | Integer |  | p.u. | p.u.
6348 | DNOM Component | Node | NODE |  | VMEASACTUALPHA | SCADA measured voltage of phase A | String
6349 | DNOM Component | Node | NODE |  | VMEASACTUALPHB | SCADA measured voltage of phase B | String
6350 | DNOM Component | Node | NODE |  | VMEASACTUALPHC | SCADA measured voltage of phase C | String
6351 | DNOM Component | Node | NODE |  | VMEASPHA | Measured voltage of phase A | Float |  | V or kV | V or kV
6352 | DNOM Component | Node | NODE |  | VMEASPHANGLEA | SCADA measured voltage angle of phase A | Float |  | Deg | Deg
6353 | DNOM Component | Node | NODE |  | VMEASPHANGLEB | SCADA measured voltage angle of phase B | Float |  | Deg | Deg
6354 | DNOM Component | Node | NODE |  | VMEASPHANGLEC | SCADA measured voltage angle of phase C | Float |  | Deg | Deg
6355 | DNOM Component | Node | NODE |  | VMEASPHB | Measured voltage of phase B | Float |  | V or kV | V or kV
6356 | DNOM Component | Node | NODE |  | VMEASPHC | Measured voltage of phase C | Float |  | V or kV | V or kV
6357 | DNOM Component | Node | NODE |  | VOLTANDANGLEANA | Connection node calculated voltage and angle of phase A (for Analyst pop-up) | Float |  | kV | kV
6358 | DNOM Component | Node | NODE |  | VOLTANDANGLEANALG | Phase A LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
6359 | DNOM Component | Node | NODE |  | VOLTANDANGLEANALL | Phase A LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
6360 | DNOM Component | Node | NODE |  | VOLTANDANGLEANB | Connection node calculated voltage and angle of phase B (for Analyst pop-up) | Float |  | kV | kV
6361 | DNOM Component | Node | NODE |  | VOLTANDANGLEANBLG | Phase B LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
6362 | DNOM Component | Node | NODE |  | VOLTANDANGLEANBLL | Phase B LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
6363 | DNOM Component | Node | NODE |  | VOLTANDANGLEANC | Connection node calculated voltage and angle of phase C (for Analyst pop-up) | Float |  | kV | kV
6364 | DNOM Component | Node | NODE |  | VOLTANDANGLEANCLG | Phase C LG voltage (magnitude on configurable voltage base and angle in degrees). | Float
6365 | DNOM Component | Node | NODE |  | VOLTANDANGLEANCLL | Phase C LL voltage (magnitude on configurable voltage base and angle in degrees). | Float
6366 | DNOM Component | Node | NODE |  | VOLTANDANGLEOPA | Connection node calculated voltage and angle of phase A (for Operator pop-up) | Float |  | kV | kV
6367 | DNOM Component | Node | NODE |  | VOLTANDANGLEOPB | Connection node calculated voltage and angle of phase B (for Operator pop-up) | Float |  | kV | kV
6368 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | ADDRESS.NOAPPSTR | Address | String |  |  |  | NDPFST
6369 | DNOM Component | Node | NODE |  | VOLTANDANGLEOPC | Connection node calculated voltage and angle of phase C (for Operator pop-up) | Float |  | kV | kV
6370 | DNOM Component | Node | NODE |  | VOLTCALC | Node mask | Integer
6371 | DNOM Component | Node | NODE | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
6372 | DNOM Component | Node | NODE | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
6373 |  | Node | NODE | input | FDRBOUNDARYNODE | Indicates whether this is a feeder boundary point | Boolean
6374 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | ADDRESS | Address | String |  |  |  | NDPFST
6375 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | ALTERNATENAME | Alternate name | String
6376 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary. | Boolean |  | #N/A | #N/A
6377 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | EXSBNAME | External substation name. | String |  | #N/A | #N/A
6378 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String
6379 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer
6380 | DNOM Group Object | Non Electrical | NONELECTRICAL | input | NONELECTSTATNAME | Station name | String
6381 | DNOM Component | Non-Simalated Measurement | NSMEAS | input | AREAIND | Integer (index) into station permission area list | Integer
6382 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | DATASOURCEFEED | SCADA datasource feed. 0 = Telemetered (coming from RTU) 1 = Manual (Local) | Integer
6383 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | DEFQUALITY | Default quality | Integer
6384 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | DEFVALUE | Analog measurement default value | Integer
6385 | DNOM Component | Non-Simalated Measurement | NSMEAS | input | ID | Object unique ID | String
6386 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | ISANALOG | Flag indicating whether the measurement is an analog or a status measurement (true = analog, false = status) | Boolean
6387 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | MBITMASK | Bitmask field for measurements. (bit 0 - normal status value, 1 - current status value, 2 - last status value, 3 - invert value, 4 - BLA obtained, 5 - DDNOM multi state measurement, the combination of SDIS and XDIS is hard coded, 6 - scada multi state measurement, the combination with XDIS = true is defined in config file, 7 - not used now, 8 - has effective device set, 9 - extended current status value, 10 - extended last status value, 11 - extended invert value, 12 - extended BLA obtained, 13 - multi state false value 01, 14 - multi state false value 11, 15 - Not used now, 16 - multichange normal status value, 17 - multichange current status value, 18 - multichange last status value, 19 - multichange invert value, 20 - multi state True value 01, 21 - multi state True value 11, 23 - Meas DNAF flag, 24 - Possible interface voltage measurement, 25 - analogue and status measurement initialized, 26 - Not used now, 27 - Indicates this is a Group Multi-Phase Measurement for a device that has individual phase measurements for the same function. | Integer
6388 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | MEASCLAS | Measurement classification (analog, status, set point, or control point) | Integer
6389 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | OPERATETIME | Measurement operate time | Integer
6390 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | QUALITY | Masked measurement quality | Integer
6391 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | RVALUE | Analog measurement value | Float
6392 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | SIMONLY | A flag indicating a simulated measurement (always true) | Boolean
6393 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | SITENAME | Name of the site | String
6394 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | TIMEOUT | Measurement timeout | Integer
6395 | DNOM Component | Non-Simalated Measurement | NSMEAS |  | WAITTIME | Measurement wait time | Integer
6396 | DNAF Object | Objective Function | OBJFNT |  | ACTIVEOPERATIONMODE | Specifies the ID of the operation mode that is used for the current problem formulation. This allows each problem formulation to have its own defined plan execution parameters. | Integer
6397 | DNAF Object | Objective Function | OBJFNT |  | ALLOWSEC | A flag indicating that plans that have violations are allowed | Boolean
6398 | DNAF Object | Objective Function | OBJFNT |  | APPLITYPE | Bitmask for the application type | Integer
6399 | DNAF Object | Objective Function | OBJFNT |  | DEFAULTVRAMOUNT | Specifies the default voltage reduction target in percentage for the Fixed Regulation LVM. | Float
6400 | DNAF Object | Objective Function | OBJFNT |  | DELTAVOLTHIGHAPPLIMITENFORCE | Application limit enforcement percentage for delta high voltage | Integer
6401 | DNAF Object | Objective Function | OBJFNT |  | DELTAVOLTHIGHPREVENTCLOSEDLOOP | Prevent closed loop execution percentage for delta high voltage | Integer
6402 | DNAF Object | Objective Function | OBJFNT |  | DELTAVOLTLOWAPPLIMITENFORCE | Application limit enforcement percentage for delta low voltage | Integer
6403 | DNAF Object | Objective Function | OBJFNT |  | DELTAVOLTLOWPREVENTCLOSEDLOOP | Prevent closed loop execution percentage for delta low voltage | Integer
6404 | DNAF Object | Objective Function | OBJFNT |  | DESCRIPT | Description | String
6405 | DNAF Object | Objective Function | OBJFNT |  | DISABLEVOLTAGERAILS | Specifies whether capacitor voltage rails are disabled | Boolean
6406 | DNAF Object | Objective Function | OBJFNT |  | DISCARDVMEASLOAD | Specifies whether the LVM solution discards a load voltage measurement if the deviation between the measurement and the DPF calculated value exceeds the tolerance set on the DPF page using the Maximum Voltage Mismatch at Load Point parameter. | Boolean
6407 | DNAF Object | Objective Function | OBJFNT |  | ELIGIBLESWITCHDEVICETYPE | Eligible Switching Device (0: Automatic Only, 1: Manual Only, 2: Automatic and Manual) | Integer
6408 | DNAF Object | Objective Function | OBJFNT |  | FIXEDVRTYPE | If set to 0, the fixed voltage reduction is enabled and the voltage reduction target specified in the VRAMOUNT field is applied. If set to 1, the fixed voltage reduction is disabled and the voltage reduction target specified in the DEFAULTVRAMOUNT field is applied. | Integer
6409 | DNAF Object | Objective Function | OBJFNT |  | FLOWAPPLIMITENFORCE | Application limit enforcement percentage for flow | Integer
6410 | DNAF Object | Objective Function | OBJFNT |  | FLOWLIM | Respect all flow (Amps, kW) violations flag | Enumeration
6411 | DNAF Object | Objective Function | OBJFNT |  | FLOWPREVENTCLOSEDLOOP | Prevent closed loop execution percentage for flow | Integer
6412 | DNAF Object | Objective Function | OBJFNT |  | HEULVMLOWVOLLIM | Lower limit for heuristic LVM | Integer
6413 | DNAF Object | Objective Function | OBJFNT |  | HEULVMUPPERVOLLIM | Upper limit for heuristic LVM | Integer
6414 | DNAF Object | Objective Function | OBJFNT |  | ISRECONFIGPROBFORM | A flag indicating a reconfigurable application (FISR, AFR, FISRCA, and PLOS) problem formulation | Boolean
6415 | DNAF Object | Objective Function | OBJFNT |  | ISVVCPROBFORM | A flag indicating a LVM problem formulation | Boolean
6416 | DNAF Object | Objective Function | OBJFNT |  | LDDROPFN | Switching rule for allowing dropped loads in the final configuration (final) | Integer
6417 | DNAF Object | Objective Function | OBJFNT |  | LDDROPTP | Switching rule for allowing dropped loads in the final configuration (intermediate) | Integer
6418 | DNAF Object | Objective Function | OBJFNT |  | LOOPFN | Switching rule for allowing loops in the final configuration (final) | Integer
6419 | DNAF Object | Objective Function | OBJFNT |  | LOOPTP | Switching rule for allowing loops in the intermediate configurations (intermediate) | Integer
6420 | DNAF Object | Objective Function | OBJFNT |  | LVMAREAREACTIVESUPPORT | Flag for power factor support for LVM | Boolean
6421 | DNAF Object | Objective Function | OBJFNT |  | LVMDEMANDREDUCTION | Flag for demand reduction target for LVM | Boolean
6422 | DNAF Object | Objective Function | OBJFNT |  | LVMEXPPF1 | Exponential scaling of power factor weight. Weight = PF1 * exp (PF1) | Integer
6423 | DNAF Object | Objective Function | OBJFNT |  | LVMEXPPF2 | Exponential scaling of power factor weight. Weight = PF2 * exp (PF2) | Integer
6424 | DNAF Object | Objective Function | OBJFNT |  | LVMEXPVF1 | Exponential scaling of voltage flattening weight. weight = VF1 * exp (VF1) | Integer
6425 | DNAF Object | Objective Function | OBJFNT |  | LVMEXPVF2 | Exponential scaling of voltage flattening weight. weight = VF2 * exp (VF2) | Integer
6426 | DNAF Object | Objective Function | OBJFNT |  | LVMLOSSREDUCTION | Flag for loss reduction for LVM | Boolean
6427 | DNAF Object | Objective Function | OBJFNT |  | LVMREDUCEVIOLATION | Flag for reduce violation target for LVM | Boolean
6428 | DNAF Object | Objective Function | OBJFNT |  | LVMSOLUTION | LVM solution type (0 - Optimization based LVM, 1 - Heuristic LVM, 2 - Fixed Regulation LVM) | Integer
6429 | DNAF Object | Objective Function | OBJFNT |  | MAXDELTAVOL | Maximum percent difference between LVM calculated deltaV and deltaV from the controller (SCADA analog) | Integer
6430 | DNAF Object | Objective Function | OBJFNT |  | MAXSWCTR | The maximum number of switchings for a control (e.g., 2 means that a device could be opened and closed once within a plan) | Integer
6431 | DNAF Object | Objective Function | OBJFNT |  | MAXSWPLN | Maximum number of switchings per plan | Integer
6432 | DNAF Object | Objective Function | OBJFNT |  | MINPOWERFACTOR | Effective lower limit for voltage flattening when using power factor control objective | Integer
6433 | DNAF Object | Objective Function | OBJFNT |  | OBJNUMB | Unique objective function number. Used in schedule representation. | Integer
6434 | DNAF Object | Objective Function | OBJFNT |  | PERFCMI | Performance index for CMI | Integer
6435 | DNAF Object | Objective Function | OBJFNT |  | PERFCTFN | Performance index for control cost (final) | Integer
6436 | DNAF Object | Objective Function | OBJFNT |  | PERFCTTP | Performance index for control cost (intermediate) | Integer
6437 | DNAF Object | Objective Function | OBJFNT |  | PERFDRFN | Performance index for dropped customer count (final) | Integer
6438 | DNAF Object | Objective Function | OBJFNT |  | PERFDRTP | Performance index for dropped customer count (intermediate) | Integer
6439 | DNAF Object | Objective Function | OBJFNT |  | PERFFLFN | Performance index for ampacity limit violations (final) | Integer
6440 | DNAF Object | Objective Function | OBJFNT |  | PERFFLTP | Performance index for ampacity limit violations (intermediate) | Integer
6441 | DNAF Object | Objective Function | OBJFNT |  | PERFFVDR | Performance index for feeder voltage drop | Integer
6442 | DNAF Object | Objective Function | OBJFNT |  | PERFINDVOLTLOADFINAL | Performance index for load voltage limit violations (final) | Integer
6443 | DNAF Object | Objective Function | OBJFNT |  | PERFINDVOLTLOADTEMP | Performance index for load voltage limit violations (intermediate) | Integer
6444 | DNAF Object | Objective Function | OBJFNT |  | PERFLDFN | Performance index for lost load in kW (final) | Integer
6445 | DNAF Object | Objective Function | OBJFNT |  | PERFLDTP | Performance index for lost load in kW (intermediate) | Integer
6446 | DNAF Object | Objective Function | OBJFNT |  | PERFLMI | Performance index for LMI | Integer
6447 | DNAF Object | Objective Function | OBJFNT |  | PERFLOSS | Performance index for losses in kW (final only) | Integer
6448 | DNAF Object | Objective Function | OBJFNT |  | PERFMARG | Performance index for ampacity margin (final only) | Integer
6449 | DNAF Object | Objective Function | OBJFNT |  | PERFMAXSEGMENT | Performance Index for maximum segment load | Integer
6450 | DNAF Object | Objective Function | OBJFNT |  | PERFMOVE | Performance index for total number of control moves (final only) | Integer
6451 | DNAF Object | Objective Function | OBJFNT |  | PERFMOVETHIRD | Performance index for total number of control moves involving third-party equipment (final only) | Integer
6452 | DNAF Object | Objective Function | OBJFNT |  | PERFMXTR | Performance index for equalization of critical voltages maximize tap ranges | Integer
6453 | DNAF Object | Objective Function | OBJFNT |  | PERFPRIORITYCMI | Performance index for Priority CMI | Integer
6454 | DNAF Object | Objective Function | OBJFNT |  | PERFRADFN | Performance index for maintaining a radial configuration (final) | Integer
6455 | DNAF Object | Objective Function | OBJFNT |  | PERFRADTP | Performance index for maintaining a radial configuration (intermediate) | Integer
6456 | DNAF Object | Objective Function | OBJFNT |  | PERFRPRT | Performance index for the execution of the fault analysis function (for the top-ranked plans) | Integer
6457 | DNAF Object | Objective Function | OBJFNT |  | PERFVOLTIMBAL | Performance Index for voltage imbalance | Integer
6458 | DNAF Object | Objective Function | OBJFNT |  | PERFVTFN | Performance index for bus voltage limit violations (final) | Integer
6459 | DNAF Object | Objective Function | OBJFNT |  | PERFVTTP | Performance index for bus voltage limit violations (intermediate) | Integer
6460 | DNAF Object | Objective Function | OBJFNT |  | POWFACTORWEIGHT | Relative weight to be given to power factor | Integer
6461 | DNAF Object | Objective Function | OBJFNT |  | PRFDRPRF | Performance index for load drop groups - not implemented (final) | Integer
6462 | DNAF Object | Objective Function | OBJFNT |  | PRFDRPRT | Performance index for load drop groups - not implemented (intermediate) | Integer
6463 | DNAF Object | Objective Function | OBJFNT |  | PRFMAIFI | Performance index for MAIFI (Final) | Integer
6464 | DNAF Object | Objective Function | OBJFNT |  | PRFSAIDI | Performance index for SAIDI (Final) | Integer
6465 | DNAF Object | Objective Function | OBJFNT |  | PRFSAIFI | Performance index for SAIFI (Final) | Integer
6466 | DNAF Object | Objective Function | OBJFNT |  | SWITCHINGSOLUTION | Switching Application Solution method (0: Tree, 1: Turbo) | Enumeration
6467 | DNAF Object | Objective Function | OBJFNT |  | USEGEN | A flag indicating that generators should be used | Boolean
6468 | DNAF Object | Objective Function | OBJFNT |  | USESHUNT | A flag indicating that shunts should be used | Boolean |  | Commented out
6469 | DNAF Object | Objective Function | OBJFNT |  | USESWIT | A flag indicating that switches should be used | Boolean
6470 | DNAF Object | Objective Function | OBJFNT |  | USETFTAP | A flag indicating that transformer tap changers should be used | Boolean |  | Commented out
6471 | DNAF Object | Objective Function | OBJFNT |  | VOLFLATLIM | The global voltage flattening limit | Integer
6472 | DNAF Object | Objective Function | OBJFNT |  | VOLFLATWEIGHT | Relative weight to be given to voltage flattening | Integer
6473 | DNAF Object | Objective Function | OBJFNT |  | VOLREGMARG | The global voltage regulation margin | Integer
6474 | DNAF Object | Objective Function | OBJFNT |  | VOLTAGEREDUCTIONWEIGHT | Voltage Reduction Weight, used for Heuristic LVM | Integer
6475 | DNAF Object | Objective Function | OBJFNT |  | VOLTLIM | Respect all voltage violations flag | Enumeration
6476 | DNAF Object | Objective Function | OBJFNT |  | VOLTLIMSTRATEGYMODE | Voltage Limit Strategy Mode (0: Operational Normal, 1: Operational Emergency, 2: Optimization Normal, 3: Optimization Emergency) | Integer
6477 | DNAF Object | Objective Function | OBJFNT |  | VOLTLIMSTRATEGYMONITORBUS | Flag for voltage limit monitor bus | Boolean
6478 | DNAF Object | Objective Function | OBJFNT |  | VOLTLIMSTRATEGYMONITORLOAD | Flag for voltage limit monitor load | Boolean
6479 | DNAF Object | Objective Function | OBJFNT |  | VRAMOUNT | Specifies the current voltage reduction target in percentage for the Fixed Regulation LVM. | Float
6480 | DNOM Component | Overcurrent Protection | OCPROT |  | CURRSETTING | Number of current setting index | Integer
6481 | DNOM Component | Overcurrent Protection | OCPROT |  | DEFGRNDTRIP | A flag indicating that the protective ground trip is enabled | Boolean
6482 | DNOM Component | Overcurrent Protection | OCPROT |  | DEFSETTING | Number of protection setting index | Integer
6483 | DNOM Component | Overcurrent Protection | OCPROT |  | GRNDTRIPCAP | A flag indicating that the protection is ground trip capable | Boolean
6484 | DNOM Component | Overcurrent Protection | OCPROT |  | LARGESTFUSE | Largest coordination fuse rating | Float
6485 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSETTINGS.GROUNDTRIP | Ground trip current | Float |  |  |  | PROTSET
6486 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSETTINGS.PHASETRIP | Phase trip current ( used if the setting is selected by phase trip level) | Float |  |  |  | PROTSET
6487 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSETTINGS.SCADAINDEX | Index of the applicable SCADA measurement type (for control, enabling, setting, etc.). Can be 0-8, where 0 - unmapped) | Integer |  |  |  | PROTSET
6488 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSETTINGS.SETTING | Name of the setting (e.g. S1) | String |  |  |  | PROTSET
6489 | DNOM Component | Overcurrent Protection | OCPROT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
6490 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSOURCES.SETTING | Name of the setting (e.g. S1) | String |  |  |  | PROTSET
6491 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSOURCES.SOURCESUB | Supply substation - used if setting is selected by source substation | String |  |  |  | PROTSET
6492 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTSOURCESS.SOURCEFEEDER | Supply feeder - used if setting is selected by source feeder | String |  |  |  | PROTSET
6493 | DNOM Component | Overcurrent Protection | OCPROT | output | NEUCURRATING | The relay neutral current setting in Amps | Float | DPF | Amps | Amps
6494 | DNOM Component | Overcurrent Protection | OCPROT | output | NEUCURRELAY | Specifies whether the neutral current relay setting exists | Boolean | DPF
6495 | DNOM Component | Overcurrent Protection | OCPROT |  | NOTE | Notes | String
6496 | DNOM Component | Overcurrent Protection | OCPROT |  | NUMPROTSETTING | Number of protection settings populated | Integer
6497 | DNOM Component | Overcurrent Protection | OCPROT |  | NUMPROTSOURCES | Number of protection sources populated | Integer
6498 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTDATA | Protection data source | Enumeration
6499 | DNOM Component | Overcurrent Protection | OCPROT | input | PROTSETTINGS | Pointer to the protection settings populated | String
6500 | DNOM Component | Overcurrent Protection | OCPROT | input | PROTSOURCES | Pointer to the protection sources populated | String
6501 | DNOM Component | Overcurrent Protection | OCPROT |  | PROTTYPE | Protection device type | Enumeration
6502 | DNOM Component | Overcurrent Protection | OCPROT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
6503 | DNOM Component | Overcurrent Protection | OCPROT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
6504 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | ACTIVESETTINGGROUP | Name of the currently active protection settings group | String
6505 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | CONTROLTYPE | Type of control (Not Identified, Open/Close, Open/Close, Raise/Lower, Voltage Setpoint, Voltage Reduction Setpoint, Voltage Reduction Status, Setting Group, VAR Output, Power Factor Output, VAR Output, Power Factor Output, WATT Output, Connection Status Output, Curve Output) | String
6506 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICECONTROLTYPE | Device control type | String
6507 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | DEVICEGEOM | Name of the geometry that is associated with the device | String
6508 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICEID | Device ID | Integer
6509 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICEINDEX | Vector index of device | Integer
6510 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICENAME | Name of control device | String
6511 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICENETTYPE | Device type | Integer
6512 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICEPHASING | Phasing of device | Integer
6513 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | DEVICESWSECT | Switchable section ID | String
6514 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICETYPE | Type of the device included in the optimization step | String
6515 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | DEVICETYPEMAP | Device type map | String
6516 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | FINAL | Flag indicating that the final move. If true, this is a final move in the plan for this control, and there are no subsequent moves of the same control in this plan. | Boolean
6517 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | ISDEVICECONTROLLABLE | A flag indicating that the device can be automatically controlled | Boolean
6518 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | ISSWTCONTROLLABLE | A flag indicating that the switch can be automatically controlled | Boolean
6519 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | ISVVCMOVE | A flag indicating that the optimization step is associated with the LVM application | Boolean
6520 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | LVMEXEMODE | LVM execution mode. Can be closed loop or advisory. | String
6521 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MAX
6522 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MAXLOADCURRENT | The maximum load current, in Amps | Float |  | Amps | Amps
6523 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MAXLOADSAFETYFACTOR | The maximum load current multiplied by the peak load safety factor, in Amps | Float |  | Amps | Amps
6524 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MIN
6525 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MINPHASECURRENT | The minimum phase fault current, in Amps | Float |  | Amps | Amps
6526 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MINGROUNDCURRENT | The minimum ground fault current, in Amps | Float |  | Amps | Amps
6527 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MINPHASECURRENTPHASE | The minimum phase fault type that is simulated in the PRV application that is executed in the scope of a reconfiguration application to determine the minimum phase fault current. For example, a line-to-line fault between phases A and B is displayed as “AB”. | String
6528 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MINGROUNDCURRENTPHASE | The minimum ground fault type.The minimum ground fault type that is simulated in the PRV application that is executed in the scope of a reconfiguration application to determine the minimum ground fault current. For example, a single line-to-ground fault between phase A and ground is displayed as “AG”. | String
6529 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | MOVEDEVICEFDRMAIN | A flag indicating that the optimization device is on the feeder backbone | Boolean
6530 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | MOVEDEVICESGTEMPLATE | The name of the associated settings group template for the plan step device | String
6531 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | MOVEXECSTATUS | Execution status for the plan step | String
6532 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | MOVEXECSTATUSCODE | Optimization control move FSD execution status code (None = 0, NotTested = 1, InProgress = 2, TestedNotFaulty =3, FaultIdentified = 4, NotEligible = 5) | Integer
6533 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | MOVEXECTIMEEND | Execution end time for the plan step | DateTime
6534 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | output | MOVEXECTIMESTART | Execution start time for the plan step | DateTime
6535 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | NEWPHASETRIP | The new phase trip current, in Amps | Float |  | Amps | Amps
6536 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | NEWGROUNDTRIP | The new ground trip current, in Amps | Float |  | Amps | Amps
6537 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | NEXTINDEX | Index of the previous "ShowUser" move of this control in the plan. If null, this is the first move. | Enumeration
6538 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | NORMALSETTINGGROUP | Name of the nominal protection settings group | String
6539 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OBJFUNCID | Objective function ID. Used for the LVM pre-implementation plan check. | Integer
6540 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OLDPHASETRIP | The previously applied phase trip current, in Amps | Float |  | Amps | Amps
6541 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OLDGROUNDTRIP | The previously applied ground trip current, in Amps | Float |  | Amps | Amps
6542 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTDEVNAME | Name of the device included in the optimization step | String
6543 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVADDR | Address of the optimization step | String
6544 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVDEVALTID | Alternate ID of the device | String
6545 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVDEVID | ID of the device included in the optimization step | String
6546 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVDEVIDORSUBNAME | ID or substation name of the device included in the optimization step | String
6547 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVENUMIMPACTSTATECHANGEDDEVICE | The number of switching devices with state change before and after the solution which impacting this control move. | String
6548 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVSECTIONDESC | Description of the involved restoration section information. | String
6549 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVEDEVISTHIRDPARTY | Specifies whether the devide included in the optimization step is owned by a third-party company | Boolean
6550 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVDEVNAME | Name of the device included in the optimization step | String
6551 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVDEVPHASE | Phases of the device included in the optimization step | String
6552 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVFEEDERNAME | Name of the feeder the device included in the optimization step belongs to | String
6553 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVFINALVALUE | Optimization step final value | String
6554 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVFINALVAR | Final VAR injection | String |  | kVAR | kVAR
6555 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVINITVALUE | Optimization step initial value | String
6556 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVINITVAR | Initial VAR injection | String |  | kVAR | kVAR
6557 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVLOADEFFECT | Load effect | String
6558 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVLOADEFFECTAMPA | Load effect Amps phase A | String
6559 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVLOADEFFECTAMPB | Load effect Amps phase B | String
6560 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVLOADEFFECTAMPC | Load effect Amps phase C | String
6561 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVOPERATION | Optimization step operation | String
6562 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN._KEY | The unique identifier to represent a device | String |  |  |  | OPTCONTROLPLAN
6563 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAFINALPF | Final area power factor after plan | Float |  |  |  | OPTCONTROLPLAN
6564 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAFINALREACTIVEDEMAND | Final (post plan) station reactive power demand | Float |  |  |  | OPTCONTROLPLAN
6565 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAFINALREALDEMAND | Final (post plan) station real power demand | Float |  |  |  | OPTCONTROLPLAN
6566 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAINITPF | Initial area power factor before plan | Float |  |  |  | OPTCONTROLPLAN
6567 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAINITREACTIVEDEMAND | Initial station reactive power demand | Integer |  |  |  | OPTCONTROLPLAN
6568 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.AREAINITREALDEMAND | Initial station real power demand | Integer |  |  |  | OPTCONTROLPLAN
6569 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CHANGEINREACTIVEDEMAND | Total change in reactive power demand | Integer |  | kVAR | kVAR | OPTCONTROLPLAN
6570 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CHANGEINREALDEMAND | Total change in real power demand | Integer |  | kW | kW | OPTCONTROLPLAN
6571 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) | Integer |  |  |  | OPTCONTROLPLAN
6572 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.COMMENT | Operator comment | String |  |  |  | OPTCONTROLPLAN
6573 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.COSTPI | Weight of the final step total cost performance index | Integer |  |  |  | OPTCONTROLPLAN
6574 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.COSTTEMPPI | Weight of the intermediate step total cost performance index | Integer |  |  |  | OPTCONTROLPLAN
6575 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CRITVOLT | Equalization of critical voltages (maximize TCUL tap range) | Integer |  |  |  | OPTCONTROLPLAN
6576 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CTVUSPRE | Value of uninterrupted service before the plan execution | Integer |  |  |  | OPTCONTROLPLAN
6577 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.CUSTVUS | Customer economic loss of value of uninterrupted service | Integer |  |  |  | OPTCONTROLPLAN
6578 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DNAFDCEVERSION | DCE parameters version | String |  |  |  | OPTCONTROLPLAN
6579 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DNAFLASTMODIFIED | DCE parameters' last modified date | String |  |  |  | OPTCONTROLPLAN
6580 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DNAFREVISIONNUM | DCE parameter revision number | String |  |  |  | OPTCONTROLPLAN
6581 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DROPPEDCUSTOMERCOUNTPI | Weight of the final step count of the dropped customers performance index | Integer |  |  |  | OPTCONTROLPLAN
6582 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DROPPEDCUSTOMERCOUNTTEMPPI | Weight of the intermediate step count of the dropped customers performance index | Integer |  |  |  | OPTCONTROLPLAN
6583 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DROPPEDPRIORITYPI | Weight of the final step dropped customer priority performance index | Integer |  |  |  | OPTCONTROLPLAN
6584 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DROPPEDPRIORITYTEMPPI | Weight of the intermediate step dropped customer priority performance index | Integer |  |  |  | OPTCONTROLPLAN
6585 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.DSOPLANSTATE | A string indicating the state of the control plan. 1.Bad 2.Good 3.Good-Neighbouring Violation 4.Good-Violation 5.Bad (LP_infeasible) 6.Bad (Power flow_Unsolved) 7. Request Stopped 8.Suspect 9.Invalid-Topology has Changed 10.Violation Detected-LVM Correction Available 11.Violation Detected-LVM Correction Not Available | String |  |  |  | OPTCONTROLPLAN
6586 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FAULTCOMP | Associated fault device ID | String |  |  |  | OPTCONTROLPLAN
6587 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FEEDERFINALPF | Final power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
6588 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FEEDERINITPF | Initial power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
6589 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FEEDERTARGETPF | Target power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
6590 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FINALACTIVELOSS | Final (post plan) real power losses | Integer |  |  |  | OPTCONTROLPLAN
6591 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FINALPFWITHINLIMIT | A flag indicating that the final (post plan) DPF was within the limit | Boolean |  |  |  | OPTCONTROLPLAN
6592 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FINALREACTIVELOSS | Final (post plan) reactive power losses | Integer |  |  |  | OPTCONTROLPLAN
6593 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FINALVOLTPI | Final (post plan) voltage performance index | Integer |  |  |  | OPTCONTROLPLAN
6594 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FINALWORSTVOVERLOAD | Highest overload value after the plan | Integer |  |  |  | OPTCONTROLPLAN
6595 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FISRCARESULTID | ID of the FISRCA result | String |  |  |  | OPTCONTROLPLAN
6596 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FISRCASOLUTIONID | ID of the FISRCA solution | String |  |  |  | OPTCONTROLPLAN
6597 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FLOWPI | Weight of the final step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
6598 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.FLOWTEMPPI | Weight of the intermediate step flow violations performance index | Integer |  |  |  | OPTCONTROLPLAN
6599 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INITACTIVELOSS | Initial real power losses | Integer |  |  |  | OPTCONTROLPLAN
6600 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INITPFWITHINLIMIT | A flag indicating that the initial DPF was within the limit | Boolean |  |  |  | OPTCONTROLPLAN
6601 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INITREACTIVELOSS | Initial reactive power losses | Integer |  |  |  | OPTCONTROLPLAN
6602 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INITVOLTPI | Initial voltage performance index | Integer |  |  |  | OPTCONTROLPLAN
6603 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INITWORSTVOVERLOAD | Highest overload value before the plan | Integer |  |  |  | OPTCONTROLPLAN
6604 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.INTVAL | Initial value | String |  |  |  | OPTCONTROLPLAN
6605 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.ISAFRPLAN | A flag indicating a AFR plan | Boolean |  |  |  | OPTCONTROLPLAN
6606 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.ISFISRPLAN | A flag indicating a FISR plan | Boolean |  |  |  | OPTCONTROLPLAN
6607 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.ISPLORSPLAN | A flag indicating a PLOS plan | Boolean |  |  |  | OPTCONTROLPLAN
6608 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.ISVVCPLAN | A flag indicating a LVM plan | Boolean |  |  |  | OPTCONTROLPLAN
6609 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.KWNTRST | Total real power not restored including faulted switchable sections | Integer |  | kW | kW | OPTCONTROLPLAN
6610 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.KWRSTORE | The restored real power | Integer |  | kW | kW | OPTCONTROLPLAN
6611 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.LMIPI | Weight of the performance index for Load Minutes Interruption (LMI) | Integer |  |  |  | OPTCONTROLPLAN
6612 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.LOSSESPI | Weight of the final step losses performance index | Integer |  |  |  | OPTCONTROLPLAN
6613 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.LOSTLOADPI | Weight of the final step lost load performance index | Integer |  |  |  | OPTCONTROLPLAN
6614 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.LOSTLOADTEMPPI | Weight of the intermediate step lost load performance index | Integer |  |  |  | OPTCONTROLPLAN
6615 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.LOSTREV | Lost revenue value (adjusted for supply costs) | Integer |  |  |  | OPTCONTROLPLAN
6616 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAIFIPI | Weight of the performance index for the final step Momentary Average Interruption Frequency Index (MAIFI) | Integer |  |  |  | OPTCONTROLPLAN
6617 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAIFIPOSTPLAN | Post-plan MAIFI value | Integer |  |  |  | OPTCONTROLPLAN
6618 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAIFIPREPLAN | Pre-plan MAIFI value | Integer |  |  |  | OPTCONTROLPLAN
6619 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MARGINPI | Weight of the performance index for the final step maximum margin | Integer |  |  |  | OPTCONTROLPLAN
6620 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAXDEVVLT | Maximum device voltage | Float |  |  |  | OPTCONTROLPLAN
6621 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAXSEGLD | The maximum branch loading (percent) | Float |  |  |  | OPTCONTROLPLAN
6622 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MAXSEGMENTMARGINPI | Weight of performance index for the maximum segment load | Integer |  |  |  | OPTCONTROLPLAN
6623 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MINDEVVLT | Minimum device voltage | Float |  |  |  | OPTCONTROLPLAN
6624 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MINFDRVD | Minimum feeder voltage drop | Integer |  |  |  | OPTCONTROLPLAN
6625 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.MOVESPI | Weight of final step number of control moves performance index | Integer |  |  |  | OPTCONTROLPLAN
6626 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMCSTNRT | Total number of customers not restored including customers on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
6627 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMCSTOUT | The number of de-energized customers | Integer |  |  |  | OPTCONTROLPLAN
6628 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMCSTRES | Number of customers restored | Integer |  |  |  | OPTCONTROLPLAN
6629 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMCSTRES_ORG | The number of restored customers | Integer |  |  |  | OPTCONTROLPLAN
6630 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMCSVERYPOISON | Total number of customers very poison on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
6631 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMHPCSTNRT | The number of dropped customers with high priority | Integer |  |  |  | OPTCONTROLPLAN
6632 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMTFNRT | Total number of transformers not restored including transformers on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
6633 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMTFOUT | The number of de-energized transformers | Integer |  |  |  | OPTCONTROLPLAN
6634 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NMTFRES | The number of restored transformers | Integer |  |  |  | OPTCONTROLPLAN
6635 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NUMCMBUS | Number of common buses tap changer bus (AFR). | Integer |  |  |  | OPTCONTROLPLAN
6636 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NUMCONTROLMOVE | Number of control moves | Integer |  |  |  | OPTCONTROLPLAN
6637 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NUMRANK | Plan ranking (in ascending order from 1 to n number of plans) | Integer |  |  |  | OPTCONTROLPLAN
6638 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NUMSUBSTATIONS | Number of associated substations | Integer |  |  |  | OPTCONTROLPLAN
6639 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.NUMVOLTLIMCOMP | Number of voltage limiting devices | Integer |  |  |  | OPTCONTROLPLAN
6640 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTMOVES | Optimization steps | String |  |  |  | OPTCONTROLPLAN
6641 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANHASVIOLATION | A flag indicating that the optimization plan has violations | Boolean |  |  |  | OPTCONTROLPLAN
6642 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANID | ID of the optimization plan | String |  |  |  | OPTCONTROLPLAN
6643 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANTOAPPROVE | Optimization plan to approve | String |  |  |  | OPTCONTROLPLAN
6644 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANTOGOBACK | Optimization plan to go back | String |  |  |  | OPTCONTROLPLAN
6645 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANTOIMPLEMENT | Optimization plan to implement | String |  |  |  | OPTCONTROLPLAN
6646 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTPLANTOREJECT | Optimization plan to reject | String |  |  |  | OPTCONTROLPLAN
6647 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OPTSINGLEMOVES | Number of optimization steps in the plan | String |  |  |  | OPTCONTROLPLAN
6648 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OSMFISRFAULTEDCOMPS | [5 empty] | OPTCONTROLPLAN
6649 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.OUTAGEENERGIZEDPI | Weight of the performance index for lost energization | Integer |  |  |  | OPTCONTROLPLAN
6650 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANBACKFEEDKW | Backfeed real power flow | Float |  | kW | kW | OPTCONTROLPLAN
6651 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANBACKFEEDSUBID | Backfeed substation ID | String |  |  |  | OPTCONTROLPLAN
6652 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANBACKFEEDTRANSID | Backfeed transformer ID | String |  |  |  | OPTCONTROLPLAN
6653 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANDEVICES | Devices associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
6654 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANDEVICESFDRMAIN | A flag indicating that the device is located on the feeder backbone | Boolean |  |  |  | OPTCONTROLPLAN
6655 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANDEVICESORSTATIONS | Devices or stations associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
6656 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANEVALTIME | Evaluation time of the optimization plan | String |  |  |  | OPTCONTROLPLAN
6657 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANEVALTIME_TICKS | The time of the last optimization plan | String |  |  |  | OPTCONTROLPLAN
6658 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANFEEDERS | Feeders associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
6659 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANFUNCID | Plan function ID | String |  |  |  | OPTCONTROLPLAN
6660 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANLOSTKW | Lost kW | String |  |  |  | OPTCONTROLPLAN
6661 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXLOADSEGID | ID of the most heavily loaded branch | String |  |  |  | OPTCONTROLPLAN
6662 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXLOADSEGIDONLY | ID of the segment with the highest load in the plan | String |  |  |  | OPTCONTROLPLAN
6663 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXLOADSEGSUBID | ID of the substation the segment with the highest load belongs to | String |  |  |  | OPTCONTROLPLAN
6664 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXVLTDEVID | ID of the bus or load that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6665 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXVLTSUBID | ID of the substation that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6666 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMAXVLTTRANID | ID of the transformer that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6667 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMINVLTDEVID | ID of the bus or load that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6668 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMINVLTSUBID | ID of the substation that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6669 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANMINVLTTRANID | ID of the transformer that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
6670 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANSTATE | Plan state | Enumeration |  |  |  | OPTCONTROLPLAN
6671 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANSTATIONID | ID of the substation the optimization plan is associated with | String |  |  |  | OPTCONTROLPLAN
6672 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANSTATIONNAME | Name of the substation the optimization plan is associated with | String |  |  |  | OPTCONTROLPLAN
6673 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLANTYPE | Type of the plan, such as FISR Loss of Voltage or AFR Overload | Enumeration |  |  |  | OPTCONTROLPLAN
6674 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLOSSPRE | Real power losses before the plan execution (AFR) | Integer |  |  |  | OPTCONTROLPLAN
6675 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PLOSSPST | Real power losses after the plan execution (AFR) | Integer |  |  |  | OPTCONTROLPLAN
6676 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PREDUCTION | Total change in real power demand (kW) | Float |  |  |  | OPTCONTROLPLAN
6677 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PRIORITYCMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) with priority | Integer |  |  |  | OPTCONTROLPLAN
6678 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PROTECTIONPI | Weight of performance index for the final step execution of the Protection Validation function | Integer |  |  |  | OPTCONTROLPLAN
6679 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.PROTVAL | Protection value | String |  |  |  | OPTCONTROLPLAN
6680 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.QREDUCTION | Total change in reactive power demand (kVAR) | Float |  |  |  | OPTCONTROLPLAN
6681 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.RADIALFINAL | A flag indicating that the final switching state is radial | Boolean |  |  |  | OPTCONTROLPLAN
6682 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.RADIALPI | Weight for the final step radial condition performance index | Integer |  |  |  | OPTCONTROLPLAN
6683 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.RADIALTEMPPI | Weight for the intermediate step radial condition performance index | Integer |  |  |  | OPTCONTROLPLAN
6684 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.RECONFIGAPPNAME | Name of the reconfigurable application | String |  |  |  | OPTCONTROLPLAN
6685 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.REVNUPRE | Revenue before the plan execution | Integer |  |  |  | OPTCONTROLPLAN
6686 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.REVNUPST | Revenue after the plan execution | Integer |  |  |  | OPTCONTROLPLAN
6687 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIDIPI | Weight of the performance index for the final step System Average Interruption Duration Index (SAIDI) | Integer |  |  |  | OPTCONTROLPLAN
6688 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIDIPOSTPLAN | Post-plan SAIDI value | Integer |  |  |  | OPTCONTROLPLAN
6689 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIDIPREPLAN | Pre-plan SAIDI value | Integer |  |  |  | OPTCONTROLPLAN
6690 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIFIPI | Weight of the performance index for the final step System Average Interruption Frequency Index (SAIFI) | Integer |  |  |  | OPTCONTROLPLAN
6691 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIFIPOSTPLAN | Post-plan SAIFI value | Integer |  |  |  | OPTCONTROLPLAN
6692 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SAIFIPREPLAN | Pre-plan SAIFI value | Integer |  |  |  | OPTCONTROLPLAN
6693 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SECONDRATINGVIOLATIONS | A flag indicating that the second (emergency) ratings were violated at some point in the course of this plan | Boolean |  |  |  | OPTCONTROLPLAN
6694 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SHOWAFRPLAN | A flag to show AFR plans | Boolean |  |  |  | OPTCONTROLPLAN
6695 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SHOWFISRCAPLAN | A flag to show FISRCA plans | Boolean |  |  |  | OPTCONTROLPLAN
6696 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SHOWFISRPLAN | A flag to show FISR plans | Boolean |  |  |  | OPTCONTROLPLAN
6697 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SHOWLVMPLAN | Show LVM plan | String |  |  |  | OPTCONTROLPLAN
6698 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SHOWPLORSPLAN | A flag to show PLOS plans | Boolean |  |  |  | OPTCONTROLPLAN
6699 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SOLATIONDROPPOISONLOADPI | [5 empty] | OPTCONTROLPLAN
6700 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.SOLUTIONID | ID of the DNAF solution | String |  |  |  | OPTCONTROLPLAN
6701 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.STDCBPRE | Initial common tap changer bus standard deviation | Integer |  |  |  | OPTCONTROLPLAN
6702 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.STDCBPST | Final (post plan) common tap changer bus standard deviation | Integer |  |  |  | OPTCONTROLPLAN
6703 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.TFFINALPF | Final power transformer power factor | Float |  |  |  | OPTCONTROLPLAN
6704 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.TFINITPF | Initial power transformer power factor | Float |  |  |  | OPTCONTROLPLAN
6705 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.TOTALPI | Total performance index | Integer |  |  |  | OPTCONTROLPLAN
6706 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VOLTPI | Weight of the final step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
6707 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VOLTTEMPPI | Weight of the intermediate step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
6708 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCFINALLOSS | Post-plan active and reactive power losses | String |  |  |  | OPTCONTROLPLAN
6709 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCFLOWLIMITS | The flow violation limits strategy used in LVM | String |  |  |  | OPTCONTROLPLAN
6710 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCINITIALLOSS | Pre-plan active and reactive power losses | String |  |  |  | OPTCONTROLPLAN
6711 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCMAXTARGETPF | Maximum power factor target for station from manual overrride or from schedule | Float |  |  |  | OPTCONTROLPLAN
6712 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCMAXTARGETPFFORCE | LVM maximum target power force | String |  |  |  | OPTCONTROLPLAN
6713 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCMINTARGETPF | Minimum power factor target for station from manual overrride or from schedule | Float |  |  |  | OPTCONTROLPLAN
6714 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCMINTARGETPFFORCE | LVM minimum target power force | String |  |  |  | OPTCONTROLPLAN
6715 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCPROBFORM | The name of LVM problem formulation | String |  |  |  | OPTCONTROLPLAN
6716 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCSTATGROUP | The name of substation group | String |  |  |  | OPTCONTROLPLAN
6717 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN.VVCVOLTLIMITS | The voltage violation limits strategy used in LVM | String |  |  |  | OPTCONTROLPLAN
6718 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVSECONDID | Alternate ID of the device included in the optimization step | String
6719 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVSUBANDFEEDERNAME | Name of the substation and the feeder the optimization step is associated with | String
6720 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVSUBID | ID of the substation the optimization step is associated with | String
6721 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVSUBNAME | Name of the dynamic substation the optimization step device is associated with. | String
6722 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVTOGOBACK | Optimization step to go back | String
6723 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTMOVTOIMPLEMENT | Optimization step to implement | String
6724 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTPARENTAPPSTR | Address of the optimization device | String
6725 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | OPTPLAN | Pointer to the associated optimization control plan | String
6726 | DNAF Object | Optimization Control Plan | OPTCONTROLMOVE |  | OPTPLANSUBNAME | Optimization plan substation name | String
6727 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.CONTROLTYPE | Type of control | String |  |  |  | OPTCONTROLMOVE
6728 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICEINDEX | Vector index of device | Integer |  |  |  | OPTCONTROLMOVE
6729 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICENAME | Name of control device | String |  |  |  | OPTCONTROLMOVE
6730 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICENETTYPE | Device type | Integer |  |  |  | OPTCONTROLMOVE
6731 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICEPHASING | Phasing of device | Integer |  |  |  | OPTCONTROLMOVE
6732 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICETYPE | Type of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6733 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.DEVICETYPEMAP | Device type map | String |  |  |  | OPTCONTROLMOVE
6734 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.FINAL | Flag indicating that the final move. If true, this is a final move in the plan for this control, and there are no subsequent moves of the same control in this plan. | Boolean |  |  |  | OPTCONTROLMOVE
6735 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.ISSWTCONTROLLABLE | A flag indicating that the switch can be controlled | Boolean |  |  |  | OPTCONTROLMOVE
6736 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.ISVVCMOVE | A flag indicating that the optimization step is associated with the LVM application | Boolean |  |  |  | OPTCONTROLMOVE
6737 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.LVMEXEMODE | LVM execution mode. Can be closed loop or advisory. | String |  |  |  | OPTCONTROLMOVE
6738 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.MAX | [5 empty] | OPTCONTROLMOVE
6739 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.MIN | [5 empty] | OPTCONTROLMOVE
6740 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.MOVEDEVICEFDRMAIN | A flag indicating that the optimization device is on the feeder backbone | Boolean |  |  |  | OPTCONTROLMOVE
6741 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.NEXTINDEX | Index of the previous "ShowUser" move of this control in the plan. If null, this is the first move. | Enumeration |  |  |  | OPTCONTROLMOVE
6742 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTDEVNAME | Name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6743 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVADDR | Address of the optimization step | String |  |  |  | OPTCONTROLMOVE
6744 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVDEVALTID | Alternate ID of the device | String |  |  |  | OPTCONTROLMOVE
6745 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVDEVID | ID of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6746 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVDEVIDORSUBNAME | ID or substation name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6747 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVDEVNAME | Name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6748 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVDEVPHASE | Phases of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6749 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVFEEDERNAME | Name of the feeder the device included in the optimization step belongs to | String |  |  |  | OPTCONTROLMOVE
6750 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVFINALVALUE | Optimization step final value | String |  |  |  | OPTCONTROLMOVE
6751 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVFINALVAR | Final VAR injection | String |  | kVAR | kVAR | OPTCONTROLMOVE
6752 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVINITVALUE | Optimization step initial value | String |  |  |  | OPTCONTROLMOVE
6753 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVINITVAR | Initial VAR injection | String |  | kVAR | kVAR | OPTCONTROLMOVE
6754 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVLOADEFFECT | Load effect | String |  |  |  | OPTCONTROLMOVE
6755 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVLOADEFFECTAMPA | Load effect Amps phase A | String |  |  |  | OPTCONTROLMOVE
6756 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVLOADEFFECTAMPB | Load effect Amps phase B | String |  |  |  | OPTCONTROLMOVE
6757 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVLOADEFFECTAMPC | Load effect Amps phase C | String |  |  |  | OPTCONTROLMOVE
6758 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVOPERATION | Optimization step operation | String |  |  |  | OPTCONTROLMOVE
6759 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVSECONDID | Alternate ID of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6760 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVSUBANDFEEDERNAME | Name of the substation and the feeder the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6761 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVSUBID | ID of the substation the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6762 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVSUBNAME | Name of the substation the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6763 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVTOGOBACK | Optimization step to go back | String |  |  |  | OPTCONTROLMOVE
6764 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTMOVTOIMPLEMENT | Optimization step to implement | String |  |  |  | OPTCONTROLMOVE
6765 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTPARENTAPPSTR | Address of the optimization device | String |  |  |  | OPTCONTROLMOVE
6766 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTPLANTOGOBACK | Optimization plan to go back | String |  |  |  | OPTCONTROLMOVE
6767 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.OPTPLANTOIMPLEMENT | Optimization plan to implement | String |  |  |  | OPTCONTROLMOVE
6768 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.PLANFUNCID | Plan function ID | String |  |  |  | OPTCONTROLMOVE
6769 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.PLANSTATIONLVMHEU | Plan station LVM heuristic | Boolean |  |  |  | OPTCONTROLMOVE
6770 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.PLANSTATIONNAME | Name of the substation the plan belongs to | String |  |  |  | OPTCONTROLMOVE
6771 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.PLANSTEPNO | Starting from 1, indicates the step number in the plan | Integer |  |  |  | OPTCONTROLMOVE
6772 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.PREVINDEX | Index of the next "ShowUser" move of this control in the plan | Enumeration |  |  |  | OPTCONTROLMOVE
6773 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.SUBNAME | Name of the associated substation | String |  |  |  | OPTCONTROLMOVE
6774 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.SWITCHINGTYPE | Switching type (used by FISR, FISRCA, and PLOS) | Enumeration |  |  |  | OPTCONTROLMOVE
6775 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PNEXT.VIEWERTYPE | Device viewer type | String |  |  |  | OPTCONTROLMOVE
6776 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTPLANTOGOBACK | Optimization plan to go back | String
6777 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.CONTROLTYPE | Type of control | String |  |  |  | OPTCONTROLMOVE
6778 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICEINDEX | Vector index of device | Integer |  |  |  | OPTCONTROLMOVE
6779 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICENAME | Name of control device | String |  |  |  | OPTCONTROLMOVE
6780 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICENETTYPE | Device type | Integer |  |  |  | OPTCONTROLMOVE
6781 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICEPHASING | Phasing of device | Integer |  |  |  | OPTCONTROLMOVE
6782 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICETYPE | Type of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6783 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.DEVICETYPEMAP | Device type map | String |  |  |  | OPTCONTROLMOVE
6784 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.FINAL | Flag indicating that the final move. If true, this is a final move in the plan for this control, and there are no subsequent moves of the same control in this plan. | Boolean |  |  |  | OPTCONTROLMOVE
6785 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.ISSWTCONTROLLABLE | A flag indicating that the switch can be controlled | Boolean |  |  |  | OPTCONTROLMOVE
6786 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.ISVVCMOVE | A flag indicating that the optimization step is associated with the LVM application | Boolean |  |  |  | OPTCONTROLMOVE
6787 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.LVMEXEMODE | LVM execution mode. Can be closed loop or advisory. | String |  |  |  | OPTCONTROLMOVE
6788 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.MAX | [5 empty] | OPTCONTROLMOVE
6789 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.MIN | [5 empty] | OPTCONTROLMOVE
6790 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.MOVEDEVICEFDRMAIN | A flag indicating that the optimization device is on the feeder backbone | Boolean |  |  |  | OPTCONTROLMOVE
6791 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.NEXTINDEX | Index of the previous "ShowUser" move of this control in the plan. If null, this is the first move. | Enumeration |  |  |  | OPTCONTROLMOVE
6792 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTDEVNAME | Name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6793 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVADDR | Address of the optimization step | String |  |  |  | OPTCONTROLMOVE
6794 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVDEVALTID | Alternate ID of the device | String |  |  |  | OPTCONTROLMOVE
6795 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVDEVID | ID of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6796 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVDEVIDORSUBNAME | ID or substation name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6797 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVDEVNAME | Name of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6798 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVDEVPHASE | Phases of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6799 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVFEEDERNAME | Name of the feeder the device included in the optimization step belongs to | String |  |  |  | OPTCONTROLMOVE
6800 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVFINALVALUE | Optimization step final value | String |  |  |  | OPTCONTROLMOVE
6801 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVFINALVAR | Final VAR injection | String |  | kVAR | kVAR | OPTCONTROLMOVE
6802 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVINITVALUE | Optimization step initial value | String |  |  |  | OPTCONTROLMOVE
6803 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVINITVAR | Initial VAR injection | String |  | kVAR | kVAR | OPTCONTROLMOVE
6804 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVLOADEFFECT | Load effect | String |  |  |  | OPTCONTROLMOVE
6805 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVLOADEFFECTAMPA | Load effect Amps phase A | String |  |  |  | OPTCONTROLMOVE
6806 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVLOADEFFECTAMPB | Load effect Amps phase B | String |  |  |  | OPTCONTROLMOVE
6807 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVLOADEFFECTAMPC | Load effect Amps phase C | String |  |  |  | OPTCONTROLMOVE
6808 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVOPERATION | Optimization step operation | String |  |  |  | OPTCONTROLMOVE
6809 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVSECONDID | Alternate ID of the device included in the optimization step | String |  |  |  | OPTCONTROLMOVE
6810 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVSUBANDFEEDERNAME | Name of the substation and the feeder the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6811 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVSUBID | ID of the substation the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6812 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVSUBNAME | Name of the substation the optimization step is associated with | String |  |  |  | OPTCONTROLMOVE
6813 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVTOGOBACK | Optimization step to go back | String |  |  |  | OPTCONTROLMOVE
6814 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTMOVTOIMPLEMENT | Optimization step to implement | String |  |  |  | OPTCONTROLMOVE
6815 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTPARENTAPPSTR | Address of the optimization device | String |  |  |  | OPTCONTROLMOVE
6816 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTPLANTOGOBACK | Optimization plan to go back | String |  |  |  | OPTCONTROLMOVE
6817 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.OPTPLANTOIMPLEMENT | Optimization plan to implement | String |  |  |  | OPTCONTROLMOVE
6818 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.PLANFUNCID | Plan function ID | String |  |  |  | OPTCONTROLMOVE
6819 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.PLANSTATIONLVMHEU | Plan station LVM heuristic | Boolean |  |  |  | OPTCONTROLMOVE
6820 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.PLANSTATIONNAME | Name of the substation the plan belongs to | String |  |  |  | OPTCONTROLMOVE
6821 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.PLANSTEPNO | Starting from 1, indicates the step number in the plan | Integer |  |  |  | OPTCONTROLMOVE
6822 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.PREVINDEX | Index of the next "ShowUser" move of this control in the plan | Enumeration |  |  |  | OPTCONTROLMOVE
6823 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.SUBNAME | Name of the associated substation | String |  |  |  | OPTCONTROLMOVE
6824 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.SWITCHINGTYPE | Switching type (used by FISR, FISRCA, and PLOS) | Enumeration |  |  |  | OPTCONTROLMOVE
6825 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PPREV.VIEWERTYPE | Device viewer type | String |  |  |  | OPTCONTROLMOVE
6826 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | OPTPLANTOIMPLEMENT | Optimization plan to implement | String
6827 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PEAKLOADSAFETYFACTOR | Peak load safety factor | Float
6828 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PHASETRIPSAFETYFACTOR | The new phase trip current multiplied by the protection reach safety factor, in Amps | Float |  | Amps | Amps
6829 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PLANFUNCID | Plan function ID | String
6830 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PLANSTATIONLVMHEU | Plan station LVM heuristic | Boolean
6831 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PLANSTATIONNAME | Name of the substation the plan belongs to | String
6832 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PLANSTEPNO | Starting from 1, indicates the step number in the plan | Integer
6833 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE | input | PPREV | Pointer to the previous optimization plan control move | String
6834 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | PREVINDEX | Index of the next "ShowUser" move of this control in the plan | Enumeration
6835 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | REACHSAFETYFACTOR | Protection reach safety factor | Float
6836 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | SGOPTMOVECTRLTYPE | Control type (settings group type) | String
6837 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | SUBNAME | Name of the associated substation | String
6838 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | SWITCHINGTYPE | Switching type (used by FISR, FISRCA, and PLOS) | Enumeration
6839 | DNAF Object | Optimization Control Move | OPTCONTROLMOVE |  | VIEWERTYPE | Device viewer type | String
6840 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | _KEY | The unique identifier to represent a device | String
6841 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | AREAFINALPF | Final area power factor after plan | Float
6842 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | AREAFINALREACTIVEDEMAND | Final (post plan) station reactive power demand | Float
6843 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | AREAFINALREALDEMAND | Final (post plan) station real power demand. | Float
6844 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | AREAINITPF | Initial area power factor before plan | Float
6845 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | AREAINITREACTIVEDEMAND | Initial station reactive power demand | Integer
6846 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | AREAINITREALDEMAND | Initial station real power demand | Integer
6847 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | BUSVOLTIMBPI | Bus voltage imbalance performance index | String
6848 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CHANGEINREACTIVEDEMAND | Total change in reactive power demand | Integer |  | kVAR | kVAR
6849 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CHANGEINREALDEMAND | Total change in real power demand | Integer |  | kW | kW
6850 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) | Integer
6851 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | COMMENT | Operator comment | String
6852 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | COSTPI | Weight of the final step total cost performance index | Integer
6853 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | COSTTEMPPI | Weight of the intermediate step total cost performance index | Integer
6854 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CRITVOLT | Equalization of critical voltages (maximize TCUL tap range) | Integer
6855 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CTVUSPRE | Value of uninterrupted service before the plan execution | Integer
6856 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | CUSTVUS | Customer economic loss of value of uninterrupted service | Integer
6857 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DISPATCHSTARTTIME | The start date and time for a plan dispatch. Applies to LVM DER dispatch plans. | DateTime
6858 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DISPATCHDURATION | Number of minutes the plan is dispatched. Applies to LVM DER dispatch plans. | Integer
6859 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DNAFDCEVERSION | DCE parameters version | String
6860 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DNAFLASTMODIFIED | DCE parameters' last modified date | String
6861 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DNAFREVISIONNUM | DCE parameter revision number | String
6862 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DROPPEDCUSTOMERCOUNTPI | Weight of the final step count of the dropped customers performance index | Integer
6863 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DROPPEDCUSTOMERCOUNTTEMPPI | Weight of the intermediate step count of the dropped customers performance index | Integer
6864 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DROPPEDPRIORITYPI | Weight of the final step dropped customer priority performance index | Integer
6865 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DROPPEDPRIORITYTEMPPI | Weight of the intermediate step dropped customer priority performance index | Integer
6866 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | DSOPLANPROBFORMNAME | The name of problem formulation used in the optimization plan. | String
6867 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | DSOPLANSTATE | A string indicating the state of the control plan. 1.Bad 2.Good 3.Good-Neighbouring Violation 4.Good-Violation 5.Bad (LP_infeasible) 6.Bad (Power flow_Unsolved) 7. Request Stopped 8.Suspect 9.Invalid-Topology has Changed 10.Violation Detected-LVM Correction Available 11.Violation Detected-LVM Correction Not Available | String
6868 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REVERTEXECUTIONMODE | A string indicating the change in the plan execution mode due to the presence of third party owned equipment in a switching plan. This automatic change in the plan execution mode is based on the user-specified selection of the Third-Party Owned Equipment Options in the Switching Reconfiguration Problem Formulations page in the DNAF Configuration Editor. There are three possible values: Revert to Semi-Automatic”, “Revert to Advisory”, or “--". The default value is “--”. If ThirdPartyEquipInvolved bit is set, and the current plan execution is “Closed Loop” or “Closed Loop – Calculated Voltage Limit Violation Not Worse”, the plan execution mode for this plan will be automatically reverted to “Semi-Automatic”. If the ThirdPartyEquipInvolved bit is set, and the current plan execution is “Semi-Automatic”, the plan execution mode for this plan will be automatically reverted to “Advisory”. | String
6869 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FAULTCOMP |  | String
6870 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FEEDERFINALPF | Final power factor of the feeders | Float
6871 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FEEDERINITPF | Initial power factor of the feeders | Float
6872 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FEEDERTARGETPF | Target power factor of the feeders | Float
6873 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FINALACTIVELOSS | Final (post plan) real power losses | Integer
6874 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FINALPFWITHINLIMIT | A flag indicating that the final (post plan) DPF was within the limit | Boolean
6875 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FINALREACTIVELOSS | Final (post plan) reactive power losses | Integer
6876 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FINALVOLTPI | Final (post plan) voltage performance index | Integer
6877 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FINALWORSTVOVERLOAD | Highest overload value after the plan | Integer
6878 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FISRCARESULTID | ID of the FISRCA result | String
6879 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FISRCASOLUTIONID | ID of the FISRCA solution | String
6880 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FLOWPI | Weight of the final step bus voltage violations performance index | Integer
6881 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FLOWTEMPPI | Weight of the intermediate step flow violations performance index | Integer
6882 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDFEEDERNOMCRITICALCUSTOMERS | The nominal number of priority customers connected to the feeder (calculated by the FSD application) | Integer
6883 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDFEEDERNOMCUSTOMERS | The nominal number of customers connected to the feeder (calculated by the FSD application) | Integer
6884 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDFEEDERNOMGENERATION | The nominal generation on the feeder (calculated by the FSD application) | Float |  | kW | kW
6885 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDFEEDERNOMLOAD | The nominal load on the feeder (calculated by the FSD application) | Float |  | kW | kW
6886 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPOSTSTAGE2CRITICALCUSTOMERS | The number of de-energized priority customers after FSD Stage 2 (calculated by the FSD application) | Integer
6887 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPOSTSTAGE2CUSTOMERS | The number of de-energized customers after FSD Stage 2 (calculated by the FSD application) | Integer
6888 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPOSTSTAGE2GENERATION | The total generation on the feeder after FSD Stage 2 (calculated by the FSD application) | Float |  | kW | kW
6889 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPOSTSTAGE2LOAD | The total load on the feeder after FSD Stage 2 (calculated by the FSD application) | Float |  | kW | kW
6890 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPRESTAGE2CRITICALCUSTOMERS | The number of de-energized priority customers before FSD Stage 2 (calculated by the FSD application) | Integer
6891 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPRESTAGE2CUSTOMERS | The number of de-energized customers before FSD Stage 2 (calculated by the FSD application) | Integer
6892 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPRESTAGE2GENERATION | The total generation on the feeder before FSD Stage 2 (calculated by the FSD application) | Float |  | kW | kW
6893 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | FSDPRESTAGE2LOAD | The total load on the feeder before FSD Stage 2 (calculated by the FSD application) | Float |  | kW | kW
6894 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | FSDSTAGE | FSD application stage (1 or 2) | Integer
6895 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INITACTIVELOSS | Initial real power losses | Integer
6896 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INITPFWITHINLIMIT | A flag indicating that the initial DPF was within the limit | Boolean
6897 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INITREACTIVELOSS | Initial reactive power losses | Integer
6898 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INITVOLTPI | Initial voltage performance index | Integer
6899 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INITWORSTVOVERLOAD | Highest overload value before the plan | Integer
6900 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | INTVAL | Initial value | String
6901 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | ISAFRPLAN | A flag indicating a AFR plan | Boolean
6902 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | ISFISRPLAN | A flag indicating a FISR plan | Boolean
6903 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | ISOLATIONDROPPOISONLOADPI | Isolation dropped poison load performance index | String
6904 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | ISPLORSPLAN | A flag indicating a PLOS plan | Boolean
6905 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | ISVVCPLAN | A flag indicating a LVM plan | Boolean
6906 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWNTRST | Total real power not restored including faulted switchable sections | Float |  | kW | kW
6907 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTOREDERPHSA | Total real power of all DER loads after the plan minus the total real power of all energized DER loads before the plan for phase A | Float |  | kW | kW
6908 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTOREDERPHSB | Total real power of all DER loads after the plan minus the total real power of all energized DER loads before the plan for phase B | Float |  | kW | kW
6909 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTOREDERPHSC | Total real power of all DER loads after the plan minus the total real power of all energized DER loads before the plan for phase C | Float |  | kW | kW
6910 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTORENATPHSA | Total real power of all native loads after the plan minus the total real power of all energized native loads before the plan for phase A | Float |  | kW | kW
6911 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTORENATPHSB | Total real power of all native loads after the plan minus the total real power of all energized native loads before the plan for phase B | Float |  | kW | kW
6912 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRESTORENATPHSC | Total real power of all native loads after the plan minus the total real power of all energized native loads before the plan for phase C | Float |  | kW | kW
6913 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | KWRSTORE | The restored real power | Float |  | kW | kW
6914 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LMIPI | Weight of the performance index for Load Minutes Interruption (LMI) | Integer
6915 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LOSSESPI | Weight of the final step losses performance index | Integer
6916 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LOSTLOADPI | Weight of the final step lost load performance index | Integer
6917 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LOSTLOADTEMPPI | Weight of the intermediate step lost load performance index | Integer
6918 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LOSTREV | Lost revenue value (adjusted for supply costs) | Integer
6919 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LVMPLANTYPE | LVM plan type (Station Level Plan or Bank-Level Sub-Plan) | String
6920 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LVMSOLUTIONAREA | LVM solution area | String
6921 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | LVMSOLUTIONMIXED | Specifies whether the LVM solution includes plans for mixed problem formulations | Boolean
6922 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MAIFIPI | Weight of the performance index for the final step Momentary Average Interruption Frequency Index (MAIFI) | Integer
6923 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MAIFIPOSTPLAN | Post-plan MAIFI value | Integer
6924 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MAIFIPREPLAN | Pre-plan MAIFI value | Integer
6925 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MARGINPI | Weight of the performance index for the final step maximum margin | Integer
6926 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MAXDEVVLT | Maximum device voltage | Float
6927 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MAXNOOPERATION | Maximum number of operations performance index | Float
6928 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MAXNOSWITCHING | Maximum number of switching steps performance index | Float
6929 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MAXSEGLD | The maximum branch loading (percent) against regular flow limit | Float
6930 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MAXSEGMENTMARGINPI | Weight of performance index for the maximum segment load | Integer
6931 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MAXVLTVIO | Highest load voltage violation after reconfiguration in percentage | Float
6932 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MAXVLTVIOLIM | Highest violated voltage limit after reconfiguration in percentage | Float
6933 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MINDEVVLT | Minimum device voltage | Float
6934 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MINFDRVD | Minimum feeder voltage drop | Integer
6935 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MINVLTVIO | Lowest load voltage violation after reconfiguration in percentage | Float
6936 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | MINVLTVIOLIM | Lowest violated voltage limit after reconfiguration in percentage | Float
6937 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MOVESPI | Weight of final step number of control moves performance index | Integer
6938 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | THIRDPARTYMOVESPI | Weight of final step number of control moves involving third-party equipment performance index | Integer
6939 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | MOVEXECTIMEELAPSED | Time stent for execution of the control move | String
6940 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMCSTNRT | Total number of customers not restored including customers on the faulted switchable section | Integer
6941 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMCSTOUT | The number of de-energized customers | Integer
6942 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMCSTRES | Number of customers restored | Integer
6943 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMCSTRES_ORG | The number of restored customers | Integer
6944 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMCSVERYPOISON | Total number of customers very poison on the faulted switchable section | Integer
6945 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMHPCSTNRT | The number of dropped customers with high priority | Integer
6946 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMTFNRT | Total number of transformers not restored including transformers on the faulted switchable section | Integer
6947 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMTFOUT | The number of de-energized transformers | Integer
6948 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NMTFRES | The number of restored transformers | Integer
6949 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | NONCONVERGEDBLAISLANDPI | Non converged BLA islands performance index | String
6950 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | NUMBLANOTALLOCATEDMEASISLAND | Number of not allocated measurement islands | String
6951 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | NUMCMBUS | Number of common buses tap changer bus (AFR). | Integer
6952 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | NUMCONTROLMOVE | Number of control moves. | Integer
6953 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NUMMEASISLAND | Number of measurement islands | String
6954 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NUMNONCONVERGEDMEASISLAND | Number of non-converged measurement islands | String
6955 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NUMRANK | Plan ranking (in ascending order from 1 to n number of plans) | Integer
6956 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NUMSUBSTATIONS | Number of associated substations | Integer
6957 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | NUMTAPCHANGER | Number of affected tap changers | String
6958 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | NUMVOLTLIMCOMP | Number of voltage limiting devices | Integer
6959 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OBJFUNCID | Objective function ID. Used for the LVM pre-implementation plan check. | Integer
6960 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPMODEID | Operation mode ID | Integer
6961 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTMOVES | Optimization steps | String
6962 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANBRANCHFLOWPOSTVIOLATION | Optimization plan has post-plan branch flow violation (Indicates whether branch flow violations existed in the final loading, taking into account DER re-energization delay) | Boolean
6963 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANBRANCHFLOWPREVIOLATION | Optimization plan has pre-plan branch flow violation (Indicates whether branch flow violations existed in the initial loading) | Boolean
6964 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASBACKFEEDVIOLATION | Optimization plan has backfeed violation | Boolean
6965 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASFLOWVIOLATION | Optimization plan has flow violation | Boolean
6966 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASHIVOLTVIOLATION | Optimization plan has high voltage violation | Boolean
6967 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASLOWVOLTVIOLATION | Optimization plan has low voltage violation | Boolean
6968 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASNOTWORSEHIVOLTVIOLATION | Optimization plan has not worse high voltage violation | Boolean
6969 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASNOTWORSELOWVOLTVIOLATION | Optimization plan has not worse low voltage violation | Boolean
6970 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASPHASETRIPVIOLATION | Optimization plan has phase trip violation | Boolean
6971 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANHASVIOLATION | A flag indicating that the optimization plan has violations | Boolean
6972 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANID | ID of the optimization plan | String
6973 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANTOAPPROVE | Optimization plan to approve | Boolean
6974 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANTOGOBACK | Optimization plan to go back | Boolean
6975 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANTOIMPLEMENT | Optimization plan to implement | Boolean
6976 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTPLANTOREJECT | Optimization plan to reject | Boolean
6977 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OPTSINGLEMOVES | Number of optimization steps in the plan | String
6978 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OSMFISRFAULTEDCOMPS | FISR faulted components | String
6979 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | OUTAGEENERGIZEDPI | Weight of the performance index for lost energization | Integer
6980 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PILOADVOLTVIOLATIONFINAL | Load voltage violation weighted performance index | Float
6981 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PILOADVOLTVIOLATIONINT | Load voltage violation weighted performance index during intermediate steps | Float
6982 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PIMAXSEGMENTLOAD | Maximum segment margin performance index | Float
6983 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PIPROTECTIONMARGIN | Protection margin weighted performance index | Float
6984 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PIPROTECTIONREACH | Protection reach weighted performance index | Float
6985 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PISUMFLOWFINAL | Sum of real and reactive power performance index | Float
6986 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PIVOLTVIOLATIONFINAL | Bus voltage violation weighted performance index | Float
6987 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PIVOLTVIOLATIONINT | Bus voltage violation weighted performance index during intermediate steps | Float
6988 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBACKFEEDKW | Backfeed real power flow | Float |  | kW | kW
6989 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBACKFEEDSUBID | Backfeed substation ID | String
6990 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBACKFEEDTRANSID | Backfeed transformer ID | String
6991 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBACKFEEDTRANSIDGEOM | Geometry info of the transformer with backfeed | String
6992 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBACKFEEDTRANSLOCATEID | ID of the transformer with backfeed | String
6993 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBLAISLANDBRID | BLA island branch ID | String
6994 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBLAISLANDBRNAME | BLA island branch name | String
6995 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBLAISLANDINDEX | BLA island index | String
6996 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBLAISLANDNAME | BLA island name | String
6997 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANBLAISLANDSUBNAME | BLA island substation name | String
6998 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANDEVICES | Devices associated with the optimization plan | String
6999 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANDEVICESFDRMAIN | A flag indicating that the device is located on the feeder backbone | Boolean
7000 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANDEVICESORSTATIONS | Devices or stations associated with the optimization plan | String
7001 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANEVALTIME | Evaluation time of the optimization plan | String
7002 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANEVALTIME_TICKS | The time of the last optimization plan | String
7003 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANEXECSTATUSCODE | Plan execution status code | Integer
7004 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANEXECTYPE | Plan execution mode (for example, Closed Loop) | String
7005 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANFAULTEDFEEDERNAME | Name of the faulted feeder, as determined during FSD stage 1 | String
7006 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANTRIGGERINGDEVICENAME | The name of the device that triggered the plan | String
7007 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REVERTEXECUTIONMODE | Shows the new the plan execution mode if the plan execution mode changed due to the presence of third party owned equipment in a switching plan (for example, Revert to Semi Automatic). | String
7008 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANFEEDERS | Feeders associated with the optimization plan | String
7009 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANFINALAREAPF | Final (post-plan) area power factor | String
7010 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANFLOWLIMITTYPE | A string indicating the type of flow limit used to calculate the loading of the segment with maximum loading(Regular or De-rated) | String
7011 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANFUNCID | Plan function ID | String
7012 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANHASBACKFEEDTRANS | Optimization plan has backfeed transformer | Boolean
7013 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANIMPLEMENTINCLOSEDLOOP | A string indicating if the plan will be implemented automatically if the associated FISR/AFR execution is in “Closed Loop” mode or “Closed Loop – Calculated voltage Limit violation Not Worse” mode (Yes or No) | String
7014 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANINITIALAREAPF | Initial (pre-plan) area power factor | String
7015 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANLOSTKW | Lost kW | String
7016 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXFLOW | The maximum segment flow value after reconfiguration | Float |  | % | %
7017 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXFLOWDEROFF | The initial flow with DERs off for the maximum loaded segment in the final loading | Float |  | kVA/Amp | kVA/Amp
7018 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADING | The maximum branch loading (percent) against regular flow limit. It is against regular limit if adjusting limits based on reserved capacity is not enabled, and it is against de-rated limit if adjusting limits based on reserved capacity is enabled. | Float |  | % | %
7019 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADINGDERATEDLIMIT | The maximum branch loading (percent) against de-rated flow limit because of reserved capacity | Float
7020 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADINGDEROFF | The initial loading with DERs off for the maximum loaded segment in the final loading | Float |  | kVA/Amp | kVA/Amp
7021 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADINGREGULARLIMIT | The maximum branch loading (percent) against regular flow limit | Float
7022 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGDERATEDLIMITGEOM | Geometry info of the derated limit maximum loading segment | String
7023 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGDERATEDLIMITLOCATEID | ID of the derated limit maximum loading segment | String
7024 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGGEOM | Geometry info of the segment with maximum loading. | String
7025 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGGEONAME | Geometry name of the location of the maximum loaded segment after the LVM plan. | String
7026 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADSEGID | ID of the most heavily loaded branch against regular flow limit | String
7027 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXLOADSEGIDDERATEDLIMIT | ID of the most heavily loaded branch against de-rated flow limit because of reserved capacity | String
7028 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGIDONLY | ID of the segment with the highest load in the plan | String
7029 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGIDONLYDERATEDLIMIT | Plan maximum loading segment ID only derated limit | String
7030 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGLOCATEID | ID of the segment with maximum loading against regular flow limit. | String
7031 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGSUBID | ID of the substation the segment with the highest load belongs to | String
7032 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXLOADSEGSUBIDDERATEDLIMIT | Plan maximum loading segment substation ID derated limit | String
7033 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXPHASETRIPLOADING | The maximum recloser/breaker loading (percent) against phase trip rating. | Float
7034 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXPHASETRIPLOADINGDEVICEGEOM | Geometry info of the recloser/breaker that has the maximum loading against phase trip rating | String
7035 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXPHASETRIPLOADINGDEVICEID | ID of the recloser/breaker that has the maximum loading against phase trip rating for a switching reconfiguration plan | String
7036 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXPHASETRIPLOADINGDEVICELOCATEID | ID of the recloser/breaker that has the maximum loading against phase trip rating for a switching reconfiguration plan | String
7037 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXPHASETRIPLOADINGDEVICESUBNAME | Name of the station of the recloser/breaker that has the maximum loading against phase trip rating for a switching reconfiguration plan | String
7038 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXREGVOLTIMBID | ID of the device with the maximum regulator group voltage imbalance after the LVM plan. | String
7039 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXVLTDEVID | ID of the bus or load that has the maximum voltage for a switching reconfiguration or LVM plan | String
7040 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._FINALVALUE | The switch's final status that is involved in the optimization move | String |  |  |  | SWT
7041 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._OPTMOVADDR | The switch's device address that is involved in the optimization move | String |  |  |  | SWT
7042 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._OPTMOVDEVID | The switch's device ID that is involved in the optimization move | String |  |  |  | SWT
7043 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._OPTMOVDEVNAME | Switch's name | String |  |  |  | SWT
7044 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._OPTMOVSUBNAME | Switch's substation name | String |  |  |  | SWT
7045 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW._PLANID | The plan ID for the optimization plan contains the switch | String |  |  |  | SWT
7046 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.ABNDATETIME | Date and time the status was last changed | String |  |  |  | SWT
7047 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.ABNDATETIME_TICKS | The time when the switch’s status changed to abnormal | String |  |  |  | SWT
7048 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String |  |  |  | OSMQUERYDEVICE
7049 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
7050 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDARY | The boundary flag | Integer |  |  |  | SWT
7051 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWDYNFDR1 | Boundary Switch Dynamic Feeder 1 | String |  |  |  | SWT
7052 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWDYNFDR2 | Boundary Switch Dynamic Feeder 2 | String |  |  |  | SWT
7053 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.BOUNDSWFRNODE1 | To end node 1 of the boundary switch | String |  |  |  | SWT
7054 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.BOUNDSWFRNODE2 | To end node 2 of the boundary switch | String |  |  |  | SWT
7055 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWFRNODEDYNFDR1 | Boundary Switch From Node Dynamic Feeder 1 | String |  |  |  | SWT
7056 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWFRNODEDYNFDR2 | Boundary Switch From Node Dynamic Feeder 2 | String |  |  |  | SWT
7057 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWSUB1 | Boundary Switch Station 1 | String |  |  |  | SWT
7058 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWSUB2 | Boundary Switch Station 2 | String |  |  |  | SWT
7059 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.BOUNDSWTONODE1 | From end node 1 of the boundary switch | String |  |  |  | SWT
7060 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.BOUNDSWTONODE2 | From end node 2 of the boundary switch | String |  |  |  | SWT
7061 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWTONODEDYNFDR1 | Boundary Switch To Node Dynamic Feeder 1 | String |  |  |  | SWT
7062 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BOUNDSWTONODEDYNFDR2 | Boundary Switch To Node Dynamic Feeder 2 | String |  |  |  | SWT
7063 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.BRAKERHASMANUALENTRY | Flag indicating the switch has manual fault location input | Boolean |  |  |  | SWT
7064 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BRKFAULTINDSETSTATUSPHASE | Breaker fault indicator phases that are set | Boolean |  |  |  | SWT
7065 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BRKGRTRPAMP | Breaker ground trip setting | Float |  | Amps | Amps | SWT
7066 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.BRKPHTRPAMP | Breaker phase trip setting | Float |  | Amps | Amps | SWT
7067 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.CHGNOPEN | Flag indicating the change of the normally open status | Boolean |  |  |  | SWT
7068 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.CLOSEDBREAKER | Flag indicting the switch is closed breaker | Boolean |  |  |  | SWT
7069 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.COMPCONFIRMCLOSED | Confirmed Closed | Boolean |  |  |  | SWT
7070 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.COMPMEMBER | Whether the switch is associated with the composite switches | Boolean |  |  |  | SWT
7071 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.COMPPREDICTEDOUT | The device is closed but predicted open | Boolean |  |  |  | SWT
7072 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.CONNECTTOGROUND | Flag indicating the switch is energized and grounded | Integer |  |  |  | TOPOCOMP
7073 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.CROSSPHASE | Flag indicating the switch is cross phase | Boolean |  |  |  | SWT
7074 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.CURRENTSETINDEX | Current set index | String |  |  |  | SWT
7075 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.CURRENTSETTING | Current setting | String |  |  |  | SWT
7076 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.CURROPEN | Flag indicating the current open status | Boolean |  |  |  | SWT
7077 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.CURRPROTSETTING | Current protection setting | String |  |  |  | SWT
7078 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.CURRPROTSOURCES | Current protection sources | String |  |  |  | SWT
7079 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.DEVICEDSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String |  |  |  | SWT
7080 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DEVICEPHASE | Switch's available phases | String |  |  |  | SWT
7081 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DEVTYPE | Enumeration of device type (0 - None (should never occur), 1 - Switch, 2- Fuse, 3- Recloser, 4 - Breaker, 5 - Sectionalizer, 6 - Jumper/Permanent Jumper, 7 - NetworkProtector) | Enumeration |  |  |  | SWT
7082 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.DMSRECLOSERTYPE | Recloser type | String |  |  |  | SWT
7083 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DNOMTABNAME | The DNOM table name of the switch | String |  |  |  | SWT
7084 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DNOMX | Coordinate X | Float |  |  |  | DNMOBJ
7085 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DNOMY | Coordinate Y | Float |  |  |  | DNMOBJ
7086 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
7087 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DSOSWCONTROLENABLED | Flag indicting if the switch is optimization enabled for FISR under the current problem formulation. | Boolean |  |  |  | SWT
7088 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DYNAMICFEEDER | Switch's dynamic feeder | String |  |  |  | SWT
7089 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.DYNFEEDERNAME2 | Second dynamic energizing feeder name (for currently open switches) | String |  |  |  | SWT
7090 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.DYNSTATIONNAME2 | Name of the abnormally energizing substation | String |  |  |  | SWT
7091 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.EXTERNALINTERFACE | Flag indicating if the switch is membership in external interface | Boolean |  |  |  | SWT
7092 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.EXTERNALLYOWNED | Flag indicating if the switch's status is provided by the external system | Boolean |  |  |  | SWT
7093 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.FADEVTYPE | Whether the switch is used in PRV validation | Boolean |  |  |  | SWT
7094 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.FDRMAIN | Flag indicating the switch is a part of the feeder main | Boolean |  |  |  | SWT
7095 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.FEEDERMAIN | Flag indicating if the switch is on feeder main | Boolean |  |  |  | TOPOCOMP
7096 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.FEEDINGFEEDER | The dynamic feeder name | String |  |  |  | SWT
7097 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.FEEDINGSUB | The substation name of dynamic feeder | String |  |  |  | SWT
7098 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.FEEDMAINBOUND | A flag indicating that the switch is a feeder main boundary device | Boolean |  |  |  | SWT
7099 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.FROMEMS | Flag indicting the object is described in the EMS file during model construction | Boolean |  |  |  | TOPOLOGYOBJECT
7100 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.FROMLINEVERTEXSX | X coordinates of the from line vertices | Float |  |  |  | SWT
7101 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.FROMLINEVERTEXSY | Y coordinates of the from line vertices | Float |  |  |  | SWT
7102 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.FUSEKVAD | DPF calculated total apparent power flow (kVA) | Float |  | kVA | kVA | SWT
7103 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.FUSELOADPERCENT | DPF calculated three-phase loading percentage | Float |  | percent | percent | SWT
7104 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.FUSELOOPNUMBER | Loop Number | String |  |  |  | SWT
7105 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.FUSETOTALAMPS | DPF calculated total current flow | Float |  | Amps | Amps | SWT
7106 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.HAS_STATUS_MEAS | A flag indicating that the switch has status measurement | Boolean |  |  |  | SWT
7107 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.HASSETGROUP | Flag indicating the switch has protection settings group | Boolean |  |  |  | SWT
7108 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.ID | Unique and persistent ID | String |  |  |  | DNMOBJ
7109 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.ISAUTOMATEDSWITCH | Whether the switch is an automated switch | Boolean |  |  |  | TOPOCOMP
7110 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MAXCAPRATIOS | Maximum interruption violation ratio | Float |  | percent | percent | SWT
7111 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MAXFAULTCURRENT | Maximum fault current | Float |  | Amps | Amps | SWT
7112 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.MAXINTERRUPT | Maximum interrupting current rating (breakers and reclosers) | Float |  |  |  | SWT
7113 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MAXINTERRUPTVIOLATION | Flag indicating maximum interruption violation exists for the breaker or recloser | Boolean |  |  |  | SWT
7114 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.MAXPHANGLEDIFF | Maximum phase angle tolerance for feeder main switch | Float |  | degree | degree | SWT
7115 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGNDPROTDEVCUR | Minimum Ground Fault Current. Calculated minimum ground fault current in amps. This value is calculated by the PRV function. For all devices, single line-to-ground fault current is calculated. | String |  |  |  | SWT
7116 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGNDPROTDEVID | Minimum Ground Protective Device ID. The ID of the device that protects the zone from the minimum ground fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String |  |  |  | SWT
7117 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGNDPROTDEVLIMIT | Minimum ground pick-up current limit in amps | String |  | Amps | Amps | SWT
7118 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGNDPROTDEVNAME | Minimum Ground Protective Device Name. The name of the device that protects the zone from the minimum ground fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String |  |  |  | SWT
7119 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGROUNDFAULTCURRENT | Minimum ground fault current | Float |  | Amps | Amps | SWT
7120 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.MINGROUNDFAULTLOCATION | The line or distribution transformer id that connected to minimum single phase to ground fault node | String |  |  |  | SWT
7121 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGROUNDFAULTSUBNAME | The owning station name of the ground fault node | String |  |  |  | SWT
7122 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGROUNDFAULTTYPE | Type of minimum ground fault | String |  |  |  | SWT
7123 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.MINGROUNDPICKUP | Minimum ground pick up rating | Float |  |  |  | SWT
7124 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGROUNDPICKUPRATIOS | Minimum ground pick-up violation ratio | Float |  | percent | percent | SWT
7125 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINGROUNDPICKUPVIOLATION | Flag indicating minimum ground pick-up violation exists for the breaker or recloser | Boolean |  |  |  | SWT
7126 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHASEFAULTCURRENT | Minimum phase fault current | Float |  | Amps | Amps | SWT
7127 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHASEFAULTLOCATION | ID of min phase fault node | String |  |  |  | SWT
7128 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHASEFAULTSUBNAME | The owning station name of the phase fault node | String |  |  |  | SWT
7129 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.MINPHASEPICKUP | Minimum phase pick up rating | Float |  |  |  | SWT
7130 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHASEPICKUPRATIOS | Minimum phase pick-up violation ratio | Float |  | percent | percent | SWT
7131 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHASEPICKUPVIOLATION | Flag indicating minimum phase pick-up violation exists for the breaker or recloser | Boolean |  |  |  | SWT
7132 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHPROTDEVCUR | Minimum Phase Fault Current. Calculated minimum phase fault current in amps. This field is not applicable for two-phase reclosers, single-phase reclosers, or fuses. | String |  |  |  | SWT
7133 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHPROTDEVID | Minimum Phase Protective Device ID. The ID of the device that protects the zone from the minimum phase fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String |  |  |  | SWT
7134 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHPROTDEVLIMIT | Minimum phase pick-up current limit in amps. This field is only applicable for three-phase devices. | String |  | Amps | Amps | SWT
7135 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.MINPHPROTDEVNAME | Minimum Phase Protective Device Name. The name of the device that protects the zone from the minimum phase fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String |  |  |  | SWT
7136 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.NAME | Name | String |  |  |  | DNMOBJ
7137 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.NEWATMSK | Additional attributes bitmask flag flag | Integer |  |  |  | TOPOLOGYOBJECT
7138 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.NEWATMSK2 | More additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
7139 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.NOMINALSETTING | Nominal setting | String |  |  |  | SWT
7140 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.NOPEN | Flag indicating the normally open status | Boolean |  |  |  | SWT
7141 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.NORMOPENPHASES | Normally open phases | String |  |  |  | SWT
7142 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.NORMPOSITION | Normal position | String |  |  |  | SWT
7143 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
7144 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.OPTMANDSOVISIBLE |  | Boolean |  |  |  | SWT
7145 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.OSMDEVTLN | Switch ID used in OSM application | String |  |  |  | SWT
7146 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.PENDPERMNEWSTATENAME | Pending permanent switch nominal status | String |  |  |  | SWT
7147 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.PENDPERMSTATUS | Pending permanent status (true = awaiting permanent status change) | Boolean |  |  |  | SWT
7148 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.PENDPERMSWNAME | Pending permanent switch name | String |  |  |  | SWT
7149 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.PROTCOORD | Short Circuit Coordination. This field returns a value of Coordinated or Uncoordinated after checking the fault analysis protection coordination calculation. This is an optional study mode only calculation performed within the fault analysis application. | String |  |  |  | SWT
7150 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.PROTCOORDUPDEV | Upstream Protection Device. The name of the coordinated upstream protection device. This device can be the further upstream protection device if the device immediately upstream is not coordinated. | String |  |  |  | SWT
7151 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING1 | Protection setting group 1 | String |  |  |  | SWT
7152 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING10 | Protection setting group 10 | String |  |  |  | SWT
7153 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING2 | Protection setting group 2 | String |  |  |  | SWT
7154 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING3 | Protection setting group 3 | String |  |  |  | SWT
7155 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING4 | Protection setting group 4 | String |  |  |  | SWT
7156 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING5 | Protection setting group 5 | String |  |  |  | SWT
7157 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING6 | Protection setting group 6 | String |  |  |  | SWT
7158 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING7 | Protection setting group 7 | String |  |  |  | SWT
7159 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING8 | Protection setting group 8 | String |  |  |  | SWT
7160 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSETTING9 | Protection setting group 9 | String |  |  |  | SWT
7161 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES1 | Protection source 1 | String |  |  |  | SWT
7162 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES10 | Protection source 10 | String |  |  |  | SWT
7163 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES2 | Protection source 2 | String |  |  |  | SWT
7164 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES3 | Protection source 3 | String |  |  |  | SWT
7165 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES4 | Protection source 4 | String |  |  |  | SWT
7166 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES5 | Protection source 5 | String |  |  |  | SWT
7167 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES6 | Protection source 6 | String |  |  |  | SWT
7168 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES7 | Protection source 7 | String |  |  |  | SWT
7169 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES8 | Protection source 8 | String |  |  |  | SWT
7170 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.PROTSOURCES9 | Protection source 9 | String |  |  |  | SWT
7171 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.PROTVALID | Protected or "Unprotected" determined by the protection validation calculation | String |  |  |  | SWT
7172 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.PRVSAFETYFACTOR | PRV safety factor | String |  |  |  | SWT
7173 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECAMPRATING | Recloser's rating amps | Float |  |  |  | SWT
7174 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECGRTRIPAMPS | Recloser ground trip setting multiplied by a safety factor | Float |  | Amps | Amps | SWT
7175 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECGRTRIPAMPSNOSF | Ground trip current setting with no safety factor multiplied | Float |  | Amps | Amps | SWT
7176 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECGRTRIPCAPABLE | Flag indicating recloser has ground trip capability | Boolean |  |  |  | SWT
7177 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECGRTRIPSTATUS | Recloser ground trip status | String |  |  |  | SWT
7178 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECINTERRUPTAMPS | Maximum interruption rating | Float |  | Amps | Amps | SWT
7179 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECNOMOPMODE | Recloser's nominal operating mode | String |  |  |  | SWT
7180 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECPHTRIPAMPS | Recloser phase trip setting multiplied by a safety factor | Float |  | Amps | Amps | SWT
7181 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECPHTRIPAMPSNOSF | Phase trip current setting with no safety factor multiplied | Float |  | Amps | Amps | SWT
7182 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECRECLOSESTATUS | Reclosing Status | String |  |  |  | SWT
7183 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RECRECLOSEUISTATUS | Reclosing enabled status | String |  |  |  | SWT
7184 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.RELAYTYPE | The relay type of the switch | String |  |  |  | SWT
7185 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.REMOTE | Flag indicating the remotely controlled status | Boolean |  |  |  | SWT
7186 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.REVERSIBLEREC | Flag indicating if recloser is reversible for current flow direction | Boolean |  |  |  | SWT
7187 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SGNOTES | The notes of protection settings group | String |  |  |  | SWT
7188 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SGNUM | The number of limits in protection settings group | Integer |  |  |  | SWT
7189 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SGSETTINGS | The station, feeder, setting of protection setting in protection settings group | String |  |  |  | SWT
7190 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SOLIDBLADEFUSE | Flag indicating if device is a solid blade fuse | Boolean |  |  |  | SWT
7191 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.STATIONBOUNDARY | A flag indicating that the switch is a station boundary device | Boolean |  |  |  | SWT
7192 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWCLOSEDPHASES | Switch's phases in "Closed" state | String |  |  |  | SWT
7193 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWCURRENTPOSITION | Current position | String |  |  |  | SWT
7194 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWHASMANFLOWLIM | Flag indicating the manual entry flow limit | Boolean |  |  |  | SWT
7195 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWHASMANLDBRKCAP | Flag indicating the manual entry load break capability | Boolean |  |  |  | SWT
7196 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWHASMANLDBRKRAT | Flag indicating the manual entry load break rating | Boolean |  |  |  | SWT
7197 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWHASMANUALENTRY | Flag indicating the switch has manual entry | Boolean |  |  |  | SWT
7198 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHCUSTCNT | Customer count, number of energized downstream customers | Integer |  |  |  | TOPOCOMP
7199 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHMODPHA | Get the phase A's switch model name | String |  |  |  | SWT
7200 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHMODPHB | Get the phase B's switch model name | String |  |  |  | SWT
7201 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHMODPHC | Get the phase C's switch model name | String |  |  |  | SWT
7202 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHNOMINAL | Switch nominal status | String |  |  |  | SWT
7203 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHPHASEIND | Switch phase indicator | String |  |  |  | SWT
7204 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWITCHSIZE | Switch size (from associated model) | Float |  |  |  | SWT
7205 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWITCHTYPE | Switch type enumeration description of associated switch model for the switch | String |  |  |  | SWT
7206 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM1 | Level 1 limit value (used by limit monitor function) | Float |  |  |  | SWT
7207 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM1NAME | Level 1 limit name | String |  |  |  | SWT
7208 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLIM1SEASON | Level 1 limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7209 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM2 | Level 2 limit value (used by limit monitor function) | Float |  |  |  | SWT
7210 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM2NAME | Level 2 limit name | String |  |  |  | SWT
7211 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLIM2SEASON | Level 2 limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7212 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM3 | Level 3 limit value (used by limit monitor function) | Float |  |  |  | SWT
7213 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM3NAME | Level 3 limit name | String |  |  |  | SWT
7214 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLIM3SEASON | Level 3 limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7215 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM4 | Level 4 limit value (used by limit monitor function) | Float |  |  |  | SWT
7216 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM4NAME | Level 4 limit name | String |  |  |  | SWT
7217 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLIM4SEASON | Level 4 limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7218 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM5 | Level 5 limit value (used by limit monitor function) | Float |  |  |  | SWT
7219 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLIM5NAME | Level 5 limit name | String |  |  |  | SWT
7220 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLIM5SEASON | Level 5 limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7221 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLOADBRKCAPNOM | Flag indicating the switch has nominal load break capability | Boolean |  |  |  | SWT
7222 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWLOADBRKRATING | Load break rating | Float |  |  |  | SWT
7223 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWLOADBRKRATINGNOM | nominal load break rating (amps per phase) | Float |  |  |  | SWT
7224 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMANDSO | Flag indicting if the switch is optimization enabled | Boolean |  |  |  | SWT
7225 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMANFLOWLIM | Manual entry flow limit value | String |  |  |  | SWT
7226 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMANLDBRKCAP | Manual entry load break capability | Boolean |  |  |  | SWT
7227 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWMANLDBRKCAPABLE | Flag indicating if the switch has manual entry load break capability | Boolean |  |  |  | SWT
7228 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMANLDBRKRAT | Manual entry load break rating (amps per phase) | Float |  |  |  | SWT
7229 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
7230 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWMASK2 | Mask that shows bits about the phase independent switching | Integer |  |  |  | SWT
7231 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWMASKD | Switch attribute mask | Integer |  |  |  | SWT
7232 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWNOMLIM1 | Level 1 nominal limit information under current season of associated switch model of the switch | String |  |  |  | SWT
7233 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWOPENPHASEA | Indicates if phase A is open | Boolean |  |  |  | SWT
7234 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWOPENPHASEB | Indicates if phase B is open | Boolean |  |  |  | SWT
7235 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWOPENPHASEC | Indicates if phase C is open | Boolean |  |  |  | SWT
7236 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWOPENPHASES | Switch's phases in "Open" state | String |  |  |  | SWT
7237 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWOSWTINFOMASK | Additional bits for related phase independent statuses | Integer |  |  |  | SWT
7238 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWSTATUS | The switch status. Deenergized, Open, Looped, Paralleled, Closed. | String |  |  |  | SWT
7239 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWSTRINGTYPE | The switch device type | String |  |  |  | SWT
7240 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTABNORMAL | Phases abnormally energized | String |  |  |  | SWT
7241 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTALARMSTATUS | Alarm status measurement | String |  |  |  | SWT
7242 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTAUTOMANUAL | Auto/Manual status measurement. Deprecated. Use SWTAUTOMANUALSTATUS instead. | String |  |  |  | SWT
7243 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTAUTORECLSTATUS | Automatic reclosing status measurement | String |  |  |  | SWT
7244 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTAUTOSCH | Flag indicting if the auto scheme is enabled | Boolean |  |  |  | SWT
7245 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTCURPOSSTATUS | Current switch state measurement | String |  |  |  | SWT
7246 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTCURPOSSTATUSMEASID | ID of the switch status measurement point | String |  |  |  | SWT
7247 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTDEVICEFAIL | Flag indicting if the switch is set as failure for all phases in SCADA | Boolean |  |  |  | SWT
7248 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTDSOSCADA | Flag indicting switch is currently DSO SCADA decides | Boolean |  |  |  | SWT
7249 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTDSOUSEROFF | Flag indicting switch is currently DSO user disabled | Boolean |  |  |  | SWT
7250 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTDSOUSERON | Flag indicting switch is currently DSO user enabled | Boolean |  |  |  | SWT
7251 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTFLOWIMBLIMITPERCENT | Get flow imbalance limit percent value by method 1 (with safety factor) | Float |  | percent | percent | SWT
7252 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTFLOWIMBLIMITPERCENT2 | Flow imbalance limit percent value by method 2 | Float |  | percent | percent | SWT
7253 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTFLOWIMBLIMITVALUE | Flow imbalance limit value | Float |  | Amps | Amps | SWT
7254 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTFLOWIMBVALUE | Get flow imbalance value by method 1 (with safety factor) | Float |  | Amps | Amps | SWT
7255 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTFLOWIMBVALUE2 | Get flow imbalance value by method 2 | Float |  | Amps | Amps | SWT
7256 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTFRPHANGLEA | Phase A voltage angle of from node | Float |  | degree | degree | SWT
7257 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTFRPHANGLEB | Phase B voltage angle of from node | Float |  | degree | degree | SWT
7258 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTFRPHANGLEC | Phase C voltage angle of from node | Float |  | degree | degree | SWT
7259 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTFUTURE | Future (not constructed) phases | String |  |  |  | SWT
7260 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTHASFLOWIMBLVIOLATION | Flag indicting the switch has flow imbalance violation by method 1 (with safety factor) | Boolean |  |  |  | SWT
7261 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANSW.SWTHASFLOWIMBLVIOLATION2 | Flag indicting the switch has flow imbalance violation by method 2 | Boolean |  |  |  | SWT
7262 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTHOTLINETAGSTATUS | Hot line tag status measurement | String |  |  |  | SWT
7263 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWTLOCKOUT | Flag indicating the switch is lockout | Boolean |  |  |  | SWT
7264 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTLOCKOUTSTATUS | Lockout status measurement | String |  |  |  | SWT
7265 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTLOOPED | Phases currently in a loop | String |  |  |  | SWT
7266 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTMANSCADADSO | Flag indicting if the switch is currently DSO SCADA decides | Boolean |  |  |  | SWT
7267 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWTMANUSERDSODISABLED | Flag indicating if the switch is currently DSO user disabled | Boolean |  |  |  | SWT
7268 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTMANUSERDSOENABLED | Flag indicating if the switch is currently DSO user enabled | Boolean |  |  |  | SWT
7269 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTPHANGLEADIFF | Phase A voltage angle difference between from node and to node | Float |  | degree | degree | SWT
7270 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTPHANGLEBDIFF | Phase B voltage angle difference between from node and to node | Float |  | degree | degree | SWT
7271 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWTPHANGLECDIFF | Phase C voltage angle difference between from node and to node | Float |  | degree | degree | SWT
7272 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTPREVENTCLOSE | Flag indicting if the switch is in Block Close mode. In this mode, switch can not be closed. | Boolean |  |  |  | SWT
7273 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTRECLOSEROPMODESTATUS | Recloser mode status measurement | String |  |  |  | SWT
7274 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTREMOTECONTROLSTATUS | Remote control status measurement | String |  |  |  | SWT
7275 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTREMOTECTRL | Flag indicates whether the switch is remotely controlled | Boolean |  |  |  | SWT
7276 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTSCADADSO | Flag indicting if the switch is currently DSO SCADA decides | Boolean |  |  |  | SWT
7277 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTSCUTOUT | Flag indicting if the switch is in Supervisory Cutout mode. In this mode, switch is not controllable by the operator but it can be manually operated in the field. | Boolean |  |  |  | SWT
7278 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.SWTSUPERVISORYCUTOUTSTATUS | Supervisory cutout status measurement | String |  |  |  | SWT
7279 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTTOPHANGLEA | Phase A voltage angle of to node | Float |  | degree | degree | SWT
7280 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTTOPHANGLEB | Phase B voltage angle of to node | Float |  | degree | degree | SWT
7281 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.SWTTOPHANGLEC | Phase C voltage angle of to node | Float |  | degree | degree | SWT
7282 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWTTYPECODE | Switch device type enumeration | Integer |  |  |  | SWT
7283 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.SWTUSERDSODISABLED | Flag indicating if the switch is currently DSO user disabled | Boolean |  |  |  | SWT
7284 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW.SWTUSERDSOENABLED | Flag indicating if the switch is currently DSO user enabled | Boolean |  |  |  | SWT
7285 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS1A | Phase A amps of Feeder 1 of TC solution for the switch | Float |  |  |  | SWT
7286 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS1B | Phase B amps of Feeder 1 of TC solution for the switch | Float |  |  |  | SWT
7287 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS1C | Phase C amps of Feeder 1 of TC solution for the switch | Float |  |  |  | SWT
7288 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS2A | Phase A amps of Feeder 2 of TC solution for the switch | Float |  |  |  | SWT
7289 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS2B | Phase B amps of Feeder 2 of TC solution for the switch | Float |  |  |  | SWT
7290 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCAMPS2C | Phase C amps of Feeder 2 of TC solution for the switch | Float |  |  |  | SWT
7291 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCDEVTYPE | Flag indicating the switch has transfer capacity | Boolean |  |  |  | SWT
7292 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCFEEDFROM1 | Feeder name of from node side in TC result | String |  |  |  | SWT
7293 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCFEEDFROM2 | Feeder name of from node side in TC result | String |  |  |  | SWT
7294 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCFEEDTO1 | Feeder name of to node side in TC result | String |  |  |  | SWT
7295 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.TCFEEDTO2 | Feeder name of to node side in TC result | String |  |  |  | SWT
7296 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCMARKDEVICES | Two limiting switch Id and owning station name if TC for the switch is solved | String |  |  |  | SWT
7297 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCSW1SUBNAME | limiting switch 1 owning station name if TC for the switch is solved | String |  |  |  | SWT
7298 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCSW2SUBNAME | limiting switch 2 owning station name if TC for the switch is solved | String |  |  |  | SWT
7299 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCSWFILTER | Flag indicating a non-zero TC solution exists for the switching device | Boolean |  |  |  | SWT
7300 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCSWITCH1 | limiting switch 1 name if TC for the switch is solved | String |  |  |  | SWT
7301 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Output | PLANSW.TCSWITCH2 | limiting switch 2 name if TC for the switch is solved | String |  |  |  | SWT
7302 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | Input | PLANSW.TESTSWITCHATTRIBUTE | Test attribute value for a switch | String |  |  |  | SWT
7303 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.TOLINEVERTEXSX | X coordinates of the to line vertices | Float |  |  |  | SWT
7304 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.TOLINEVERTEXSY | Y coordinates of the to line vertices | Float |  |  |  | SWT
7305 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.TOPOABNORMAL | Phases abnormally energized | String |  |  |  | SWT
7306 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSW.TOPOLOOPED | Phases currently in a loop | String |  |  |  | SWT
7307 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXVLTGEONAME | Geometry name of the location of the load with the maximum voltage after the LVM plan. | String
7308 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXVLTSUBID | ID of the substation that has the maximum voltage for a switching reconfiguration or LVM plan | String
7309 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXVLTTRANID | ID of the transformer that has the maximum voltage for a switching reconfiguration or LVM plan | String
7310 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXVLTTRANIDGEOM | Geometry info of the transformer with maximum voltage | String
7311 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMAXVLTTRANLOCATEID | ID of the transformer with maximum voltage | String
7312 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXVLTVIODEVID | ID of the load with highest voltage violation | String
7313 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXVLTVIOSUBID | ID of the substation that is associated with the load with the highest voltage violation | String
7314 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXVLTVIOTRANIDGEOM | Geometry name of the location of the device with the highest voltage violation after the plan | String
7315 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMAXVLTVIOTRANLOCATEID | ID of the transformer that is associated with the load with the highest voltage violation | String
7316 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTDEVID | ID of the bus or load that has the minimum voltage for a switching reconfiguration or LVM plan | String
7317 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTGEONAME | Geometry name of the location of the load with the minimum voltage after the LVM plan. | String
7318 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTSUBID | ID of the substation that has the minimum voltage for a switching reconfiguration or LVM plan | String
7319 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTTRANID | ID of the transformer that has the minimum voltage for a switching reconfiguration or LVM plan | String
7320 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTTRANIDGEOM | Geometry info of the transformer with minimum voltage | String
7321 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANMINVLTTRANLOCATEID | ID of the transformer with minimum voltage | String
7322 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMINVLTVIODEVID | ID of the load with lowest voltage violation | String
7323 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMINVLTVIOSUBID | ID of the substation that is associated with the load with lowest voltage violation | String
7324 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMINVLTVIOTRANIDGEOM | Geometry name of the location of the device with the lowest voltage violation after the plan | String
7325 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANMINVLTVIOTRANLOCATEID | ID of the transformer that is associated with the load with lowest voltage violation | String
7326 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANNOLONGERVALIDTIMEMAXLOADING | The maximum branch overloading (percent) against regular flow limit at the plan no longer valid time when cold load pickup is considered. | Float
7327 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANNOLONGERVALIDTIMEMAXLOADSEGGEOM | Geometry info of the segment with maximum overloading at the plan no longer valid time when cold load pickup is considered.. | String
7328 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANNOLONGERVALIDTIMEMAXLOADSEGID | ID of the most heavily overloaded branch against regular flow limit at the plan no longer valid time when cold load pickup is considered. | String
7329 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANNOLONGERVALIDTIMEMAXLOADSEGLOCATEID | ID of the segment with maximum overloading against regular flow limit at the plan no longer valid time when cold load pickup is considered. | String
7330 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANNOLONGERVALIDTIMEMAXLOADSEGSUBID | ID of the substation which the highest overloaded branch belongs to at the plan no longer valid time when cold load pickup is considered. | String
7331 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSTATE | Plan state | Enumeration
7332 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSTATIONID | ID of the substation the optimization plan is associated with | String
7333 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANSTATIONNAME | Name of the substation the optimization plan is associated with | String
7334 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | PLANSW | Pointer to the switch associated with the plan | String
7335 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANTRIGGERINGCOMPID | ID of the component that triggered the plan solution | String
7336 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PLANTYPE | Type of the plan, such as FISR Loss of Voltage or AFR Overload | Enumeration
7337 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANVALIDDURATION | The estimated time period after the outage, after which overloads caused by CLPU occur, in hours. Applicable only when CLPU is considered for reconfiguration applications. | String
7338 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANVALIDENDTIME | Time when the plan is considered no longer valid | String
7339 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLANVOLTIMBGEONAME | Geometry name of the location of the device with the maximum regulator group voltage imbalance after the LVM plan. | String
7340 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLOSSPRE | Real power losses before the plan execution (AFR) | Integer
7341 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PLOSSPST | Real power losses after the plan execution (AFR) | Integer
7342 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PREDUCTION | Total change in real power demand (kW) | Float
7343 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PREPLANDEENERGIZEDKW | Total real power de-energized at the peak evaluation time, without CLPU effect, in kW | String
7344 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | PREPLANDEENERGIZEDKWCLPU | Total real power de-energized at the peak evaluation time, with CLPU effect, in kW. Applicable only when CLPU is considered for reconfiguration applications | String
7345 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PRIORITYCMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) with priority | Integer
7346 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PROTECTIONMARGINPI | Weight of the protection margin performance index | Float
7347 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PROTECTIONPI | Weight of performance index for the final step execution of the Protection Validation function | Integer
7348 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PROTECTIONREACHPI | Weight of protection reach performance index | Float
7349 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PROTVAL | Protection validation | String
7350 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PRVSTATUS | PRV status | String
7351 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | PRVSTATUSCODE | Reconfiguration plan PRV status (text name or code) | String
7352 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | QREDUCTION | Total change in reactive power demand (kVAR) | Float
7353 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | RADIALFINAL | A flag indicating that the final switching state is radial | Boolean
7354 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | RADIALPI | Weight for the final step radial condition performance index | Integer
7355 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | RADIALTEMPPI | Weight for the intermediate step radial condition performance index | Integer
7356 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | RECONFIGAPPNAME | Name of the reconfigurable application | String
7357 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REENERGIZEDDERGENP | Real power of generators and DERs re-energized by the switching plan, in kW. These objects will not run or contribute power during intermediate steps | Float
7358 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REENERGIZEDDERGENQ | Reactive power of generators and DERs re-energized by the switching plan, in kVAR. These objects will not run or contribute power during intermediate steps | Float
7359 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REENERGIZEDLOADGENP | Real power of embedded generation re-energized by the switching plan, in kW. These objects will not run or contribute power during intermediate steps | Float
7360 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | REENERGIZEDLOADGENQ | Reactive power of embedded generation re-energized by the switching plan, in kVAR. These objects will not run or contribute power during intermediate steps | Float
7361 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | input | REVERSEFLOWTHROUGHNONREVERSIBLEDEVICEPI | Reverse flow through non-reversible breakers/reclosers performance index | String
7362 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | REVNUPRE | Revenue before the plan execution | Integer
7363 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | REVNUPST | Revenue after the plan execution | Integer
7364 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIDIPI | Weight of the performance index for the final step System Average Interruption Duration Index (SAIDI) | Integer
7365 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIDIPOSTPLAN | Post-plan SAIDI value | Integer
7366 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIDIPREPLAN | Pre-plan SAIDI value | Integer
7367 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIFIPI | Weight of the performance index for the final step System Average Interruption Frequency Index (SAIFI) | Integer
7368 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIFIPOSTPLAN | Post-plan SAIFI value | Integer
7369 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SAIFIPREPLAN | Pre-plan SAIFI value | Integer
7370 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SECONDRATINGVIOLATIONS | A flag indicating that the second (emergency) ratings were violated at some point in the course of this plan | Boolean
7371 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWAFRPLAN | Shows "True" for AFR plans | String
7372 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWFISRCAPLAN | Shows "True" for FISRCA plans | String
7373 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWFISRPLAN | Shows "True" for FISR plans | String
7374 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWLVMPLAN | Shows "True" for LVM plans | String
7375 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWOPTCONTROLPLAN | Shows "True" for advanced application plans | String
7376 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SHOWPLORSPLAN | A flag to show PLOS plans | Boolean
7377 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SOLUTIONEVALTIME_TICKS | Time of the latest solution evaluation in ticks | String
7378 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SOLUTIONEXETIME_TICKS | Time of the latest solution execution in ticks | String
7379 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SOLUTIONID | ID of the DNAF solution | String
7380 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONOUTAGETIME | Outage time calculated by the system | String
7381 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SOLUTIONPLANTYPE | Control plan type and evaluation status (for example, FISR Fault - Eligible Execution Plan) | String
7382 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | STDCBPRE | Initial common tap changer bus standard deviation | Integer
7383 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | STDCBPST | Final (post plan) common tap changer bus standard deviation | Integer
7384 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKFERRORESONANCE | The state of the ferroresonance switching validation check | String
7385 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKFERRORESONANCEPI | Ferroresonance switching validation check weighted performance index | Float
7386 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKGROUNDEDLOADNEUTRAL | The state of the 3-Wire/4-Wire switching validation check | String
7387 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKGROUNDEDLOADNEUTRALPI | 3-Wire/4-Wire switching validation check weighted performance index | Float
7388 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKPARALLELCIRCUIT | The state of the paralleling circuits switching validation check | String
7389 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKPARALLELCIRCUITPI | Paralleling circuits switching validation check weighted performance index | Float
7390 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKSTATE | The state of the switching validation check | String
7391 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | SWITCHINGVALIDATIONCHECKVISIBILITYCONDITION | A flag indicating switching validation check status | Boolean
7392 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | TFFINALPF | Final power transformer power factor | Float
7393 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | TFINITPF | Initial power transformer power factor | Float
7394 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | TOTALPI | Total performance index | Integer
7395 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VOLTPI | Weight of the final step bus voltage violations performance index | Integer
7396 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VOLTTEMPPI | Weight of the intermediate step bus voltage violations performance index | Integer
7397 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCFINALLOSS | Post-plan active and reactive power losses | String
7398 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCFINALLOSSP | LVM post-plan real power losses | String
7399 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCFINALLOSSQ | LVM post-plan reactive power losses | String
7400 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCFLOWLIMITS | The flow violation limits strategy used in LVM | String
7401 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCINITIALLOSS | Pre-plan active and reactive power losses | String
7402 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCINITIALLOSSP | LVM pre-plan real power losses | String
7403 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCINITIALLOSSQ | LVM pre-plan reactive power losses | String
7404 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | VVCMAXTARGETPF | Maximum power factor target for station from manual overrride or from schedule | Float
7405 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCMAXTARGETPFFORCE | LVM maximum target power force | String
7406 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | VVCMINTARGETPF | Minimum power factor target for station from manual overrride or from schedule | Float
7407 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCMINTARGETPFFORCE | LVM minimum target power force | String
7408 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCPROBFORM | The name of LVM problem formulation | String
7409 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCSTATGROUP | The name of substation group | String
7410 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN |  | VVCVOLTLIMITS | The voltage violation limits strategy used in LVM | String
7411 | DNOM Component | Optimization Control Plan | OPTCONTROLPLAN | input | FSDEXECUTIONSTATE | FSD Stage 1 execution status | String
7412 | DNOM Component | Optimization Control Plan | OPTCONTROLPLAN | output | PLANFULLRESTORATION | Indicates whether this is a full restoration plan. The value is False for partial restoration plans (plans, which were solved for a part of the faulted sections) and reduced restoration plans (plans, which do not restore sections where violations appear or made worse by the plan). | Boolean
7413 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEVSUBNAME | For FISR permanent fault only, station name for the first tripped device | String
7414 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEVID | For FISR permanent fault only, device id for the first tripped device | String
7415 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEVNAME | For FISR permanent fault only, device name for the first tripped device | String
7416 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEVTYPE | For FISR permanent fault only, device type for the first tripped device | String
7417 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEVOPTIME_TICKS | For FISR permanent fault only, operating time, in ticks, for the first tripped device | String
7418 | DNAF Object | Optimization Control Plan | OPTCONTROLPLAN | output | SOLUTIONINITIATINGDEV | For FISR permanent fault only, formatted string "<station name> <device type> <device name>" for the first tripped device | String
7419 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONACTUALVALUE | Actual value for comparison with the limit value for the violation | String
7420 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONCONSTRVIOL | Violation type (Violation or Constraint). | String
7421 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONDEVICETYPE | The type of the object the violation is associated with | String
7422 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONFEEDER | Feeder that the violation is associated with | String
7423 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONGEOID | Geometry ID | String
7424 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONGEONAME | Geometry name (for example, DETAIL) | String
7425 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONISPREPLAN | Boolean flag indicating whether the violation exists pre plan implementation | String
7426 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONLIMITABLEOBJECTID | The ID of the object the limit is attached to | String
7427 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONLIMITPHASING | Phasing of the limit for the violation | String
7428 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONLIMITTYPE | Limit type for the violation | String
7429 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONLIMITVALUE | Limit value for the violation | String
7430 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONMAXSENSCONTROL | LVM control type with the greatest sensitivity on the violation (for example, Capacitor or Generator Power Factor) | String
7431 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONMAXSENSDEV | ID of the LVM plan device with the greatest sensitivity on the violation | String
7432 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONMAXSENSVALUE | The difference between the actual value and the limit value for the device with the greatest sensitivity on the violation (in 120 V base) | String
7433 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONOVERLOAD | Percentage of the actual value with respect to the limit value | String
7434 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONPLANID | The ID of the plan the violation is attached to | String
7435 | DNAF Object | Optimization Control Plan Violation | OPTCONTROLPLANVIOLATION |  | LVMVIOLATIONSUBNAME | Substation name of the object the limit is attached to | String
7436 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | DAENABLEDFEEDERS | Optimization enabled feeders | String
7437 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | DNAFDCEVERSION | The version number of DNAF parameters file | String
7438 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | DNAFLASTMODIFIED | The last modified date of DNAF parameters file | String
7439 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | DNAFREVISIONNUM | The revision number of DNAF parameter file | String
7440 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | ELIGIBLESWLIST | List of eligible switches | String
7441 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | FISRCASUBNAME | Name of the substation the FISRCA is associated with | String
7442 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | LVMENABLEDFEEDERS | LVM enabled feeders | String
7443 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | NETSELFEEDERLIST | Feeders considered for involvement in this solution | String
7444 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | NUMCUSTNOTRESTORED | Number of customers not restored outside of the faulted switchable section | Integer
7445 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | NUMFISRCAPLAN | Number of FISRCA plans available | Integer
7446 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | NUMPLANSINSOLUTION | Number of plans | String
7447 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | PLANLIFE | Time period for the plans to live. Plans that exist longer than this period are deleted. | Integer |  | seconds | seconds
7448 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SHOWAFRSOLUTION | A flag to show AFR solution | Boolean
7449 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SHOWFISRCASOLUTION | A flag to show FISRCA solution | Boolean
7450 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SHOWFISRSOLUTION | A flag to show FISR solution | Boolean
7451 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SHOWPLORSSOLUTION | A flag to show PLOS solution | Boolean
7452 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONCOMPLETION | Solution completion time | String
7453 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONCOMPLETION_TICKS | Time of the latest solution completion | String
7454 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONEVALTIME | Solution evaluation time | String
7455 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONEVALTIME_TICKS | Time of the latest solution evaluation | String
7456 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONEXETIME | Solution execution time | String
7457 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONEXETIME_TICKS | Time of the latest solution execution | String
7458 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONID | ID of the solution | String
7459 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONPEAKEVALTIME | Peak solution evaluation time | String
7460 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONPEAKEVALTIME_TICKS | Time of the latest peak solution evaluation | String
7461 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONSUBID | ID of the substation that is associated with the solution | String
7462 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONSUBNAME | Name of the substation the solution is associated with | String
7463 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONTYPE | Solution (aplication) type | Enumeration
7464 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONUSEDPROBFORMS | Problem formulations used in the solution | String
7465 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | TOTALNUMCUSTNOTRESTORED | Total number of customers not restored | Integer
7466 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | FISRSTATUS | FISR solution status | String
7467 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | FISRPLANAVAILABLE | Indicates whether FISR plan is available | Boolean
7468 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEVSUBNAME | For FISR permanent fault only, station name for the first tripped device | String
7469 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEVID | For FISR permanent fault only, device id for the first tripped device | String
7470 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEVNAME | For FISR permanent fault only, device name for the first tripped device | String
7471 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEVTYPE | For FISR permanent fault only, device type for the first tripped device | String
7472 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEVOPTIME_TICKS | For FISR permanent fault only, operating time, in ticks, for the first tripped device | String
7473 | DNAF Object | Optimization Control Solution | OPTCONTROLSOL | output | SOLUTIONINITIATINGDEV | For FISR permanent fault only, formatted string "<station name> <device type> <device name>" for the first tripped device | String
7474 | Virtual Object | Optimization Device | OPTDEVICE | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
7475 | Virtual Object | Optimization Device | OPTDEVICE | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
7476 | Virtual Object | Optimization Device | OPTDEVICE |  | CANCHOOSEOPTMULTIPLE | Specifies whether an optimization mode (On/Off) can be selected for multiple devices of the specified device's type for a device's feeder or substation | Boolean
7477 | Virtual Object | Optimization Device | OPTDEVICE |  | CANCHOOSEOPTSCADADECIDEMULTIPLE | Specifies whether an optimization mode (On/Off) can be selected for multiple devices of the specified device's type for a device's feeder or substation | Boolean
7478 | Virtual Object | Optimization Device | OPTDEVICE |  | CANCHOOSEOPTOFF | Optimization can not be enabled | String
7479 | Virtual Object | Optimization Device | OPTDEVICE |  | CANCHOOSEOPTON | Optimization can be enabled | String
7480 | Virtual Object | Optimization Device | OPTDEVICE |  | CANCHOOSEOPTSCADADECIDE | Optimization is SCADA decide | String
7481 | Virtual Object | Optimization Device | OPTDEVICE | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
7482 | Virtual Object | Optimization Device | OPTDEVICE | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
7483 | Virtual Object | Optimization Device | OPTDEVICE | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
7484 | Virtual Object | Optimization Device | OPTDEVICE | input | DSOTAPCONTROLENABLED | The enable status of tap changer. | String
7485 | Virtual Object | Optimization Device | OPTDEVICE | input | ID | Object unique ID | String |  |  |  | DNMOBJ
7486 | Virtual Object | Optimization Device | OPTDEVICE |  | ISLVMCONTROLDEV | If the device is LVM controllable device. | Boolean
7487 | Virtual Object | Optimization Device | OPTDEVICE | output | ISOPTDEVICEDSOELIGIBLE | If the device is eligible for control at the current time. | Boolean
7488 | Virtual Object | Optimization Device | OPTDEVICE | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
7489 | Virtual Object | Optimization Device | OPTDEVICE | output | MANUALEXCLUSIONFLAG | Specifies whether the device is manually excluded for LVM | Boolean
7490 | Virtual Object | Optimization Device | OPTDEVICE | output | MANUALEXCLUSIONFLAGTIME | The timestamp of the manual exclusion) | String
7491 | Virtual Object | Optimization Device | OPTDEVICE | input | NAME | Object name | String |  |  |  | DNMOBJ
7492 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTAUTOMANUAL | Auto/Manual status measurement and measurement quality | String
7493 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTAUTOMANUALQUAL | Auto/Manual status measurement quality | String
7494 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTCONTROLAVAIL | Control Available status measurement and measurement quality | String
7495 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTCONTROLAVAILQUAL | Control Available status measurement quality | String
7496 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTCURMEASSTATUS | Current status of the step measurement and measurement quality | String
7497 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTCURQUALITY | Current measurement quality | String
7498 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTCURRENTOPERATIONMODE | Current operation mode | String
7499 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTCURSTATUS | Current (final) step for powerflow solution | Integer
7500 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTDEVHASREMOTE | If the device has remote control. | Boolean
7501 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTDEVHASREMOTELOCAL | If the device has remote and local control. | Boolean
7502 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEENERGIZINGFEEDER | The name of the dynamic (currently energizing) feeder | String
7503 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONREASONS | The LVM exclusion reason codes | String
7504 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONREASONSDESC | The LVM exclusion reason description | String
7505 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONREASONSDESCFULL | Comma-separated descriptions of all LVM exclusion reasons that apply to the device | String
7506 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONREASONSNUM | The number of LVM device exclusion reasons that apply to the device | Integer
7507 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONTAGS | The type of each tag placed on the device. | String
7508 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEEXCLUSIONTIME | The timestamp of the control failure exclusion | String
7509 | Virtual Object | Optimization Device | OPTDEVICE | output | OPTDEVICEHASEXCLUSION | Specifies whether the device is currently excluded for LVM | Boolean
7510 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTDSOCONTROLENABLED | The enable status of shunt impedance/tap changer. | String
7511 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTDSOELIGIBLE | If the capacitor/tap changer is eligible for control at the current time. | Boolean
7512 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTELIGIBLEREASON | Reason indicates for the reason why the device is not eligible control. | String
7513 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTISREMOTE | If the current operation mode of the device is remote. | Boolean
7514 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTMANDSOELIGIBLE | DSO eligible state. | Integer
7515 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTMANDSOSCADADECIDE | If the enable status of shunt impedance/tap changer is decided by scada side. | Boolean
7516 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTMANDSOVISIBLE | Optimization eligibility manual visible | Boolean
7517 | Virtual Object | Optimization Device | OPTDEVICE | input | OPTMANUSERDSOENABLED | If the enable status of shunt impedance/tap changer is decided by user side. | Boolean
7518 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTPREVENTTAG | Prevent operation tags | String
7519 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTREMOTELOCAL | Remote/Local status measurement and measurement quality | String
7520 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTREMOTELOCALQUAL | Remote/Local status measurement quality | String
7521 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTSUPERCUTOUTQUAL | Supervisory Cutout status measurement quality | String
7522 | Virtual Object | Optimization Device | OPTDEVICE |  | OPTSUPERVISORYCUTOUT | Supervisory Cutout status measurement and measurement quality | String
7523 | Virtual Object | Optimization Device | OPTDEVICE |  | REMOTE | Remote status | String
7524 | Virtual Object | Optimization Device | OPTDEVICE | output | SUSPECTCONTROL | Does the device has suspect control(s) | Boolean
7525 | Virtual Object | Optimization Device | OPTDEVICE |  | SUSPECTCONTTYPE | Suspect control type | String
7526 | Virtual Object | Optimization Device | OPTDEVICE |  | SUSPECTDEVICETYPE | Suspect device type | String
7527 | Virtual Object | Optimization Device | OPTDEVICE | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
7528 | Virtual Object | Optimization Device | OPTDEVICE | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
7529 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
7530 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | COMPINSIDECONTAINER | Is device contained either inside station, vault or cabinet | String
7531 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | INSIDECABINET | Is device contained in cabinet | String
7532 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | INSIDECONTAINER | Is device contained either in UI container or cabinet, or vault | String
7533 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | INSIDEUICONTAINER | Is device contained in UI container | String
7534 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | INSIDEVAULT | Is device contained in vault | String
7535 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | OSMDEVADDRESS | OSM device address. | String
7536 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | OSMDEVFEEDID | OSM device dynamic feeder ID. | String
7537 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | OSMDEVFEEDNAME | OSM device dynamic feeder name. | String
7538 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
7539 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
7540 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
7541 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
7542 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
7543 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
7544 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
7545 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
7546 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
7547 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
7548 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | OSMDEVNOMVOLT | OSM device nominal voltage level voltage (line to neutral,kV) | Float
7549 | Virtual Object | OSM Specific Device | OSMQUERYDEVICE | input | OSMSWSERVCNTRFILTER | If the service center matches the string,the string remain unchanged, else the string will be wiped out. | String
7550 | DNOM Component | Outage Report | OUTREP |  | COMMENT | Operator comments | String
7551 | DNOM Component | Outage Report | OUTREP |  | EQUIPMNT | Equipment involved in the outage | String
7552 | DNOM Component | Outage Report | OUTREP |  | SWORDNUM | Switch order number | String
7553 | DNOM Component Placement | Placement Object | PLACE | input | BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer
7554 | DNOM Component Placement | Placement Object | PLACE | input | GEOMETRY | Pointer to associated geometry | String
7555 | DNOM Component Placement | Placement Object | PLACE | input | GSCOMPALTNAME | Alternate name of the component | String
7556 | DNOM Component Placement | Placement Object | PLACE | input | GSCOMPGEOMNAME | Name of the geometry | String
7557 | DNOM Component Placement | Placement Object | PLACE | input | GSCOMPID | ID of the component | String
7558 | DNOM Component Placement | Placement Object | PLACE | input | GSCOMPNAME | Name of the component | String
7559 | DNOM Component Placement | Placement Object | PLACE | input | GSSTATIONNAME | Name of the substation | String
7560 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAGROUNDBOLTEDFAULTCURRENT | The ground short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a zero fault impedance | Float | PRV | Amps | Amps
7561 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAGROUNDIMPEDANCEFAULTCURRENT | The ground short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
7562 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAGROUNDPICKUPRATIOSBOLTED | The ratio of the minimum ground pick-up current (multiplied by a safety factor) to the minimum ground fault current evaluated with a zero-fault impedance in percentage | Float | PRV | % | %
7563 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAGROUNDPICKUPRATIOSUSERCONFIGURED | The ratio of the minimum ground pick-up current (multiplied by a safety factor) to the minimum ground fault current evaluated with a user configured fault impedance in percentage. | Float | PRV | % | %
7564 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAGROUNDPICKUPVIOLATION | Indicator that the minimum ground fault current is less than the minimum pick-up current of the ground fault relay | Boolean
7565 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAMAXBOLTEDFAULTCURRENT | The maximum short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a zero fault impedance | Float | PRV | Amps | Amps
7566 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMAXCAPRATIOSBOLTED | The ratio of the maximum calculated fault current evaluated with a zero-fault impedance to the maximum interruption current of the switch, in percentage. | Float | PRV | % | %
7567 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMAXCAPRATIOSUSERCONFIGURED | The ratio of the maximum calculated fault current evaluated with a user configured fault impedance to the maximum interruption current of the switch, in percentage. | Float | PRV | % | %
7568 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAMAXIMPEDANCEFAULTCURRENT | The maximum short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
7569 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMAXINTERRUPTVIOLATION | Indicator that the calculated maximum fault current exceeds the capacity of the switch | String
7570 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANBOUNDEDSELFPROTECTEDTFNAME | Shows the name of the bounding self-protected power transformer. If the device name is not provided, it will show the device Id. | String
7571 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANBOUNDEDSELFPROTECTEDTFID | The ID of the bounding self-protected power transformer. | String
7572 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANBOUNDEDSELFPROTECTEDTFSUBNAME | The substation name that the bounding self-protected power transformer belongs to. | String
7573 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | OBJGEOMETRYNAMEPLANBOUNDEDSELFPROTECTEDTF | Geometry name for self-protected transformer from latest PRV calculation. | String
7574 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINGROUNDFAULTLOCATION | Minimum ground fault current location | String
7575 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINGROUNDFAULTSUBNAME | Name of the substation the device with the minimum ground fault belongs to | String
7576 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINGROUNDFAULTTYPE | Minimum ground fault fault type | String
7577 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINPHASEFAULTLOCATION | Minimum phase fault current location | String
7578 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINGRDFLTLOCHASPLACEMENT | Specifies whether a switch has placement (for the Minimum Ground Pick-Up Results display) | Boolean | PRV
7579 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINGRDFLTLOCISGEOGRAPHIC | Specifies whether the fault location is in the geographic view (for the Minimum Ground Pick-Up Results display) | Boolean | PRV
7580 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINPHSFLTLOCHASPLACEMENT | Specifies whether a switch has placement (for the Minimum Phase Pick-Up Results display) | Boolean | PRV
7581 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINPHSFLTLOCISGEOGRAPHIC | Specifies whether the fault location is in the geographic view (for the Minimum Phase Pick-Up Results display) | Boolean | PRV
7582 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAMINPHASEFAULTSUBNAME | Name of the substation the device with the minimum phase fault belongs to | String
7583 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAPEAKLOADVIOLATION | Indicator that there is peak load violation | Boolean
7584 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAPHASEFAULTSENSITIVITYBOLTED | The ratio of the minimum phase fault current evaluated with a zero-fault impedance to the minimum phase pick-up current (multiplied by a safety factor). | Float | PRV | % | %
7585 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAPHASEFAULTSENSITIVITYUSERCONFIGURED | The ratio of the minimum phase fault current evaluated with a user configured fault impedance to the minimum phase pick-up current (multiplied by a safety factor). | Float | PRV | % | %
7586 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAPHASEFBOLTEDAULTCURRENT | The phase short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a zero fault impedance | Float | PRV | Amps | Amps
7587 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAPHASEIMPEDANCEFAULTCURRENT | The phase short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
7588 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAPHASEPICKUPRATIOSBOLTED | The ratio of the minimum phase pick-up current (multiplied by a safety factor) to the minimum phase fault current evaluated with a zero-fault impedance in percentage. | Float | PRV | % | %
7589 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAPHASEPICKUPRATIOSUSERCONFIGURED | The ratio of the minimum phase pick-up current (multiplied by a safety factor) to the minimum phase fault current evaluated with a user configured fault impedance in percentage. | Float | PRV | % | %
7590 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFAPHASEPICKUPVIOLATION | Indicator that the minimum calculated fault current is less than the minimum pick-up current of the protection relay | String
7591 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFASWSUBNAME | Name of the substation the switch belongs to | String
7592 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAULTIMPEDANCEBOLTED | The bolted fault impedance (zero-fault impedance) in R + jX ohm. | Float | PRV | R + jX ohm | R + jX ohm
7593 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAULTIMPEDANCEUSERCONFIGURED | The user-configured fault impedance in R + jX ohm. | Float | PRV | R + jX ohm | R + jX ohm
7594 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAULTIMPEDANCEEVALUATIONTYPE | Fault impedance evaluation type (Bolted Fault or User Configured Impedance). | Float | PRV | Amps | Amps
7595 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANFUNCID | Plan function ID | String
7596 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANNEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
7597 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT | output | PLANNEXCPTNEUCURRTSORT | The highest neutral relay current in the breaker and recloser in percent | Float | PRV | percent | percent
7598 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANSTATIONNAME | Name of the substation associated with the plan | String
7599 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANSWID | ID of the switch | String
7600 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANSWNEUTRALSETTING | Neutral relay current trip setting in Amps | Float | PRV | Amps | Amps
7601 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANSWNEUCURRENTAMPS | Neutral relay current in Amps | Float | PRV | Amps | Amps
7602 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | PLANSWSECONDID | Second ID of the switch | String
7603 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | SWCLOSEDPHASES | Switch's phases in the Closed state | String
7604 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | SWCURRENTPOSITION | Current position of the switch | String
7605 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | SWITCHMODE | The current mode of the switch (Switch, Recloser, Sectionalizer, or None.) | String
7606 | DNAF Object | Plan Fault Analysis Result | PLANFARESULT |  | SWOPENPHASES | Switch's phases in the Open state | String
7607 | DNOM Component | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAGROUNDFAULTSENSITIVITYBOLTED | The ratio of the minimum ground fault current evaluated with a zero-fault impedance to the minimum ground pick-up current (multiplied by a safety factor). | Float | PRV | % | %
7608 | DNOM Component | Plan Fault Analysis Result | PLANFARESULT | output | PLANFAGROUNDFAULTSENSITIVITYUSERCONFIGURED | The ratio of the minimum ground fault current evaluated with a user configured fault impedance to the minimum ground pick-up current (multiplied by a safety factor). | Float | PRV | % | %
7609 | DNAF Object | Plan Measurement Island Result | PLANMEASISLANDRESULT | output | PLANBLAISLANDCONVERGEDP | A string indicating if the real power converges for the measurement island involved in a plan (Yes, No, or --) | String
7610 | DNAF Object | Plan Measurement Island Result | PLANMEASISLANDRESULT | output | PLANBLAISLANDCONVERGEDQ | A string indicating if the reactive power converges for the measurement island involved in a plan (Yes, No, or --) | String
7611 | DNAF Object | Plan Measurement Island Result | PLANMEASISLANDRESULT | output | PLANBLAISLANDCONVERGEDS | A string indicating if the apparent power converges for the measurement island involved in a plan (Yes, No, or --) | String
7612 | DNAF Object | Plan Measurement Island Result | PLANMEASISLANDRESULT | output | PLANBLAISLANDLOADALLOCTYPE | A string indicating the BLA load allocation type for the measurement island involved in a plan (kW & kVAR, kVA, Amp & PF, No Allocation, Error: Undefined) | String
7613 | DNAF Object | Plan Measurement Island Result | PLANMEASISLANDRESULT | output | PLANFUNCID | Plan function ID | String
7614 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | PLANFUNCID | Plan function ID | String
7615 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | PLANSTATIONNAME | Name of the substation the associated plan belongs to. | String
7616 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERAMMEAS | The Auto/Manual measurement value. | String
7617 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERBLOCKEDMEAS | The Blocked measurement value. | String
7618 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERCONTROLTYPE | The control method used for the device (for example, Raise/Lower). | String
7619 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERAPPLIEDREGLOGIC | The tap changer regulation logic (Fixed or Regulating) | String
7620 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERCTRATIO | Regulating tap CT ratio. | Float
7621 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERDEVICETYPE | The transformer type. | String
7622 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERFINALTAPPOS | Post-plan final tap position. | Integer
7623 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERID | Tap changer ID. | String
7624 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERINITIALTAPPOS | Initial tap position. | Integer
7625 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERNAME | The associated transformer name. | String
7626 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERNOMINALFEEDER | Nominal feeder. | String
7627 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERNOMINALSTATION | Nominal substation. | String
7628 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERNOMINALVOLT | Nominal voltage. | Float |  | V | V
7629 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTA | Post-plan phase A voltage (per unit). | Float |  | p.u. | p.u.
7630 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTB | Post-plan phase B voltage (per unit). | Float |  | p.u. | p.u.
7631 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTC | Post-plan phase C voltage (per unit). | Float |  | p.u. | p.u.
7632 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTTARGET | Effective voltage target (per unit). | Float |  | p.u. | p.u.
7633 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTTARGETMAX | Effective voltage target maximum (per unit). | Float |  | p.u. | p.u.
7634 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPOSTPLANVOLTTARGETMIN | Effective voltage target minimum (per unit). | Float |  | p.u. | p.u.
7635 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERPTRATIO | Regulating transformer PT ratio. | Float
7636 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERRATEDVOLT | Voltage specified on the nameplate. | Float |  | V | V
7637 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERREGULATIONDIRECTION | Regulation direction. | String
7638 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERREGULATIONMODE | The name of the regulation mode. | String
7639 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERREGULATIONMODENAME | The name of the network node that is used as the sensing point for voltage regulation by the controller. | String
7640 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERREGULATIONNODEID | The ID of the network node that is used as the sensing point for voltage regulation by the controller. | String
7641 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERREVOLTREDUCTION | The voltage reduction percentage. | Float |  | % | %
7642 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERRLMMEAS | The Remote/Local measurement value. | String
7643 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERTAPBANDWIDTH | The regulation voltage bandwidth in Volts. | Float |  | V | V
7644 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERTAPLDCR | The LDC resistance in Volts. | Float |  | V | V
7645 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERTAPLDCX | The LDC reactance in Volts. | Float |  | V | V
7646 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERTAPVOLTTARGET | Voltage targed in Volts. | Float |  | V | V
7647 | DNAF Object | Plan Tap Changer Result | PLANTAPCHANGERRESULT | output | TAPCHANGERWINDING | The transformer winding. | String
7648 | DNOM Component | Primary Bus | PRIMBS | input | ADDRESSAREANAME | Associated area name | String |  |  |  | SUB
7649 | DNOM Component | Primary Bus | PRIMBS | input | AFRCLOSEDLOOPDNAFENABLEDAPPS | DNAF enabled applications bitmask | Integer |  |  |  | SUB
7650 | DNOM Component | Primary Bus | PRIMBS | input | AFRPROFORMINDEXFISRPROFORMINDEX | Number of FISR problem formulation indices | Integer |  |  |  | SUB
7651 | DNOM Component | Primary Bus | PRIMBS | input | ALTNAMEISSUBFED | Flag indicating if it is subFed station support | Boolean |  |  |  | SUB
7652 | DNOM Component | Primary Bus | PRIMBS | input | AREANAMEPAREANME | Associated permission area name | String |  |  |  | SUB
7653 | DNOM Component | Primary Bus | PRIMBS | input | BLKREGVREDSTAT | Voltage reduction flag | Boolean |  |  |  | SUB
7654 | DNOM Component | Primary Bus | PRIMBS | input | BUSMANCOUNTLINEMANCOUNT | Number of line manual inputs | Integer |  |  |  | SUB
7655 | DNOM Component | Primary Bus | PRIMBS | input | CAPMANCOUNTTAPMANCOUNT | Number of tap changer manual inputs | Integer |  |  |  | SUB
7656 | DNOM Component | Primary Bus | PRIMBS | input | DESCRIPTALTNAME | Alternate name | String |  |  |  | SUB
7657 | DNOM Component | Primary Bus | PRIMBS | input | DISTTFMANCOUNTLOADMANCOUNT | Number of load manual inputs | Integer |  |  |  | SUB
7658 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDAFALARMSDNAFENABLEDVVALARMS | DNAF enabled LVM alarms bitmask | Integer |  |  |  | SUB
7659 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDAPPSDNAFENABLEDPFALARMS | DNAF enabled DPF alarms bitmask | Integer |  |  |  | SUB
7660 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDFIALARMSDNAFENABLEDAFALARMS | DNAF enabled AFR alarms bitmask | Integer |  |  |  | SUB
7661 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.ADDRESS | The feeder address | String |  |  |  | FDR
7662 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.ALTERNATENAME | Alternate name of the feeder | String |  |  |  | FDR
7663 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
7664 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
7665 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.DEFCOLOR | Default color | Integer |  |  |  | FDR
7666 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
7667 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
7668 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
7669 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
7670 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
7671 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
7672 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
7673 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
7674 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
7675 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
7676 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
7677 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
7678 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
7679 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
7680 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
7681 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
7682 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
7683 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
7684 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
7685 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
7686 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NAME | Name of the object | String |  |  |  | DNMOBJ
7687 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
7688 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
7689 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
7690 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String |  |  |  | FDR
7691 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
7692 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
7693 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
7694 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
7695 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDPFALARMSDNAFENABLEDPVALARMS | DNAF enabled PV alarms bitmask | Integer |  |  |  | SUB
7696 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDPVALARMSDNAFENABLEDFIALARMS | DNAF enabled FISR alarms bitmask | Integer |  |  |  | SUB
7697 | DNOM Component | Primary Bus | PRIMBS | input | DNAFENABLEDVVALARMSLVMPROFORMINDEX | Number of LVM problem formulation indices | Integer |  |  |  | SUB
7698 | DNOM Component | Primary Bus | PRIMBS | input | DNOMXDNOMY | Y coordinate | Float |  |  |  | DNMOBJ
7699 | DNOM Component | Primary Bus | PRIMBS | input | DNOMYAREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
7700 | DNOM Component | Primary Bus | PRIMBS | input | DUPTOPOBSCPOSSQR | Source positive sequence resistance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7701 | DNOM Component | Primary Bus | PRIMBS | input | DYNFEED | Pointer to the associated feeder | String
7702 | DNOM Component | Primary Bus | PRIMBS | input | FAULTLOCATIONMANCOUNTSWITCHMANCOUNT | Number of switch manual inputs | Integer |  |  |  | SUB
7703 | DNOM Component | Primary Bus | PRIMBS | input | FEEDERMANCOUNTREFERENCEBUSMANCOUNT | Number of reference bus manual inputs | Integer |  |  |  | SUB
7704 | DNOM Component | Primary Bus | PRIMBS | input | FISRCAPROFORMINDEXPLORSPROFORMINDEX | Number of PLOS problem formulation indices | Integer |  |  |  | SUB
7705 | DNOM Component | Primary Bus | PRIMBS | input | FISRCLOSEDLOOPAFRCLOSEDLOOP | Flag indicating that AFR is running in a closed loop mode | Boolean |  |  |  | SUB
7706 | DNOM Component | Primary Bus | PRIMBS | input | FISRLOSSVOLTPLANEXEC | Loss of voltage plan execution mode for FISR | Integer |  |  |  | SUB
7707 | DNOM Component | Primary Bus | PRIMBS | input | FISRPERMFAULTPLANEXEC | Permanent fault plan execution mode for FISR | Integer |  |  |  | SUB
7708 | DNOM Component | Primary Bus | PRIMBS | input | FISRPROFORMINDEXFISRCAPROFORMINDEX | Number of FISRCA problem formulation indices | Integer |  |  |  | SUB
7709 | DNOM Component | Primary Bus | PRIMBS | input | FUTUREDUPTOPOB | Flag indicating that the station has duplicate topology objects most likely due to multi-phase transformer bank fed from different stations | Boolean |  |  |  | SUB
7710 | DNOM Component | Primary Bus | PRIMBS | input | GENERATORMANCOUNTCAPMANCOUNT | Number of capacitor manual inputs | Integer |  |  |  | SUB
7711 | DNOM Component | Primary Bus | PRIMBS | input | HASNPID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
7712 | DNOM Component | Primary Bus | PRIMBS | input | IDNAME | Name of the object | String |  |  |  | DNMOBJ
7713 | DNOM Component | Primary Bus | PRIMBS | input | ISMBLSUBMBSUBXPS | Current x coordinate position | Integer |  |  |  | SUB
7714 | DNOM Component | Primary Bus | PRIMBS | input | ISSUBFEDNUMPOWTF | The number of power transformers | Integer |  |  |  | SUB
7715 | DNOM Component | Primary Bus | PRIMBS | input | ISTRNSSBLVMCLOSEDLOOP | Flag indicating that LVM is running in a closed loop mode | Boolean |  |  |  | SUB
7716 | DNOM Component | Primary Bus | PRIMBS | input | LINEMANCOUNTHASNP | Indicates if the station has network protectors | Boolean |  |  |  | SUB
7717 | DNOM Component | Primary Bus | PRIMBS | input | LOADCATMANCOUNTBUSMANCOUNT | Number of bus manual inputs | Integer |  |  |  | SUB
7718 | DNOM Component | Primary Bus | PRIMBS | input | LOADMANCOUNTLOADCATMANCOUNT | Number of load category manual inputs | Integer |  |  |  | SUB
7719 | DNOM Component | Primary Bus | PRIMBS | input | LSCALERBLKREG | Block regulators flag | Boolean |  |  |  | SUB
7720 | DNOM Component | Primary Bus | PRIMBS | input | LVMCLOSEDLOOPFISRCLOSEDLOOP | Flag indicating that FISR is running in a closed loop mode | Boolean |  |  |  | SUB
7721 | DNOM Component | Primary Bus | PRIMBS | input | LVMDASUPPORTMODESTATIONMANCOUNT | Number of station manual inputs | Integer |  |  |  | SUB
7722 | DNOM Component | Primary Bus | PRIMBS | input | LVMPLANEXEC | Plan execution mode for LVM | Integer |  |  |  | SUB
7723 | DNOM Component | Primary Bus | PRIMBS | input | LVMPLANEXECLVMDASUPPORTMODE | LVM is currently in Distribution Automation support mode (0 - none, 1 - FISR, 2 - AFR) | Integer |  |  |  | SUB
7724 | DNOM Component | Primary Bus | PRIMBS | input | LVMPROFORMINDEXAFRPROFORMINDEX | Number of AFR problem formulation indices | Integer |  |  |  | SUB
7725 | DNOM Component | Primary Bus | PRIMBS | input | MBGEOMNMSYMBTYPE | Station display type (normal, truck with batteries, or truck with a generator). This flag is non-zero for a mobile station. | Integer |  |  |  | SUB
7726 | DNOM Component | Primary Bus | PRIMBS | input | MBNEARSBMBGEOMNM | Name of the geometry that is adjusted for the mobile substation | String |  |  |  | SUB
7727 | DNOM Component | Primary Bus | PRIMBS | input | MBSUBXPSMBSUBYPS | Current y coordinate position | Integer |  |  |  | SUB
7728 | DNOM Component | Primary Bus | PRIMBS | input | MBSUBYPSMBNEARSB | Name of the nearest substation | String |  |  |  | SUB
7729 | DNOM Component | Primary Bus | PRIMBS | input | METUNITSLSCALER | Load scaling factor applied to all loads in the DPF | Float |  |  |  | SUB
7730 | DNOM Component | Primary Bus | PRIMBS | input | NAMEDNOMX | X coordinate | Float |  |  |  | DNMOBJ
7731 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
7732 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
7733 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
7734 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
7735 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.ID | ID of the node | String |  |  |  | DNMOBJ
7736 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
7737 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
7738 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
7739 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
7740 | DNOM Component | Primary Bus | PRIMBS |  | NUMFEED | Number of feeders | Integer
7741 | DNOM Component | Primary Bus | PRIMBS | input | NUMPOWTFTFINDEXS | Array of power transformer indexes (translated into pointers) | Integer |  |  |  | SUB
7742 | DNOM Component | Primary Bus | PRIMBS | input | NUMREGDTMETUNITS | Metric units flag used mainly in line model processing for impedance and admittance (true - metric, false - non-metric units) | Boolean |  |  |  | SUB
7743 | DNOM Component | Primary Bus | PRIMBS | input | PAREANMEDESCRIPT | Station description | String |  |  |  | SUB
7744 | DNOM Component | Primary Bus | PRIMBS | input | PAREANMEVALSTAT | Validation status for the station | Integer |  |  |  | SUB
7745 | DNOM Component | Primary Bus | PRIMBS | input | PLORSPROFORMINDEXFISRPERMFAULTPLANEXEC | Permanent fault plan execution mode for FISR | Integer |  |  |  | SUB
7746 | DNOM Component | Primary Bus | PRIMBS | input | PMNODE | Pointer to the primary node | String
7747 | DNOM Component | Primary Bus | PRIMBS | input | POWERTFMANCOUNTDISTTFMANCOUNT | Number of distribution transformer manual inputs | Integer |  |  |  | SUB
7748 | DNOM Component | Primary Bus | PRIMBS | input | REFERENCEBUSMANCOUNTGENERATORMANCOUNT | Number of generator manual inputs | Integer |  |  |  | SUB
7749 | DNOM Component | Primary Bus | PRIMBS | input | SCNEGSQRSCNEGSQX | Source negative sequence reactance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7750 | DNOM Component | Primary Bus | PRIMBS | input | SCNEGSQXSCZOSSQR | Source zero sequence resistance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7751 | DNOM Component | Primary Bus | PRIMBS | input | SCPOSSQRSCPOSSQX | Source positive sequence reactance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7752 | DNOM Component | Primary Bus | PRIMBS | input | SCPOSSQXSCNEGSQR | Source negative sequence resistance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7753 | DNOM Component | Primary Bus | PRIMBS | input | SCZOSSQRSCZOSSQX | Source zero sequence reactance (in ohms, for fault analysis) | Integer |  |  |  | SUB
7754 | DNOM Component | Primary Bus | PRIMBS | input | SUBS.ADDRESS | Substation address | String |  |  |  | SUB
7755 | DNOM Component | Primary Bus | PRIMBS | input | SCZOSSQXISMBLSUB | Flag indicating this is a mobile substation | Boolean |  |  |  | SUB
7756 | DNOM Component | Primary Bus | PRIMBS | input | SETFPSETFQ | State estimator values for power transformers | Integer |  | MVAR | MVAR | SUB
7757 | DNOM Component | Primary Bus | PRIMBS | input | SETFQNUMREGDT | The number of regular day types | Integer |  |  |  | SUB
7758 | DNOM Component | Primary Bus | PRIMBS | input | STATIONMANCOUNTFEEDERMANCOUNT | Number of feeder manual inputs | Integer |  |  |  | SUB
7759 | DNOM Component | Primary Bus | PRIMBS | input | SUBDNAFDISABLEDSUBDSODISABLED | A flag indicating that DSO for the substation is disabled | Boolean |  |  |  | SUB
7760 | DNOM Component | Primary Bus | PRIMBS | input | SUBDSODISABLEDFUTURE | A flag indicating that the station has future equipment flag (true - has future) | Boolean |  |  |  | SUB
7761 | DNOM Component | Primary Bus | PRIMBS | input | SUBS | Pointer to the associated substation | String
7762 | DNOM Component | Primary Bus | PRIMBS | input | SWITCHMANCOUNTPOWERTFMANCOUNT | Number of power transformer manual inputs | Integer |  |  |  | SUB
7763 | DNOM Component | Primary Bus | PRIMBS | input | SYMBTYPEISTRNSSB | Transmission only station flag (determined based on feeder count within the Converter) | Boolean |  |  |  | SUB
7764 | DNOM Component | Primary Bus | PRIMBS | input | TAPMANCOUNTFAULTLOCATIONMANCOUNT | Number of fault location manual inputs | Integer |  |  |  | SUB
7765 | DNOM Component | Primary Bus | PRIMBS | input | TFINDEXSSETFP | State estimator values for power transformers | Integer |  | MW | MW | SUB
7766 | DNOM Component | Primary Bus | PRIMBS | input | VALSTATPAREANME | Associated permission area name | String |  |  |  | SUB
7767 | DNOM Component | Primary Bus | PRIMBS | input | VREDSTATSUBDNAFDISABLED | A flag indicating that DNAF applications for the substation is disabled | Boolean |  |  |  | SUB
7768 | DNOM Component | Protection Setting | PROTSET |  | GROUNDTRIP | Ground trip current | Float
7769 | DNOM Component | Protection Setting | PROTSET |  | PHASETRIP | Phase trip current ( used if the setting is selected by phase trip level) | Float
7770 | DNOM Component | Protection Setting | PROTSET |  | SCADAINDEX | Index of the applicable SCADA measurement type (for control, enabling, setting, etc.). Can be 0-8, where 0 - unmapped) | Integer
7771 | DNOM Component | Protection Setting | PROTSET |  | SETTING | Name of the setting (e.g. S1) | String
7772 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | ASSOCSGT | The name of the associated settings group template | String
7773 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | ID | Settings group ID | String |  |  |  | DNMOBJ
7774 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | Name | Settings group name | String |  |  |  | DNMOBJ
7775 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SETTINGGRPMODE | Protection settings group mode, such as switch, recloser, sectionalizer, or custom. | String
7776 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG1TRANSITION | The settings group transition matrix for group 1, where 1 = allowed transition, and 0 = forbidden transition. For example, transition from settings group 3 to settings group 4 is allowed, and transition from settings group 3 to settings group 7 is forbidden. | String
7777 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG2TRANSITION | The settings group transition matrix for group 2. | String
7778 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG3TRANSITION | The settings group transition matrix for group 3. | String
7779 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG4TRANSITION | The settings group transition matrix for group 4. | String
7780 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG5TRANSITION | The settings group transition matrix for group 5. | String
7781 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG6TRANSITION | The settings group transition matrix for group 6. | String
7782 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG7TRANSITION | The settings group transition matrix for group 7. | String
7783 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SG8TRANSITION | The settings group transition matrix for group 8. | String
7784 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SGMODE | Settings group mode (unknown, switch, sectionalizer, recloser, or custom) | Integer
7785 | DNOM Component | Protection Settings Group | PROTSETGROUP | input | SGTRANSITION | Settings group possible transitions | Integer
7786 | DNOM Component | Protection Source | PROTSOURCE |  | SETTING | Name of the setting (e.g. S1) | String
7787 | DNOM Component | Protection Source | PROTSOURCE |  | SOURCEFEEDER | Supply feeder - used if setting is selected by source feeder | String
7788 | DNOM Component | Protection Source | PROTSOURCE |  | SOURCESUB | Supply substation - used if setting is selected by source substation | String
7789 | DNOM Component Placement | Point Placement | PTPLCE | input | ROTATION | Rotation anagle of the placement | Integer
7790 | DNOM Component Placement | Point Placement | PTPLCE | input | SIZE | Size of the object | Integer
7791 | DNOM Component Placement | Point Placement | PTPLCE | input | X | X coordinate of the placement | Float
7792 | DNOM Component Placement | Point Placement | PTPLCE | input | X2 | X coordinate as double data type coming from GIS. Has more precision compared to common X. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
7793 | DNOM Component Placement | Point Placement | PTPLCE | input | Y | Y coordinate of the placement | Float
7794 | DNOM Component Placement | Point Placement | PTPLCE | input | Y2 | Y coordinate as double data type coming from GIS. Has more precision compared to common Y. Currently this is only use by external interface. In future, it can be used to store secondary geomtery. | Double
7795 | DNOM Component Placement | Poly Placement | PYPLCE | input | AX | Dynamic array of X coordinates | Float
7796 | DNOM Component Placement | Poly Placement | PYPLCE | input | AX2 | Dynamic array of secondary X coordinates. Secondary X coordinate property type is "double" compared to a common X coordinate, which is "float". It has more precision. This is added for an external interface which needs more accurate coordinates. In uture, it can be used to store secondary geometry. | Double
7797 | DNOM Component Placement | Poly Placement | PYPLCE | input | AY | Dynamic array of Y coordinates | Float
7798 | DNOM Component Placement | Poly Placement | PYPLCE | input | AY2 | Dynamic array of secondary Y coordinates. Secondary Y coordinate property type is "double" compared to a common X coordinate, which is "float". It has more precision. This is added for an external interface which needs more accurate coordinates. In uture, it can be used to store secondary geometry. | Double
7799 | DNOM Component Placement | Poly Placement | PYPLCE | input | NUMVERT | Number of vertices (line or polygon) | Integer
7800 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN._KEY | The unique identifier to represent a device | String |  |  |  | OPTCONTROLPLAN
7801 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAFINALPF | Final area power factor after plan | Float |  |  |  | OPTCONTROLPLAN
7802 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAFINALREACTIVEDEMAND | Final (post plan) station reactive power demand | Float |  |  |  | OPTCONTROLPLAN
7803 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAFINALREALDEMAND | Final (post plan) station real power demand | Float |  |  |  | OPTCONTROLPLAN
7804 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAINITPF | Initial area power factor before plan | Float |  |  |  | OPTCONTROLPLAN
7805 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAINITREACTIVEDEMAND | Initial station reactive power demand | Integer |  |  |  | OPTCONTROLPLAN
7806 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.AREAINITREALDEMAND | Initial station real power demand | Integer |  |  |  | OPTCONTROLPLAN
7807 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CHANGEINREACTIVEDEMAND | Total change in reactive power demand | Integer |  | kVAR | kVAR | OPTCONTROLPLAN
7808 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CHANGEINREALDEMAND | Total change in real power demand | Integer |  | kW | kW | OPTCONTROLPLAN
7809 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) | Integer |  |  |  | OPTCONTROLPLAN
7810 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.COMMENT | Operator comment | String |  |  |  | OPTCONTROLPLAN
7811 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.COSTPI | Weight of the final step total cost performance index | Integer |  |  |  | OPTCONTROLPLAN
7812 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.COSTTEMPPI | Weight of the intermediate step total cost performance index | Integer |  |  |  | OPTCONTROLPLAN
7813 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CRITVOLT | Equalization of critical voltages (maximize TCUL tap range) | Integer |  |  |  | OPTCONTROLPLAN
7814 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CTVUSPRE | Value of uninterrupted service before the plan execution | Integer |  |  |  | OPTCONTROLPLAN
7815 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.CUSTVUS | Customer economic loss of value of uninterrupted service | Integer |  |  |  | OPTCONTROLPLAN
7816 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DNAFDCEVERSION | DCE parameters version | String |  |  |  | OPTCONTROLPLAN
7817 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DNAFLASTMODIFIED | DCE parameters' last modified date | String |  |  |  | OPTCONTROLPLAN
7818 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DNAFREVISIONNUM | DCE parameter revision number | String |  |  |  | OPTCONTROLPLAN
7819 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DROPPEDCUSTOMERCOUNTPI | Weight of the final step count of the dropped customers performance index | Integer |  |  |  | OPTCONTROLPLAN
7820 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DROPPEDCUSTOMERCOUNTTEMPPI | Weight of the intermediate step count of the dropped customers performance index | Integer |  |  |  | OPTCONTROLPLAN
7821 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DROPPEDPRIORITYPI | Weight of the final step dropped customer priority performance index | Integer |  |  |  | OPTCONTROLPLAN
7822 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DROPPEDPRIORITYTEMPPI | Weight of the intermediate step dropped customer priority performance index | Integer |  |  |  | OPTCONTROLPLAN
7823 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.DSOPLANSTATE | A string indicating the state of the control plan. 1.Bad 2.Good 3.Good-Neighbouring Violation 4.Good-Violation 5.Bad (LP_infeasible) 6.Bad (Power flow_Unsolved) 7. Request Stopped 8.Suspect 9.Invalid-Topology has Changed 10.Violation Detected-LVM Correction Available 11.Violation Detected-LVM Correction Not Available | String |  |  |  | OPTCONTROLPLAN
7824 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FAULTCOMP | Associated fault device ID | String |  |  |  | OPTCONTROLPLAN
7825 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FEEDERFINALPF | Final power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
7826 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FEEDERINITPF | Initial power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
7827 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FEEDERTARGETPF | Target power factor of the feeders | Float |  |  |  | OPTCONTROLPLAN
7828 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FINALACTIVELOSS | Final (post plan) real power losses | Integer |  |  |  | OPTCONTROLPLAN
7829 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FINALPFWITHINLIMIT | A flag indicating that the final (post plan) DPF was within the limit | Boolean |  |  |  | OPTCONTROLPLAN
7830 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FINALREACTIVELOSS | Final (post plan) reactive power losses | Integer |  |  |  | OPTCONTROLPLAN
7831 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FINALVOLTPI | Final (post plan) voltage performance index | Integer |  |  |  | OPTCONTROLPLAN
7832 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FINALWORSTVOVERLOAD | Highest overload value after the plan | Integer |  |  |  | OPTCONTROLPLAN
7833 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FISRCARESULTID | ID of the FISRCA result | String |  |  |  | OPTCONTROLPLAN
7834 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FISRCASOLUTIONID | ID of the FISRCA solution | String |  |  |  | OPTCONTROLPLAN
7835 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FLOWPI | Weight of the final step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
7836 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.FLOWTEMPPI | Weight of the intermediate step flow violations performance index | Integer |  |  |  | OPTCONTROLPLAN
7837 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INITACTIVELOSS | Initial real power losses | Integer |  |  |  | OPTCONTROLPLAN
7838 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INITPFWITHINLIMIT | A flag indicating that the initial DPF was within the limit | Boolean |  |  |  | OPTCONTROLPLAN
7839 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INITREACTIVELOSS | Initial reactive power losses | Integer |  |  |  | OPTCONTROLPLAN
7840 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INITVOLTPI | Initial voltage performance index | Integer |  |  |  | OPTCONTROLPLAN
7841 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INITWORSTVOVERLOAD | Highest overload value before the plan | Integer |  |  |  | OPTCONTROLPLAN
7842 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.INTVAL | Initial value | String |  |  |  | OPTCONTROLPLAN
7843 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.ISAFRPLAN | A flag indicating a AFR plan | Boolean |  |  |  | OPTCONTROLPLAN
7844 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.ISFISRPLAN | A flag indicating a FISR plan | Boolean |  |  |  | OPTCONTROLPLAN
7845 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.ISPLORSPLAN | A flag indicating a PLOS plan | Boolean |  |  |  | OPTCONTROLPLAN
7846 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.ISVVCPLAN | A flag indicating a LVM plan | Boolean |  |  |  | OPTCONTROLPLAN
7847 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.KWNTRST | Total real power not restored including faulted switchable sections | Integer |  | kW | kW | OPTCONTROLPLAN
7848 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.KWRSTORE | The restored real power | Integer |  | kW | kW | OPTCONTROLPLAN
7849 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.LMIPI | Weight of the performance index for Load Minutes Interruption (LMI) | Integer |  |  |  | OPTCONTROLPLAN
7850 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.LOSSESPI | Weight of the final step losses performance index | Integer |  |  |  | OPTCONTROLPLAN
7851 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.LOSTLOADPI | Weight of the final step lost load performance index | Integer |  |  |  | OPTCONTROLPLAN
7852 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.LOSTLOADTEMPPI | Weight of the intermediate step lost load performance index | Integer |  |  |  | OPTCONTROLPLAN
7853 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.LOSTREV | Lost revenue value (adjusted for supply costs) | Integer |  |  |  | OPTCONTROLPLAN
7854 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAIFIPI | Weight of the performance index for the final step Momentary Average Interruption Frequency Index (MAIFI) | Integer |  |  |  | OPTCONTROLPLAN
7855 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAIFIPOSTPLAN | Post-plan MAIFI value | Integer |  |  |  | OPTCONTROLPLAN
7856 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAIFIPREPLAN | Pre-plan MAIFI value | Integer |  |  |  | OPTCONTROLPLAN
7857 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MARGINPI | Weight of the performance index for the final step maximum margin | Integer |  |  |  | OPTCONTROLPLAN
7858 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAXDEVVLT | Maximum device voltage | Float |  |  |  | OPTCONTROLPLAN
7859 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAXSEGLD | The maximum branch loading (percent) | Float |  |  |  | OPTCONTROLPLAN
7860 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MAXSEGMENTMARGINPI | Weight of performance index for the maximum segment load | Integer |  |  |  | OPTCONTROLPLAN
7861 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MINDEVVLT | Minimum device voltage | Float |  |  |  | OPTCONTROLPLAN
7862 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MINFDRVD | Minimum feeder voltage drop | Integer |  |  |  | OPTCONTROLPLAN
7863 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.MOVESPI | Weight of final step number of control moves performance index | Integer |  |  |  | OPTCONTROLPLAN
7864 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMCSTNRT | Total number of customers not restored including customers on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
7865 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMCSTOUT | The number of de-energized customers | Integer |  |  |  | OPTCONTROLPLAN
7866 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMCSTRES | Number of customers restored | Integer |  |  |  | OPTCONTROLPLAN
7867 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMCSTRES_ORG | The number of restored customers | Integer |  |  |  | OPTCONTROLPLAN
7868 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMCSVERYPOISON | Total number of customers very poison on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
7869 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMHPCSTNRT | The number of dropped customers with high priority | Integer |  |  |  | OPTCONTROLPLAN
7870 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMTFNRT | Total number of transformers not restored including transformers on the faulted switchable section | Integer |  |  |  | OPTCONTROLPLAN
7871 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMTFOUT | The number of de-energized transformers | Integer |  |  |  | OPTCONTROLPLAN
7872 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NMTFRES | The number of restored transformers | Integer |  |  |  | OPTCONTROLPLAN
7873 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NUMCMBUS | Number of common buses tap changer bus (AFR). | Integer |  |  |  | OPTCONTROLPLAN
7874 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NUMCONTROLMOVE | Number of control moves | Integer |  |  |  | OPTCONTROLPLAN
7875 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NUMRANK | Plan ranking (in ascending order from 1 to n number of plans) | Integer |  |  |  | OPTCONTROLPLAN
7876 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NUMSUBSTATIONS | Number of associated substations | Integer |  |  |  | OPTCONTROLPLAN
7877 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.NUMVOLTLIMCOMP | Number of voltage limiting devices | Integer |  |  |  | OPTCONTROLPLAN
7878 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTMOVES | Optimization steps | String |  |  |  | OPTCONTROLPLAN
7879 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANHASVIOLATION | A flag indicating that the optimization plan has violations | Boolean |  |  |  | OPTCONTROLPLAN
7880 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANID | ID of the optimization plan | String |  |  |  | OPTCONTROLPLAN
7881 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANTOAPPROVE | Optimization plan to approve | String |  |  |  | OPTCONTROLPLAN
7882 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANTOGOBACK | Optimization plan to go back | String |  |  |  | OPTCONTROLPLAN
7883 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANTOIMPLEMENT | Optimization plan to implement | String |  |  |  | OPTCONTROLPLAN
7884 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTPLANTOREJECT | Optimization plan to reject | String |  |  |  | OPTCONTROLPLAN
7885 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OPTSINGLEMOVES | Number of optimization steps in the plan | String |  |  |  | OPTCONTROLPLAN
7886 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OSMFISRFAULTEDCOMPS | FISR faulted components | String |  |  |  | OPTCONTROLPLAN
7887 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.OUTAGEENERGIZEDPI | Weight of the performance index for lost energization | Integer |  |  |  | OPTCONTROLPLAN
7888 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANBACKFEEDKW | Backfeed real power flow | Float |  | kW | kW | OPTCONTROLPLAN
7889 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANBACKFEEDSUBID | Backfeed substation ID | String |  |  |  | OPTCONTROLPLAN
7890 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANBACKFEEDTRANSID | Backfeed transformer ID | String |  |  |  | OPTCONTROLPLAN
7891 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANDEVICES | Devices associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
7892 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANDEVICESFDRMAIN | A flag indicating that the device is located on the feeder backbone | Boolean |  |  |  | OPTCONTROLPLAN
7893 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANDEVICESORSTATIONS | Devices or stations associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
7894 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANEVALTIME | Evaluation time of the optimization plan | String |  |  |  | OPTCONTROLPLAN
7895 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANEVALTIME_TICKS | The time of the last optimization plan | String |  |  |  | OPTCONTROLPLAN
7896 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANFEEDERS | Feeders associated with the optimization plan | String |  |  |  | OPTCONTROLPLAN
7897 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANFUNCID | Plan function ID | String |  |  |  | OPTCONTROLPLAN
7898 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANLOSTKW | Lost kW | String |  |  |  | OPTCONTROLPLAN
7899 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXLOADSEGID | ID of the most heavily loaded branch | String |  |  |  | OPTCONTROLPLAN
7900 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXLOADSEGIDONLY | ID of the segment with the highest load in the plan | String |  |  |  | OPTCONTROLPLAN
7901 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXLOADSEGSUBID | ID of the substation the segment with the highest load belongs to | String |  |  |  | OPTCONTROLPLAN
7902 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXVLTDEVID | ID of the bus or load that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7903 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXVLTSUBID | ID of the substation that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7904 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMAXVLTTRANID | ID of the transformer that has the maximum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7905 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMINVLTDEVID | ID of the bus or load that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7906 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMINVLTSUBID | ID of the substation that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7907 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANMINVLTTRANID | ID of the transformer that has the minimum voltage for a switching reconfiguration or LVM plan | String |  |  |  | OPTCONTROLPLAN
7908 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANSTATE | Plan state | Enumeration |  |  |  | OPTCONTROLPLAN
7909 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANSTATIONID | ID of the substation the optimization plan is associated with | String |  |  |  | OPTCONTROLPLAN
7910 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANSTATIONNAME | Name of the substation the optimization plan is associated with | String |  |  |  | OPTCONTROLPLAN
7911 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLANTYPE | Type of the plan, such as FISR Loss of Voltage or AFR Overload | Enumeration |  |  |  | OPTCONTROLPLAN
7912 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLOSSPRE | Real power losses before the plan execution (AFR) | Integer |  |  |  | OPTCONTROLPLAN
7913 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PLOSSPST | Real power losses after the plan execution (AFR) | Integer |  |  |  | OPTCONTROLPLAN
7914 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PREDUCTION | Total change in real power demand (kW) | Float |  |  |  | OPTCONTROLPLAN
7915 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PRIORITYCMIPI | Weight of the performance index for Customer Minutes Interruption (CMI) with priority | Integer |  |  |  | OPTCONTROLPLAN
7916 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PROTECTIONPI | Weight of performance index for the final step execution of the Protection Validation function | Integer |  |  |  | OPTCONTROLPLAN
7917 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.PROTVAL | Protection value | String |  |  |  | OPTCONTROLPLAN
7918 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.QREDUCTION | Total change in reactive power demand (kVAR) | Float |  |  |  | OPTCONTROLPLAN
7919 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.RADIALFINAL | A flag indicating that the final switching state is radial | Boolean |  |  |  | OPTCONTROLPLAN
7920 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.RADIALPI | Weight for the final step radial condition performance index | Integer |  |  |  | OPTCONTROLPLAN
7921 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.RADIALTEMPPI | Weight for the intermediate step radial condition performance index | Integer |  |  |  | OPTCONTROLPLAN
7922 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.RECONFIGAPPNAME | Name of the reconfigurable application | String |  |  |  | OPTCONTROLPLAN
7923 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.REVNUPRE | Revenue before the plan execution | Integer |  |  |  | OPTCONTROLPLAN
7924 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.REVNUPST | Revenue after the plan execution | Integer |  |  |  | OPTCONTROLPLAN
7925 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIDIPI | Weight of the performance index for the final step System Average Interruption Duration Index (SAIDI) | Integer |  |  |  | OPTCONTROLPLAN
7926 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIDIPOSTPLAN | Post-plan SAIDI value | Integer |  |  |  | OPTCONTROLPLAN
7927 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIDIPREPLAN | Pre-plan SAIDI value | Integer |  |  |  | OPTCONTROLPLAN
7928 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIFIPI | Weight of the performance index for the final step System Average Interruption Frequency Index (SAIFI) | Integer |  |  |  | OPTCONTROLPLAN
7929 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIFIPOSTPLAN | Post-plan SAIFI value | Integer |  |  |  | OPTCONTROLPLAN
7930 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SAIFIPREPLAN | Pre-plan SAIFI value | Integer |  |  |  | OPTCONTROLPLAN
7931 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SECONDRATINGVIOLATIONS | A flag indicating that the second (emergency) ratings were violated at some point in the course of this plan | Boolean |  |  |  | OPTCONTROLPLAN
7932 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SHOWAFRPLAN | A flag to show AFR plans | Boolean |  |  |  | OPTCONTROLPLAN
7933 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SHOWFISRCAPLAN | A flag to show FISRCA plans | Boolean |  |  |  | OPTCONTROLPLAN
7934 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SHOWFISRPLAN | A flag to show FISR plans | Boolean |  |  |  | OPTCONTROLPLAN
7935 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SHOWLVMPLAN | Show LVM plan | String |  |  |  | OPTCONTROLPLAN
7936 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SHOWPLORSPLAN | A flag to show PLOS plans | Boolean |  |  |  | OPTCONTROLPLAN
7937 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SOLATIONDROPPOISONLOADPI | [5 empty] | OPTCONTROLPLAN
7938 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.SOLUTIONID | ID of the DNAF solution | String |  |  |  | OPTCONTROLPLAN
7939 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.STDCBPRE | Initial common tap changer bus standard deviation | Integer |  |  |  | OPTCONTROLPLAN
7940 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.STDCBPST | Final (post plan) common tap changer bus standard deviation | Integer |  |  |  | OPTCONTROLPLAN
7941 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.TFFINALPF | Final power transformer power factor | Float |  |  |  | OPTCONTROLPLAN
7942 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.TFINITPF | Initial power transformer power factor | Float |  |  |  | OPTCONTROLPLAN
7943 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.TOTALPI | Total performance index | Integer |  |  |  | OPTCONTROLPLAN
7944 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VOLTPI | Weight of the final step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
7945 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VOLTTEMPPI | Weight of the intermediate step bus voltage violations performance index | Integer |  |  |  | OPTCONTROLPLAN
7946 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCFINALLOSS | Post-plan active and reactive power losses | String |  |  |  | OPTCONTROLPLAN
7947 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCFLOWLIMITS | The flow violation limits strategy used in LVM | String |  |  |  | OPTCONTROLPLAN
7948 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCINITIALLOSS | Pre-plan active and reactive power losses | String |  |  |  | OPTCONTROLPLAN
7949 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCMAXTARGETPF | Maximum power factor target for station from manual overrride or from schedule | Float |  |  |  | OPTCONTROLPLAN
7950 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCMAXTARGETPFFORCE | LVM maximum target power force | String |  |  |  | OPTCONTROLPLAN
7951 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCMINTARGETPF | Minimum power factor target for station from manual overrride or from schedule | Float |  |  |  | OPTCONTROLPLAN
7952 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCMINTARGETPFFORCE | LVM minimum target power force | String |  |  |  | OPTCONTROLPLAN
7953 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCPROBFORM | The name of LVM problem formulation | String |  |  |  | OPTCONTROLPLAN
7954 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCSTATGROUP | The name of substation group | String |  |  |  | OPTCONTROLPLAN
7955 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN.VVCVOLTLIMITS | The voltage violation limits strategy used in LVM | String |  |  |  | OPTCONTROLPLAN
7956 | DNAF Object | Reconfigurable Area | RA | input | CONTROLPLAN | Pointer to the associated control plan | String
7957 | DNAF Object | Reconfigurable Area | RA |  | FAULTCOMPID | ID of faulted component | String
7958 | DNAF Object | Reconfigurable Area | RA |  | FUNCTIONTYPE | Function type | Enumeration
7959 | DNAF Object | Reconfigurable Area | RA |  | NUMSUB | Number of substations affected | Integer
7960 | DNAF Object | Reconfigurable Area | RA |  | OPERATIONMODE | Operation mode | Enumeration
7961 | DNAF Object | Reconfigurable Area | RA |  | PRIMSUBNAME | Name of primary substation | String
7962 | DNAF Object | Reconfigurable Area | RA |  | STATE | State | Enumeration
7963 | DNAF Object | Reconfigurable Area | RA |  | SUBNAMES | List of neighboring substations | String
7964 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY | Pointer to the associated reserved capacity | String
7965 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY | Pointer to the associated reserved capacity | String
7966 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | input | ISRECONFIGRABLEDEVICE | Specifies whether the device is capable of changing the feeder backbone configuration (part of a feeder main). This does not apply to switches on spurs off the main feeder, lateral lines, etc. | Boolean
7967 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | DYNSTATIONNAME | The name of the substation that is currently energizing the device. | String
7968 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | SWITCHTYPE | The type of device. | String
7969 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | SWCURRENTPOSITION | The status of the device. | String
7970 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | ISCOMPOSITESWITCH | Specifies whether this is a composite switch | Boolean
7971 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | FISRELIGIBLE | Indication of whether the device is eligible for FISR (Eligible/Not Eligible). | String
7972 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | AFRELIGIBLE | Indication of whether the device is eligible for AFR (Eligible/Not Eligible). | String
7973 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | PLOSELIGIBLE | Indication of whether the device is eligible for PLOS (Eligible/Not Eligible). | String
7974 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | MEASVAUEFORSWITCH | Status measurement. | String
7975 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.ADDRCONCOMMONPATH | Add Reserves on Common Paths | Boolean
7976 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.DNOMTABNAME | DNOM table name | String
7977 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
7978 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
7979 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FEEDDEVICEID | Feed device ID | String
7980 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDDEVICEID1 | ID of the feed device, primary feed | String
7981 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDDEVICEID2 | ID of the feed device, secondary feed | String
7982 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDDEVICEIDS | IDs of the feed devices | String
7983 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FEEDFIRMCOMMITMENT | Feed firm commitment | Boolean
7984 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDLINERESCAP | Line reserved capacity value | String
7985 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDLINERESCAP1 | Reserved capacity line values, primary feed | String |  | kW and PF | kW and PF
7986 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDLINERESCAP2 | Reserved capacity line values, secondary feed | String |  | kW and PF | kW and PF
7987 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FEEDLINERESVCAP | Feed line reserved capacity | String
7988 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FEEDPOWERFACTOR | Feed power factory | String
7989 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDSTATIONRESCAP | Station reserved capacity values | String
7990 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDSTATIONRESCAP1 | Reserved capacity station values, primary feed | String |  | kW and PF | kW and PF
7991 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FEEDSTATIONRESCAP2 | Reserved capacity station values, secondary feed | String |  | kW and PF | kW and PF
7992 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FEEDSTATIONRESVCAP | Feed station reserved capacity | String
7993 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FIRMCOMMITMENT1 | Firm Commitment, primary feed | Boolean
7994 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FIRMCOMMITMENT2 | Firm Commitment, secondary feed | Boolean
7995 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.FLAGS | Reserved capacity flags | String
7996 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.FULLRCONPARALLELPATH | Apply Full Reserve on Parallel Path | Boolean
7997 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.ID | Object unique ID | String |  |  |  | DNMOBJ
7998 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.LOADID | Load ID | String
7999 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.LOADID1 | Associated load ID, primary feed | String
8000 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.LOADID2 | Associated load ID, secondary feed | String
8001 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.LOADIDS | Associated load IDs | String
8002 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8003 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.NAME | Object name | String |  |  |  | DNMOBJ
8004 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
8005 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.NUMFEEDS | Number of feeds | String
8006 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.NUMLOADS | Number of loads | Integer
8007 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.PRIMCONN | Primary connection composite flag (mask). | Integer
8008 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RCENABLED | Indicates whether the reserved capacity is enabled | Boolean
8009 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYDYNFEEDNAME1 | Dynamic station and feeder, primary feed | String
8010 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYDYNFEEDNAME2 | Dynamic station and feeder, secondary feed | String
8011 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYLOADPVAL1 | Reserved capacity load real power, primary feed | String
8012 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYLOADPVAL2 | Reserved capacity load real power, secondary feed | String
8013 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYLOADQVAL1 | Reserved capacity load reactive power, primary feed | String
8014 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.RESERVEDCAPACITYLOADQVAL2 | Reserved capacity load reactive power, secondary feed | String
8015 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.STATIONNAME | Station name | String
8016 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL |  | RESERVECAPACITY.UNITS | Reserved capacity units | String
8017 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8018 | DNOM Component Placement | Reserved Capacity Label Placement | RCLBPL | input | RESERVECAPACITY.YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8019 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | MEASQUALITYFORSWITCH | Status measurement quality. | String
8020 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.ADDRCONCOMMONPATH | Add Reserves on Common Paths | Boolean
8021 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.DNOMTABNAME | DNOM table name | String
8022 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8023 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8024 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FEEDDEVICEID | Feed device ID | String
8025 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDDEVICEID1 | ID of the feed device, primary feed | String
8026 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDDEVICEID2 | ID of the feed device, secondary feed | String
8027 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDDEVICEIDS | IDs of the feed devices | String
8028 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FEEDFIRMCOMMITMENT | Feed firm commitment | Boolean
8029 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDLINERESCAP | Line reserved capacity value | String
8030 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDLINERESCAP1 | Reserved capacity line values, primary feed | String |  | kW and PF | kW and PF
8031 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDLINERESCAP2 | Reserved capacity line values, secondary feed | String |  | kW and PF | kW and PF
8032 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FEEDLINERESVCAP | Feed line reserved capacity | String
8033 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FEEDPOWERFACTOR | Feed power factory | String
8034 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDSTATIONRESCAP | Station reserved capacity values | String
8035 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDSTATIONRESCAP1 | Reserved capacity station values, primary feed | String |  | kW and PF | kW and PF
8036 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FEEDSTATIONRESCAP2 | Reserved capacity station values, secondary feed | String |  | kW and PF | kW and PF
8037 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FEEDSTATIONRESVCAP | Feed station reserved capacity | String
8038 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FIRMCOMMITMENT1 | Firm Commitment, primary feed | Boolean
8039 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FIRMCOMMITMENT2 | Firm Commitment, secondary feed | Boolean
8040 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.FLAGS | Reserved capacity flags | String
8041 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.FULLRCONPARALLELPATH | Apply Full Reserve on Parallel Path | Boolean
8042 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.ID | Object unique ID | String |  |  |  | DNMOBJ
8043 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.LOADID | Load ID | String
8044 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.LOADID1 | Associated load ID, primary feed | String
8045 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.LOADID2 | Associated load ID, secondary feed | String
8046 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.LOADIDS | Associated load IDs | String
8047 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8048 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.NAME | Object name | String |  |  |  | DNMOBJ
8049 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
8050 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.NUMFEEDS | Number of feeds | String
8051 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.NUMLOADS | Number of loads | Integer
8052 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.PRIMCONN | Primary connection composite flag (mask). | Integer
8053 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RCENABLED | Indicates whether the reserved capacity is enabled | Boolean
8054 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYDYNFEEDNAME1 | Dynamic station and feeder, primary feed | String
8055 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYDYNFEEDNAME2 | Dynamic station and feeder, secondary feed | String
8056 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYLOADPVAL1 | Reserved capacity load real power, primary feed | String
8057 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYLOADPVAL2 | Reserved capacity load real power, secondary feed | String
8058 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYLOADQVAL1 | Reserved capacity load reactive power, primary feed | String
8059 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.RESERVEDCAPACITYLOADQVAL2 | Reserved capacity load reactive power, secondary feed | String
8060 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.STATIONNAME | Station name | String
8061 | DNOM Component Placement | Reserved Capacity Placement | RCPLE |  | RESERVECAPACITY.UNITS | Reserved capacity units | String
8062 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8063 | DNOM Component Placement | Reserved Capacity Placement | RCPLE | input | RESERVECAPACITY.YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8064 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | NORMPOSITION | Normal position for the switch. | String
8065 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.DEFREGMODE | Default regulation mode | String
8066 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWAEDREGMETHOD | Forward regulation method | String
8067 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDFLOWTHRESHOLD | Forward regulation flow threshold | String
8068 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDLDCR | The LDC resistance for forward regulation defined in volts | String |  | Volts | Volts
8069 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDLDCX | The LDC reactance for forward regulation defined in volts | String |  | Volts | Volts
8070 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDREGNODESIDE | Forward regulation node side | String
8071 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDVBANDWIDTH | The voltage bandwidth for forward regulation | String |  | Volts | Volts
8072 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDVOLTREDUCCAPABLE | The status of forward voltage reduction capability | Boolean
8073 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDVOLTREDUCVALUE1 | The level 1 voltage reduction value for forward regulation | String |  | Volts | Volts
8074 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDVOLTREDUCVALUE2 | The level 2 voltage reduction value for forward regulation | String |  | Volts | Volts
8075 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FORWARDVOLTREDUCVALUE3 | The level 3 voltage reduction value for forward regulation | String |  | Volts | Volts
8076 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.FOWRARDVOLTAGETARGET | The voltage target for forward regulation | String |  | Volts | Volts
8077 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.ISREACTIVEFLOWSENSE | Can be true or false | Boolean
8078 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.NUMREGMODE | Number of the regulation mode | String
8079 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REGID | Regulation mode ID | String
8080 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFLDCR | The LDC resistance for forward regulation. | String
8081 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFLDCX | The LDC reactance for forward regulation. | String
8082 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFNAME | The name of the forward regulation mode. | String
8083 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFSIDE | The side of the transformer used for forward regulation. | String
8084 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFV1 | The level 1 voltage target for forward regulation. | String
8085 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFV2 | The level 2 voltage target for forward regulation. | String
8086 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFV3 | The level 3 voltage target for forward regulation. | String
8087 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFVBANDWIDTH | The voltage regulation bandwidth for forward regulation. | String
8088 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFVREDCAP | The voltage reduction capability status for forward regulation. | String
8089 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODEFVTARGET | The voltage target for forward regulation. | String
8090 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODENAME | The name of the regulation mode. | String
8091 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERLDCR | The LDC resistance for reverse regulation. | String
8092 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERLDCX | The LDC reactance for reverse regulation. | String
8093 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERNAME | The name of the reverse regulation mode. | String
8094 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERSIDE | The side of the transformer used for reverse regulation. | String
8095 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERV1 | The level 1 voltage target for reverse regulation. | String
8096 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERV2 | The level 2 voltage target for reverse regulation. | String
8097 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERV3 | The level 3 voltage target for reverse regulation. | String
8098 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERVBANDWIDTH | The voltage regulation bandwidth for reverse regulation. | String
8099 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERVREDCAP | The voltage reduction capability status for reverse regulation. | String
8100 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE.REGMODERVTARGET | The voltage target for reverse regulation. | String
8101 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REGNAME | Regulation mode name | String
8102 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REGULATIONMODENAME | Regulation mode name | String
8103 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEFLOWTHRESHOLD | Reverse regulation flow threshold | String
8104 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSELDCR | The LDC resistance for reverse regulation defined in volts | String |  | Volts | Volts
8105 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSELDCX | The LDC reactance for reverse regulation defined in volts | String |  | Volts | Volts
8106 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEREGMETHOD | Reverse regulation method | String
8107 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEREGNODESIDE | Reverse regulation node side | String
8108 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVBANDWIDTH | The voltage bandwidth for reverse regulation | String |  | Volts | Volts
8109 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVOLTAGETARGET | The voltage target for reverse regulation | String |  | Volts | Volts
8110 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVOLTREDUCCAPABLE | The status of reverse voltage reduction capability | Boolean
8111 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVOLTREDUCVALUE1 | The level 1 voltage reduction value for reverse regulation | String |  | Volts | Volts
8112 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVOLTREDUCVALUE2 | The level 2 voltage reduction value for reverse regulation | String |  | Volts | Volts
8113 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.REVERSEVOLTREDUCVALUE3 | The level 3 voltage reduction value for reverse regulation | String |  | Volts | Volts
8114 | DNAF Object | Regulation Control Definition | REGCONTROLDEF |  | REGMODE.SCADAMEASVALUE | SCADA measurement value | String
8115 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | RECONFIGSWTLOCKOUT | Flag indicating the lockout status of the device. | String
8116 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | SWTALARMSTATUS | In Alarm measurement. | String
8117 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | RECONFIGSWTPREVENTCLOSE | Hot line tag (Block Close) status (Applied or Not Applied). | String
8118 | Virtual Object | Reconfiguration Application Device | RECONFIGDEVICE | Output | RECRECLOSESTATUS | Flag indicating if the reclosing capability of the device is enabled. | String
8119 | DNAF Object | Regulation Control Definition | REGCONTROLDEF | input | REGMODE | Pointer to the regulation mode | String
8120 | DNAF Object | Regulation Mode | REGMODE |  | DEFREGMODE | Default regulation mode | String
8121 | DNAF Object | Regulation Mode | REGMODE |  | FORWAEDREGMETHOD | Forward regulation method | String
8122 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDFLOWTHRESHOLD | Forward regulation flow threshold | String
8123 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDLDCR | The LDC resistance for forward regulation defined in volts | String |  | Volts | Volts
8124 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDLDCX | The LDC reactance for forward regulation defined in volts | String |  | Volts | Volts
8125 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDREGNODESIDE | Forward regulation node side | String
8126 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDVBANDWIDTH | The voltage bandwidth for forward regulation | String |  | Volts | Volts
8127 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDVOLTREDUCCAPABLE | The status of forward voltage reduction capability | Boolean
8128 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDVOLTREDUCVALUE1 | The level 1 voltage reduction value for forward regulation | String |  | Volts | Volts
8129 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDVOLTREDUCVALUE2 | The level 2 voltage reduction value for forward regulation | String |  | Volts | Volts
8130 | DNAF Object | Regulation Mode | REGMODE |  | FORWARDVOLTREDUCVALUE3 | The level 3 voltage reduction value for forward regulation | String |  | Volts | Volts
8131 | DNAF Object | Regulation Mode | REGMODE |  | FOWRARDVOLTAGETARGET | The voltage target for forward regulation | String |  | Volts | Volts
8132 | DNAF Object | Regulation Mode | REGMODE |  | ISREACTIVEFLOWSENSE | Can be true or false | Boolean
8133 | DNAF Object | Regulation Mode | REGMODE |  | NUMREGMODE | Number of the regulation mode | String
8134 | DNAF Object | Regulation Mode | REGMODE |  | REGID | Regulation mode ID | String
8135 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFLDCR | The LDC resistance for forward regulation. | String
8136 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFLDCX | The LDC reactance for forward regulation. | String
8137 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFNAME | The name of the forward regulation mode. | String
8138 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFSIDE | The side of the transformer used for forward regulation. | String
8139 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFV1 | The level 1 voltage target for forward regulation. | String
8140 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFV2 | The level 2 voltage target for forward regulation. | String
8141 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFV3 | The level 3 voltage target for forward regulation. | String
8142 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFVBANDWIDTH | The voltage regulation bandwidth for forward regulation. | String
8143 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFVREDCAP | The voltage reduction capability status for forward regulation. | String
8144 | DNAF Object | Regulation Mode | REGMODE |  | REGMODEFVTARGET | The voltage target for forward regulation. | String
8145 | DNAF Object | Regulation Mode | REGMODE |  | REGMODENAME | The name of the regulation mode. | String
8146 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERLDCR | The LDC resistance for reverse regulation. | String
8147 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERLDCX | The LDC reactance for reverse regulation. | String
8148 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERNAME | The name of the reverse regulation mode. | String
8149 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERSIDE | The side of the transformer used for reverse regulation. | String
8150 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERV1 | The level 1 voltage target for reverse regulation. | String
8151 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERV2 | The level 2 voltage target for reverse regulation. | String
8152 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERV3 | The level 3 voltage target for reverse regulation. | String
8153 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERVBANDWIDTH | The voltage regulation bandwidth for reverse regulation. | String
8154 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERVREDCAP | The voltage reduction capability status for reverse regulation. | String
8155 | DNAF Object | Regulation Mode | REGMODE |  | REGMODERVTARGET | The voltage target for reverse regulation. | String
8156 | DNAF Object | Regulation Mode | REGMODE |  | REGNAME | Regulation mode name | String
8157 | DNAF Object | Regulation Mode | REGMODE |  | REGULATIONMODENAME | Regulation mode name | String
8158 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEFLOWTHRESHOLD | Reverse regulation flow threshold | String
8159 | DNAF Object | Regulation Mode | REGMODE |  | REVERSELDCR | The LDC resistance for reverse regulation defined in volts | String |  | Volts | Volts
8160 | DNAF Object | Regulation Mode | REGMODE |  | REVERSELDCX | The LDC reactance for reverse regulation defined in volts | String |  | Volts | Volts
8161 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEREGMETHOD | Reverse regulation method | String
8162 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEREGNODESIDE | Reverse regulation node side | String
8163 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVBANDWIDTH | The voltage bandwidth for reverse regulation | String |  | Volts | Volts
8164 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVOLTAGETARGET | The voltage target for reverse regulation | String |  | Volts | Volts
8165 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVOLTREDUCCAPABLE | The status of reverse voltage reduction capability | Boolean
8166 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVOLTREDUCVALUE1 | The level 1 voltage reduction value for reverse regulation | String |  | Volts | Volts
8167 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVOLTREDUCVALUE2 | The level 2 voltage reduction value for reverse regulation | String |  | Volts | Volts
8168 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8169 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8170 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8171 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
8172 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8173 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.NAME | Name of the object | String |  |  |  | DNMOBJ
8174 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8175 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8176 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8177 | DNAF Object | Regulation Mode | REGMODE |  | REVERSEVOLTREDUCVALUE3 | The level 3 voltage reduction value for reverse regulation | String |  | Volts | Volts
8178 | DNAF Object | Regulation Mode | REGMODE |  | SCADAMEASVALUE | SCADA measurement value | String
8179 | DNAF Object | Regulator Group | REGULATORGROUP | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8180 | DNAF Object | Regulator Group | REGULATORGROUP |  | NUMTF | The number of transformers in the regulator group | Integer
8181 | DNAF Object | Regulator Group | REGULATORGROUP | input | TFGROUP | Dynamic array of transformer pointers | String
8182 | DNAF Object | Regulator Group | REGULATORGROUP | output | VOLTIMB | Indicates whether a previous voltage imbalance was detected. Used for the tap changer voltage imbalance RTN alarm. | Boolean
8183 | DNOM Component | Reserved Capacity | RESERVECAPACITY |  | PRIMCONN | Primary connection composite flag (mask). | Integer
8184 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | ADDRCONCOMMONPATH | Add Reserves on Common Paths | Boolean
8185 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | DNOMTABNAME | DNOM table name | String
8186 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8187 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8188 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FEEDDEVICEID | Feed device ID | String
8189 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDDEVICEID1 | ID of the feed device, primary feed | String
8190 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDDEVICEID2 | ID of the feed device, secondary feed | String
8191 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDDEVICEIDS | IDs of the feed devices | String
8192 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FEEDFIRMCOMMITMENT | Feed firm commitment | Boolean
8193 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDLINERESCAP | Line reserved capacity value | String
8194 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDLINERESCAP1 | Reserved capacity line values, primary feed | String |  | kW and PF | kW and PF
8195 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDLINERESCAP2 | Reserved capacity line values, secondary feed | String |  | kW and PF | kW and PF
8196 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FEEDLINERESVCAP | Feed line reserved capacity | String
8197 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FEEDPOWERFACTOR | Feed power factory | String
8198 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDSTATIONRESCAP | Station reserved capacity values | String
8199 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDSTATIONRESCAP1 | Reserved capacity station values, primary feed | String |  | kW and PF | kW and PF
8200 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FEEDSTATIONRESCAP2 | Reserved capacity station values, secondary feed | String |  | kW and PF | kW and PF
8201 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FEEDSTATIONRESVCAP | Feed station reserved capacity | String
8202 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FIRMCOMMITMENT1 | Firm Commitment, primary feed | Boolean
8203 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FIRMCOMMITMENT2 | Firm Commitment, secondary feed | Boolean
8204 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | FLAGS | Reserved capacity flags | String
8205 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | FULLRCONPARALLELPATH | Apply Full Reserve on Parallel Path | Boolean
8206 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8207 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | LOADID | Load ID | String
8208 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | LOADID1 | Associated load ID, primary feed | String
8209 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | LOADID2 | Associated load ID, secondary feed | String
8210 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | LOADIDS | Associated load IDs | String
8211 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8212 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | NAME | Object name | String |  |  |  | DNMOBJ
8213 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | NELECSUBNAME | Name of the substation the object belongs to | String |  |  |  | NONELECTRICAL
8214 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | NUMFEEDS | Number of feeds | String
8215 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | NUMLOADS | Number of loads | Integer
8216 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
8217 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RCENABLED | Indicates whether the reserved capacity is enabled | Boolean
8218 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYDYNFEEDNAME1 | Dynamic station and feeder, primary feed | String
8219 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYDYNFEEDNAME2 | Dynamic station and feeder, secondary feed | String
8220 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYLOADPVAL1 | Reserved capacity load real power, primary feed | String
8221 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYLOADPVAL2 | Reserved capacity load real power, secondary feed | String
8222 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYLOADQVAL1 | Reserved capacity load reactive power, primary feed | String
8223 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | RESERVEDCAPACITYLOADQVAL2 | Reserved capacity load reactive power, secondary feed | String
8224 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | STATIONNAME | Station name | String
8225 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY |  | UNITS | Reserved capacity units | String
8226 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8227 | DNOM Component | Reserved Capacity | RESERVEDCAPACITY | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8228 | DNOM Component | Reference Bus Interface | RFBSIF | input | _KEY | The unique identifier to represent a device | String
8229 | DNOM Component | Reference Bus Interface | RFBSIF | input | ANGLEOVERRIDE | Indicates if manual override value for voltage angle is used | Boolean
8230 | DNOM Component | Reference Bus Interface | RFBSIF |  | ANTARGET | Nominal angle target (deg) | Float
8231 | DNOM Component | Reference Bus Interface | RFBSIF | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8232 | DNOM Component | Reference Bus Interface | RFBSIF |  | CONNECTED | A flag indicating that the interface is connected | Boolean
8233 | DNOM Component | Reference Bus Interface | RFBSIF |  | DEINTVOL | Nominal voltage target (%) | Float
8234 | DNOM Component | Reference Bus Interface | RFBSIF |  | DINTVANG | Default interface voltage angle (degrees). | Integer
8235 | DNOM Component | Reference Bus Interface | RFBSIF | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
8236 | DNOM Component | Reference Bus Interface | RFBSIF | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8237 | DNOM Component | Reference Bus Interface | RFBSIF | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8238 | DNOM Component | Reference Bus Interface | RFBSIF |  | ENABLEREFBUSINTER | A flang indicating that the reference bus interface is enabled | Boolean
8239 | DNOM Component | Reference Bus Interface | RFBSIF | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
8240 | DNOM Component | Reference Bus Interface | RFBSIF | input | GROUNDED | Flag indicating that the shunt device is grounded | Boolean |  |  |  | SHUNT
8241 | DNOM Component | Reference Bus Interface | RFBSIF |  | HASMANUALENTRY | If one or some fields of bus have value override | Boolean
8242 | DNOM Component | Reference Bus Interface | RFBSIF | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8243 | DNOM Component | Reference Bus Interface | RFBSIF |  | INTFCSWITCH | Indicates that Interface has the switch modelled. This which is used to determine, if Converter needs to add a fake switch at the interface. | Boolean
8244 | DNOM Component | Reference Bus Interface | RFBSIF |  | INTVOLTRANGE | Interface voltage range | Integer
8245 | DNOM Component | Reference Bus Interface | RFBSIF |  | ISINTERFACESUSPECT | A flag indicating that the interface is suspect | Boolean
8246 | DNOM Component | Reference Bus Interface | RFBSIF |  | ISSTUDYREFINTFC | Study interface. If YES, this interface has been dynamically created by the software during model validation. If No, this interface has been manually specified by the user in the model. For Analyst use only. | Boolean
8247 | DNOM Component | Reference Bus Interface | RFBSIF | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8248 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANANTARGET | Manual angle target (deg) | Float
8249 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER0 | Manual zero sequence resistance value. | Float
8250 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER0ENABLE | Enable the manual zero sequence resistance value. | Boolean
8251 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER1 | Manual positive sequence resistance value. | Float
8252 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER1ENABLE | Enable the manual positive sequence resistance value. | Boolean
8253 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER2 | Manual negative sequence resistance value. | Float
8254 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCER2ENABLE | Enable the manual negative sequence resistance value. | Boolean
8255 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX0 | Manual zero sequence reactance value. | Float
8256 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX0ENABLE | Enable the manual zero sequence reactance value. | Boolean
8257 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX1 | Manual positive sequence reactance value. | Float
8258 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX1ENABLE | Enable the manual positive sequence reactance value. | Boolean
8259 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX2 | Manual negative sequence reactance value. | Float
8260 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANSOURCEX2ENABLE | Enable the manual negative sequence reactance value. | Boolean
8261 | DNOM Component | Reference Bus Interface | RFBSIF | input | MANVOLTANGLE | Manually entered voltage angle value | Float |  | degrees | degrees
8262 | DNOM Component | Reference Bus Interface | RFBSIF | input | MANVOLTMAG | Manually entered voltage value | Float |  | % | %
8263 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANVTARGET | Manual voltage target (%) | Float
8264 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANVTARGETPHA | Manual voltage target of phase A (%) | Float
8265 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANVTARGETPHB | Manual voltage target of phase B (%) | Float
8266 | DNOM Component | Reference Bus Interface | RFBSIF |  | MANVTARGETPHC | Manual voltage target of phase C (%) | Float
8267 | DNOM Component | Reference Bus Interface | RFBSIF | input | NAME | Object name | String |  |  |  | DNMOBJ
8268 | DNOM Component | Reference Bus Interface | RFBSIF | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8269 | DNOM Component | Reference Bus Interface | RFBSIF | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8270 | DNOM Component | Reference Bus Interface | RFBSIF | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8271 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.AREAIND | Permission area index of the switch | String |  |  |  | DNMOBJ
8272 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.BOUNDARY | Branch mask | Integer |  |  |  | BRANCH
8273 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.CHGNOPEN | Change the normal open status flag | String |  |  |  | SWT
8274 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.CURROPEN | Current open status flag | String |  |  |  | SWT
8275 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | String |  |  |  | SWT
8276 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.DNOMX | X coordinate of the switch | String |  |  |  | DNMOBJ
8277 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.DNOMY | Y coordinate of the switch | String |  |  |  | DNMOBJ
8278 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.DSOOVER | Enumeration of advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | String |  |  |  | SWT
8279 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
8280 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.ID | ID of the breaker | String |  |  |  | DNMOBJ
8281 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.NAME | Name of the switch | String |  |  |  | DNMOBJ
8282 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8283 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8284 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.NOPEN | Normally open status flag | String |  |  |  | SWT
8285 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8286 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.REMOTE | Remote status flag | String |  |  |  | SWT
8287 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.SWMASK | Switch attribute mask | String |  |  |  | SWT
8288 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH.SWMASK2 | Switch attribute mask 2 | String |  |  |  | SWT
8289 | DNOM Component | Reference Bus Interface | RFBSIF |  | PQFLOWA | Phase A output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
8290 | DNOM Component | Reference Bus Interface | RFBSIF |  | PQFLOWB | Phase B output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
8291 | DNOM Component | Reference Bus Interface | RFBSIF |  | PQFLOWC | Phase C output power (referenced into the load, out of the bus) | Float |  | KVA | KVA
8292 | DNOM Component | Reference Bus Interface | RFBSIF |  | PQFLOWN | Phase N output complex power (referenced into the load, out of the bus) | Float |  | KVA | KVA
8293 | DNOM Component | Reference Bus Interface | RFBSIF | input | PSEUDOSWITCH | Pointer to the reference bus interface pseudo switch | String
8294 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFBUSUSED | Indicates if the reference bus is used | Boolean
8295 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFCONBRANCHID | Interface connection branch ID | String
8296 | DNOM Component | Reference Bus Interface | RFBSIF |  | REFMANANGLENABLE | A flag indicating that manual angle target is enabled | Boolean
8297 | DNOM Component | Reference Bus Interface | RFBSIF |  | REFMANVOLTENABLE | A flag indicating that manual voltage target is enabled | Boolean
8298 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFTOTALAMP | Current in amperes | Float |  | Amps | Amps
8299 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFTOTALKVAR | Reactive power | Float |  | kVAR | kVAR
8300 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFTOTALKW | Real power | Float |  | kW | kW
8301 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLT | Interface voltage in volts | Float |  | Volts | Volts
8302 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLT120BASE | Voltage in equivalent 120V value | Float |  | Volts | Volts
8303 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTAANGLE | Phase A voltage angle | Float |  | degrees | degrees
8304 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTANGLE | Voltage angle | Float |  | degree | degree
8305 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTBANGLE | Phase B voltage angle | Float |  | degrees | degrees
8306 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTCANGLE | Phase C voltage angle | Float |  | degrees | degrees
8307 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTPU | Voltage in p.u. | Float |  | per unit | per unit
8308 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTPUA | Phase A voltage in p.u. | Float |  | per unit | per unit
8309 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTPUB | Phase B voltage in p.u. | Float |  | per unit | per unit
8310 | DNOM Component | Reference Bus Interface | RFBSIF | input | REFVOLTPUC | Phase C voltage in p.u. | Float |  | per unit | per unit
8311 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCR0 | Zero sequence resistance in Ohms. | String
8312 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCR1 | Positive sequence resistance in Ohms. | String
8313 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCR2 | Negative sequence resistance in Ohms. | String
8314 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCX0 | Zero sequence reactance in Ohms. | String
8315 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCX1 | Positive sequence reactance in Ohms. | String
8316 | DNOM Component | Reference Bus Interface | RFBSIF |  | SRCX2 | Negative sequence reactance in Ohms. | String
8317 | DNOM Component | Reference Bus Interface | RFBSIF |  | STYINTFC | Indicates whether the interface is real (placed in the model) or not real (for study mode execution) | Boolean
8318 | DNOM Component | Reference Bus Interface | RFBSIF |  | USEDREFBUSFILTER | Reference bus filter | String
8319 | DNOM Component | Reference Bus Interface | RFBSIF |  | VA | Voltage angle of phase A (deg) | Float
8320 | DNOM Component | Reference Bus Interface | RFBSIF |  | VB | Voltage angle of phase B (deg) | Float
8321 | DNOM Component | Reference Bus Interface | RFBSIF |  | VC | Voltage angle of phase C (deg) | Float
8322 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTANDANGLEA | Voltage and phase angle of phase A | Float
8323 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTANDANGLEB | Voltage and phase angle of phase B | Float
8324 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTANDANGLEC | Voltage and phase angle of phase C | Float
8325 | DNOM Component | Reference Bus Interface | RFBSIF | input | VOLTANGLE | Voltage angle (either nominal values or manually entered values if provided) | Float |  | degrees | degrees
8326 | DNOM Component | Reference Bus Interface | RFBSIF | input | VOLTMAG | Voltage magnitude (either nominal values or manually entered values if provided). The nominal voltage magnitude is set for the individual reference bus interface objects via the Default Interface Bus Voltage (%) field of Substation Editor, or via the Reference Bus Default Voltage (%) option of the Converter. | Float |  | % | %
8327 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTMAGA | Voltage target for phases A. | String
8328 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTMAGB | Voltage target for phases B. | String
8329 | DNOM Component | Reference Bus Interface | RFBSIF |  | VOLTMAGC | Voltage target for phases C. | String
8330 | DNOM Component | Reference Bus Interface | RFBSIF | input | VOLTOVERRIDE | Indicates if manual override value for voltage is used | Boolean
8331 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
8332 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8333 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
8334 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8335 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8336 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.ENUMTYPE | Splice box type 1= standard, 2 = others | Integer |  |  |  | SPLBOX
8337 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
8338 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.ID | ID of the object | String |  |  |  | DNMOBJ
8339 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.NAME | Object name | String |  |  |  | DNMOBJ
8340 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
8341 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.NUMOBJ | The number of objects in the splice box | Integer |  |  |  | SPLBOX
8342 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE.REFDRAW | Reference drawing | String |  |  |  | SPLBOX
8343 | DNOM Component | Reference Bus Interface | RFBSIF |  | VTARGET | Voltage target (%) | Float
8344 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
8345 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8346 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
8347 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8348 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8349 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.ENUMTYPE | Splice box type 1= standard, 2 = others | Integer |  |  |  | SPLBOX
8350 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
8351 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.ID | ID of the object | String |  |  |  | DNMOBJ
8352 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.NAME | Object name | String |  |  |  | DNMOBJ
8353 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
8354 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.NUMOBJ | The number of objects in the splice box | Integer |  |  |  | SPLBOX
8355 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE.REFDRAW | Reference drawing | String |  |  |  | SPLBOX
8356 | DNOM Component | Reference Bus Interface | RFBSIF | input | WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
8357 | DNOM Component | Reference Bus Interface | RFBSIF | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8358 | DNOM Component | Reference Bus Interface | RFBSIF | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8359 | DNOM Component Placement | Splice Box Label Placement | SBLBPL | input | SPLICE | Pointer to the associated splice box | String
8360 | DNOM Component Placement | Splice Box Placement | SBPLE | input | SPLICE | Pointer to the associated splice box | String
8361 | Virtual Object | SCADA or DER Component (or Controllable Measurements) | SCADA_OR_DER (or CONTROLLABLE_MEAS) |  | N/A | Supports the same queries as TOPOCOMP. Filters only SCADA and DER devices. Applicable objects configured by the SCADA_OR_DER_COLLECTION parameter. By default, LOAD,GEN,ENERGYRES,SWT,TF,SHIMP,EXTBRC,RFBSIF,SV,SERIES,DISTTF | String
8362 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCCURRENTA | Phase A fault current at this location. | Float | DPF
8363 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCCURRENTB | Phase B fault current at this location. | Float | DPF
8364 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCCURRENTC | Phase C fault current at this location. | Float | DPF
8365 | DNAF Object | Short Circuit Calculation | SCCSCC | input | SCCDEVID | SCC location device Id | String
8366 | DNAF Object | Short Circuit Calculation | SCCSCC | input | SCCFAULTIMP | Fault impedance evaluation type (Bolted Fault or User Configured Impedance) | String
8367 | DNAF Object | Short Circuit Calculation | SCCSCC | input | SCCFAULTTYPE | Fault type, such as AG, etc. | Integer
8368 | Global Object | Schedule | SCHED | input | CLDLDSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
8369 | Global Object | Schedule | SCHED | input | CLDLDSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8370 | Global Object | Schedule | SCHED | input | CLDLDSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8371 | Global Object | Schedule | SCHED | input | CLDLDSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8372 | Global Object | Schedule | SCHED | input | CLDLDSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8373 | Global Object | Schedule | SCHED | input | CLDLDSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8374 | Global Object | Schedule | SCHED | input | CLDLDSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8375 | Global Object | Schedule | SCHED | input | CLDLDSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8376 | Global Object | Schedule | SCHED | input | CLDLDSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8377 | Global Object | Schedule | SCHED | input | CLDLDSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8378 | Global Object | Schedule | SCHED | input | CLDLDSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8379 | Global Object | Schedule | SCHED | input | CLDLDSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8380 | Global Object | Schedule | SCHED | input | CLDLDSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8381 | DNAF Object | Short Circuit Calculation | SCCSCC | input | SCCNODEID | SCC location node Id | String
8382 | Global Object | Schedule | SCHED | input | DAYTYPE.ACALDATE | The number of calendar days with abnormal load | Integer |  |  |  | DAYTYP
8383 | Global Object | Schedule | SCHED | input | DAYTYPE.AWEEKDAY | The number of weekdays with abnormal load | Integer |  |  |  | DAYTYP
8384 | Global Object | Schedule | SCHED | input | DAYTYPE.DESCRIPT | Day type description | String |  |  |  | DAYTYP
8385 | Global Object | Schedule | SCHED | input | DAYTYPE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8386 | Global Object | Schedule | SCHED | input | DAYTYPE.NUMCALD | The number of calendar days for the day type (given in month/day/year format) | Integer |  |  |  | DAYTYP
8387 | Global Object | Schedule | SCHED | input | DAYTYPE.NUMWEEKD | The number of weekdays for the day type (given in month/day/year format) | Integer |  |  |  | DAYTYP
8388 | DNAF Object | Short Circuit Calculation | SCCSCC | input | SCCSUBNAME | SCC station name | String
8389 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCVOLTA | Calculated phase A voltage magnitude at the faulted node | Float | SCC | p.u. | p.u.
8390 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCVOLTB | Calculated phase B voltage magnitude at the faulted node | Float | SCC | p.u. | p.u.
8391 | DNAF Object | Short Circuit Calculation | SCCSCC | output | SCCVOLTC | Calculated phase C voltage magnitude at the faulted node | Float | SCC | p.u. | p.u.
8392 | Global Object | Schedule | SCHED | input | LOADGEN.ID | ID of the schedule | String |  |  |  | DNMOBJ
8393 | Global Object | Schedule | SCHED | input | LOADGEN.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8394 | Global Object | Schedule | SCHED | input | LOADGEN.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8395 | Global Object | Schedule | SCHED | input | LOADGEN.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8396 | Global Object | Schedule | SCHED | input | LOADGEN.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8397 | Global Object | Schedule | SCHED | input | LOADGEN.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8398 | Global Object | Schedule | SCHED | input | LOADGEN.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8399 | Global Object | Schedule | SCHED | input | LOADGEN.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8400 | Global Object | Schedule | SCHED | input | LOADGEN.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8401 | Global Object | Schedule | SCHED | input | LOADGEN.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8402 | Global Object | Schedule | SCHED | input | LOADGEN.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8403 | Global Object | Schedule | SCHED | input | LOADGEN.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8404 | Global Object | Schedule | SCHED | input | LOADGEN.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8405 | Global Object | Schedule | SCHED | input | CLDLDSCH | Associated cold load schedule (only for a load schedule). This field is optional. | String
8406 | Global Object | Schedule | SCHED | input | DAYTYPE | Associated day type (for a load schedule only). | String
8407 | Global Object | Schedule | SCHED | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8408 | Global Object | Schedule | SCHED |  | LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer
8409 | Global Object | Schedule | SCHED | input | LOADCATSFORLDSCHEDULE | Name of associated load category. | String
8410 | Global Object | Schedule | SCHED | input | LOADGEN | Pointer to the load embedded generation schedule | String
8411 | Global Object | Schedule | SCHED | input | SEASON.AENDDT | Season end date | String |  |  |  | SEASON
8412 | Global Object | Schedule | SCHED | input | SEASON.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8413 | Global Object | Schedule | SCHED | input | SEASON.ASTARTDT | Season start date | String |  |  |  | SEASON
8414 | Global Object | Schedule | SCHED | input | SEASON.DESCRIPT | Season description | String |  |  |  | SEASON
8415 | Global Object | Schedule | SCHED | input | SEASON.ID | Season unique ID | String |  |  |  | DNMOBJ
8416 | Global Object | Schedule | SCHED | input | SEASON.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
8417 | Global Object | Schedule | SCHED | input | NAME | Object name | String |  |  |  | DNMOBJ
8418 | Global Object | Schedule | SCHED |  | NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale. | Boolean
8419 | Global Object | Schedule | SCHED | input | SKPTARRY.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8420 | Global Object | Schedule | SCHED | input | SKPTARRY.XVALUE | X value | Float |  |  |  | SCHPNT
8421 | Global Object | Schedule | SCHED | input | SKPTARRY.YVALUEO | First y value | Float |  |  |  | SCHPNT
8422 | Global Object | Schedule | SCHED | input | SKPTARRY.YVALUET | Second y value | Float |  |  |  | SCHPNT
8423 | Global Object | Schedule | SCHED |  | NUMSKPNT | Number of schedule points. | Integer
8424 | Global Object | Schedule | SCHED | input | TEMPSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
8425 | Global Object | Schedule | SCHED | input | TEMPSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8426 | Global Object | Schedule | SCHED | input | TEMPSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8427 | Global Object | Schedule | SCHED | input | TEMPSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8428 | Global Object | Schedule | SCHED | input | TEMPSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8429 | Global Object | Schedule | SCHED | input | TEMPSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8430 | Global Object | Schedule | SCHED | input | TEMPSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8431 | Global Object | Schedule | SCHED | input | TEMPSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String
8432 | Global Object | Schedule | SCHED | input | TEMPSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8433 | Global Object | Schedule | SCHED | input | TEMPSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8434 | Global Object | Schedule | SCHED | input | TEMPSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8435 | Global Object | Schedule | SCHED | input | TEMPSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8436 | Global Object | Schedule | SCHED | input | TEMPSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8437 | Global Object | Schedule | SCHED |  | PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only). | Boolean
8438 | Global Object | Schedule | SCHED | input | SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String
8439 | Global Object | Schedule | SCHED | input | SEASON | Associated season (for a load schedule only). | String
8440 | Global Object | Schedule | SCHED |  | SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer
8441 | Global Object | Schedule | SCHED | input | SKPTARRY | Associated array of schedule points. | String
8442 | Global Object | Schedule | SCHED | input | TEMPSCH | Associated temperature adjustment schedule (only for a load schedule). This field is optional. | String
8443 | Global Object | Schedule | SCHED |  | XAXTYPE | Type of value on x axis (time for a load schedule). | String
8444 | Global Object | Schedule | SCHED |  | XUNITS | X axis units (hours for a load schedule). | String
8445 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.ID | ID of the schedule | String |  |  |  | DNMOBJ
8446 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8447 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8448 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8449 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8450 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8451 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8452 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8453 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8454 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8455 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8456 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8457 | Global Object | Schedule Point | SCHPNT | input | SCHEDULE.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8458 | Global Object | Schedule | SCHED |  | YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule). | String
8459 | Global Object | Schedule | SCHED |  | YUNITONE | Y1 axis units. | String
8460 | Global Object | Schedule | SCHED |  | YUNITTWO | Y2 axis units. | String
8461 | Global Object | Schedule Point | SCHPNT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8462 | Global Object | Schedule Point | SCHPNT | input | NAME | Object name | String |  |  |  | DNMOBJ
8463 | Global Object | Schedule Point | SCHPNT |  | SCHEDULE | Associated schedule. | String
8464 | Global Object | Schedule Point | SCHPNT |  | XVALUE | X value. | Float
8465 | Global Object | Schedule Point | SCHPNT |  | YVALUEO | First y value. | Float
8466 | Global Object | Schedule Point | SCHPNT |  | YVALUET | Second y value. | Float
8467 | Global Object | Season | SEASON |  | AENDDT | Season end date (month/day). | String
8468 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8469 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
8470 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8471 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8472 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
8473 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8474 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.NAME | Name of the object | String |  |  |  | DNMOBJ
8475 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8476 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8477 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8478 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES.SERNOMVOLT | Nominal rating | Float |  | kV | kV | SERIES
8479 | Global Object | Season | SEASON |  | ASTARTDT | Season start date (month/day). | String
8480 | Global Object | Season | SEASON |  | DESCRIPT | Description of season. | String
8481 | Global Object | Season | SEASON | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8482 | Global Object | Season | SEASON |  | iNumDateRanges | The number of data ranges for the season. | Integer
8483 | Global Object | Season | SEASON | input | NAME | Object name | String |  |  |  | DNMOBJ
8484 | DNOM Component Placement | Series Label Placement | SELBPL | input | SERIES | Pointer to the associated series reactor | String
8485 | Virtual Object | Specific Combination of Branch | SELECTBR | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
8486 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHPAABS | Real power flow value of Phase A (absolute value). | Float
8487 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHPBABS | Real power flow value of Phase B (absolute value). | Float
8488 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHPCABS | Real power flow value of Phase C (absolute value). | Float
8489 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQAABS | Reactive flow value of Phase A (absolute value). | Float
8490 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQARELATIVE | Relative value of phase A reactive power flow (kVAR). | Float
8491 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQBABS | Reactive flow value of Phase B (absolute value). | Float
8492 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQBRELATIVE | Relative value of phase B reactive power flow (kVAR). | Float
8493 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQCABS | Reactive flow value of Phase C (absolute value). | Float
8494 | DNOM Component | Sensor | SENSOR | input | ADDRESS.NOAPPSTR | Address of the object | String |  |  |  | NDPFST
8495 | Virtual Object | Specific Combination of Branch | SELECTBR | output | BRANCHQCRELATIVE | Relative value of phase C reactive power flow (kVAR). | Float
8496 | Virtual Object | Specific Combination of Branch | SELECTBR | output | CALCULATEFLOW | Specifies whether the flow through the device is calculated by the Distribution Power Flow (DPF) and the flow direction is determined. | Boolean
8497 | Virtual Object | Specific Combination of Branch | SELECTBR | output | KVAR3PHABS | Reactive flow value of Phase A, B and C (absolute value). | Float
8498 | Virtual Object | Specific Combination of Branch | SELECTBR | output | KVAR3PHRELATIVE | Relative value of phase ABC reactive power flow (kVAR). | Float
8499 | Virtual Object | Specific Combination of Branch | SELECTBR | output | KW3PHABS | Real flow value of Phase A, B and C (absolute value). | Float
8500 | DNOM Component | Sensor | SENSOR | input | ADDRESS | Address | String |  |  |  | NDPFST
8501 | DNOM Component | Sensor | SENSOR | input | ALTID | Alternate ID of the sensor | String
8502 | DNOM Component | Sensor | SENSOR | input | FAULTIND.AMPRATE | Device rating | Float |  | Amps | Amps | FLTIND
8503 | DNOM Component | Sensor | SENSOR | input | FAULTIND.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8504 | DNOM Component | Sensor | SENSOR | input | FAULTIND.COMBITMK | Bitmask which contains overhead/unerground flag and potentially other attributes. | Integer |  |  |  | COMELC
8505 | DNOM Component | Sensor | SENSOR | input | FAULTIND.DIRECTIONA | A flag indicating that the fault indicator is directional | Boolean |  |  |  | FLTIND
8506 | DNOM Component | Sensor | SENSOR | input | FAULTIND.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8507 | DNOM Component | Sensor | SENSOR | input | FAULTIND.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8508 | DNOM Component | Sensor | SENSOR | input | FAULTIND.ENUMTYPE | Fault detector type. 1 = Automatic, 2 = Manual, 3 = Remote 4 = Arc Suppression Coil. | Integer |  |  |  | FLTIND
8509 | DNOM Component | Sensor | SENSOR | input | FAULTIND.FUTURE | The future construction phasing information.The enumeration is A = 1, B = 2, C = 4, and N = 8. | Integer |  |  |  | COMELC
8510 | DNOM Component | Sensor | SENSOR | input | FAULTIND.ID | ID of the object | String |  |  |  | DNMOBJ
8511 | DNOM Component | Sensor | SENSOR | input | FAULTIND.NAME | Object name | String |  |  |  | DNMOBJ
8512 | DNOM Component | Sensor | SENSOR | input | FAULTIND.PHASEAGNOSTICFAULTINDICATION | A flag indicating fault indicator's awareness about the faulted phase | Boolean |  |  |  | FLTIND
8513 | DNOM Component | Sensor | SENSOR | input | FAULTIND.PHASING | Connection phases + meas flags. | Integer |  |  |  | FLTIND
8514 | DNOM Component | Sensor | SENSOR | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8515 | DNOM Component | Sensor | SENSOR | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
8516 | DNOM Component | Sensor | SENSOR | input | FLOWBRANCH.BOUNDARY | The boundary flag | Integer
8517 | DNOM Component | Sensor | SENSOR |  | FLOWBRANCH.TERMFR. | From end terminal | Enumeration
8518 | DNOM Component | Sensor | SENSOR |  | FLOWBRANCH.TERMTO. | To end terminal | Enumeration
8519 | DNOM Component | Sensor | SENSOR |  | DNOMTABNAME | The DNOM table name of the sensor | String
8520 | DNOM Component | Sensor | SENSOR | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8521 | DNOM Component | Sensor | SENSOR | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8522 | DNOM Component | Sensor | SENSOR | input | FAULTIND | Pointer to the associated fault indicator | String
8523 | DNOM Component | Sensor | SENSOR |  | FAULTINDSETSTATUS | Fault indicator status (SET,UNSET) | String
8524 | DNOM Component | Sensor | SENSOR | input | Node.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
8525 | DNOM Component | Sensor | SENSOR | input | Node.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
8526 | DNOM Component | Sensor | SENSOR | input | Node.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
8527 | DNOM Component | Sensor | SENSOR | input | Node.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
8528 | DNOM Component | Sensor | SENSOR | input | Node.ID | ID of the node | String |  |  |  | DNMOBJ
8529 | DNOM Component | Sensor | SENSOR | input | Node.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8530 | DNOM Component | Sensor | SENSOR | input | Node.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8531 | DNOM Component | Sensor | SENSOR | input | Node.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8532 | DNOM Component | Sensor | SENSOR | input | Node.VOLTCALC | Node mask | Integer |  |  |  | NODE
8533 | DNOM Component | Sensor | SENSOR | input | FLOWBRANCH | Pointer to the flow branch | String
8534 | DNOM Component | Sensor | SENSOR |  | FLOWBRANCHID | Flow branch Id if pointer is set | String
8535 | DNOM Component | Sensor | SENSOR | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8536 | DNOM Component | Sensor | SENSOR | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8537 | DNOM Component | Sensor | SENSOR | input | NAME | Object name | String |  |  |  | DNMOBJ
8538 | DNOM Component | Sensor | SENSOR | input | Node | Pointer to the associated node | String
8539 | DNOM Component | Sensor | SENSOR | input | NODEID | ID of the sensor node | String
8540 | DNOM Component | Sensor | SENSOR | input | NODENUM | Node name | String
8541 | DNOM Component | Sensor | SENSOR | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
8542 | DNOM Component | Sensor | SENSOR | input | PHASING | Sensor phases | String
8543 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSMEAS | Phase ABC current measurement | String
8544 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSMEASA | Phase A current measurement | String
8545 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSMEASB | Phase B current measurement | String
8546 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSMEASC | Phase C current measurement | String
8547 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSMEASG | Phase G current measurement | String
8548 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSPF | Phase ABC current PF result | String
8549 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSPFA | Phase A current PF result | String
8550 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSPFB | Phase B current PF result | String
8551 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSPFC | Phase C current PF result | String
8552 | DNOM Component | Sensor | SENSOR | output | SENSORAMPSPFG | Phase G current PF result | String
8553 | DNOM Component | Sensor | SENSOR |  | SENSORFCURRMEAS | Phase ABC fault current measurement | String
8554 | DNOM Component | Sensor | SENSOR |  | SENSORFCURRMEASA | Phase A fault current measurement | String
8555 | DNOM Component | Sensor | SENSOR |  | SENSORFCURRMEASB | Phase B fault current measurement | String
8556 | DNOM Component | Sensor | SENSOR |  | SENSORFCURRMEASC | Phase C fault current measurement | String
8557 | DNOM Component | Sensor | SENSOR |  | SENSORFCURRMEASG | Sensor fault indicator measurement, neutral | String
8558 | DNOM Component | Sensor | SENSOR | output | SENSORFINDMEASA | Phase A fault status measurement | String
8559 | DNOM Component | Sensor | SENSOR | output | SENSORFINDMEASABC | Phase ABC fault status measurement | String
8560 | DNOM Component | Sensor | SENSOR | output | SENSORFINDMEASB | Phase B fault status measurement | String
8561 | DNOM Component | Sensor | SENSOR | output | SENSORFINDMEASC | Phase C fault status measurement | String
8562 | DNOM Component | Sensor | SENSOR | output | SENSORFINDMEASG | Phase G fault status measurement | String
8563 | DNOM Component | Sensor | SENSOR |  | SENSORKVADPF | Sensor KVA DPF | String
8564 | DNOM Component | Sensor | SENSOR |  | SENSORKVADPFA | Sensor KVA DPF, phase A | String
8565 | DNOM Component | Sensor | SENSOR |  | SENSORKVADPFB | Sensor KVA DPF, phase B | String
8566 | DNOM Component | Sensor | SENSOR |  | SENSORKVADPFC | Sensor KVA DPF, phase C | String
8567 | DNOM Component | Sensor | SENSOR |  | SENSORKVADPFG | Sensor KVA DPF, neutral | String
8568 | DNOM Component | Sensor | SENSOR |  | SENSORSUBNAME | Name of the substation the sensor belongs to | String
8569 | DNOM Component | Sensor | SENSOR |  | SENSORTYPE | Sensor type | Enumeration
8570 | DNOM Component | Sensor | SENSOR | output | SENSORVAMEAS | Phase ABC apparent power measurement | String
8571 | DNOM Component | Sensor | SENSOR | output | SENSORVAMEASA | Phase A apparent power measurement | String
8572 | DNOM Component | Sensor | SENSOR | output | SENSORVAMEASB | Phase B apparent power measurement | String
8573 | DNOM Component | Sensor | SENSOR | output | SENSORVAMEASC | Phase C apparent power measurement | String
8574 | DNOM Component | Sensor | SENSOR | output | SENSORVAMEASG | Phase G apparent power measurement | String
8575 | DNOM Component | Sensor | SENSOR | output | SENSORVARSMEAS | Phase ABC reactive power measurement | String
8576 | DNOM Component | Sensor | SENSOR | output | SENSORVARSMEASA | Phase A reactive power measurement | String
8577 | DNOM Component | Sensor | SENSOR | output | SENSORVARSMEASB | Phase B reactive power measurement | String
8578 | DNOM Component | Sensor | SENSOR | output | SENSORVARSMEASC | Phase C reactive power measurement | String
8579 | DNOM Component | Sensor | SENSOR | output | SENSORVARSMEASG | Phase G reactive power measurement | String
8580 | DNOM Component | Sensor | SENSOR | output | SENSORVARSPF | Phase ABC reactive power PF result | String
8581 | DNOM Component | Sensor | SENSOR | output | SENSORVARSPFA | Phase A reactive power PF result | String
8582 | DNOM Component | Sensor | SENSOR | output | SENSORVARSPFB | Phase B reactive power PF result | String
8583 | DNOM Component | Sensor | SENSOR | output | SENSORVARSPFC | Phase C reactive power PF result | String
8584 | DNOM Component | Sensor | SENSOR | output | SENSORVARSPFG | Phase G reactive power PF result | String
8585 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSMEAS | Phase ABC voltage measurement | String
8586 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSMEASA | Phase A voltage measurement | String
8587 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSMEASB | Phase B voltage measurement | String
8588 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSMEASC | Phase C voltage measurement | String
8589 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSMEASG | Phase G voltage measurement | String
8590 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPF | Phase ABC voltage PF result | String
8591 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFA | Phase A voltage PF result | String
8592 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFAACTUAL | Phase A voltage PF result in actual voltage base | String
8593 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFACTUAL | Phase ABC voltage PF result in actual voltage base | String
8594 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFALG | Phase A LG voltage PF result | String
8595 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFALL | Phase A LL voltage PF result | String
8596 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFB | Phase B voltage PF result | String
8597 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFBACTUAL | Phase B voltage PF result in actual voltage base | String
8598 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFBLG | Phase B LG voltage PF result | String
8599 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFBLL | Phase B LL voltage PF result | String
8600 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFC | Phase C voltage PF result | String
8601 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFCACTUAL | Phase C voltage PF result in actual voltage base | String
8602 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFCLG | Phase C LG voltage PF result | String
8603 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFCLL | Phase C LL voltage PF result | String
8604 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFG | Phase G voltage PF result | String
8605 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFGACTUAL | Phase G voltage PF result in actual voltage base | String
8606 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFGLG | Phase G LG voltage PF result | String
8607 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFGLL | Phase G LL voltage PF result | String
8608 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFLG | Phase ABC LG voltage PF result | String
8609 | DNOM Component | Sensor | SENSOR | output | SENSORVLTSPFLL | Phase ABC LL voltage PF result | String
8610 | DNOM Component | Sensor | SENSOR |  | SENSORVOLTLEVEL | Sensor line to line and line to ground voltage levels | Float
8611 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSMEAS | Phase ABC real power measurement | String
8612 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSMEASA | Phase A real power measurement | String
8613 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSMEASB | Phase B real power measurement | String
8614 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSMEASC | Phase C real power measurement | String
8615 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSMEASG | Phase G real power measurement | String
8616 | DNOM Component | Sensor | SENSOR | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
8617 | DNOM Component | Sensor | SENSOR | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
8618 | DNOM Component | Sensor | SENSOR | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
8619 | DNOM Component | Sensor | SENSOR | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
8620 | DNOM Component | Sensor | SENSOR | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
8621 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSPF | Phase ABC real power PF result | String
8622 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSPFA | Phase A real power PF result | String
8623 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSPFB | Phase B real power PF result | String
8624 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSPFC | Phase C real power PF result | String
8625 | DNOM Component | Sensor | SENSOR | output | SENSORWATTSPFG | Phase G real power PF result | String
8626 | DNOM Component | Sensor | SENSOR | input | SERVCNTR | Pointer to the associated service center | String
8627 | DNOM Component | Sensor | SENSOR | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8628 | DNOM Component | Sensor | SENSOR | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8629 | DNOM Component | Series Reactor | SERIES | output | AMPANDANGLEA | From end phase A current (magnitude and angle). | Float | DPF | Amps | Amps
8630 | DNOM Component | Series Reactor | SERIES | output | AMPANDANGLEB | From end phase B current (magnitude and angle). | Float | DPF | Amps | Amps
8631 | DNOM Component | Series Reactor | SERIES | output | AMPANDANGLEC | From end phase C current (magnitude and angle). | Float | DPF | Amps | Amps
8632 | DNOM Component | Series Reactor | SERIES | output | AMPANDANGLEN | From end phase N current (magnitude and angle). | Float | DPF | Amps | Amps
8633 | DNOM Component | Series Reactor | SERIES | output | AMPANDANGLENEUT | Vector Sum of the Amp flow on the Individual phases on the From Side (magnitude and angle) | Float | DPF
8634 | DNOM Component | Series Reactor | SERIES | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8635 | DNOM Component | Series Reactor | SERIES | input | BOUNDARY | The boundary flag, NTP flags, and DPF Flag are masked for memory savings | Integer
8636 | DNOM Component | Series Reactor | SERIES | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
8637 | DNOM Component | Series Reactor | SERIES | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8638 | DNOM Component | Series Reactor | SERIES | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8639 | DNOM Component | Series Reactor | SERIES | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
8640 | DNOM Component | Series Reactor | SERIES |  | HASMANUALENTRY | Indicates if manual entry exists | Boolean
8641 | DNOM Component | Series Reactor | SERIES | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8642 | DNOM Component | Series Reactor | SERIES |  | IFROMA | Phase A current injected at from end of line into the line | Float |  | Amps | Amps
8643 | DNOM Component | Series Reactor | SERIES |  | IFROMB | Phase B current injected at from end of line into the line | Float |  | Amps | Amps
8644 | DNOM Component | Series Reactor | SERIES |  | IFROMC | Phase C current injected at from end of line into the line | Float |  | Amps | Amps
8645 | DNOM Component | Series Reactor | SERIES |  | IFROMN | Phase N current injected at from end of line into the line | Float |  | Amps | Amps
8646 | DNOM Component | Series Reactor | SERIES |  | ITOA | Phase A current injected at to end of line into the line | Float |  | Amps | Amps
8647 | DNOM Component | Series Reactor | SERIES |  | ITOB | Phase B current injected at to end of line into the line | Float |  | Amps | Amps
8648 | DNOM Component | Series Reactor | SERIES | input | MODEL.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8649 | DNOM Component | Series Reactor | SERIES | input | MODEL.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | SERMOD
8650 | DNOM Component | Series Reactor | SERIES | input | MODEL.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | SERMOD
8651 | DNOM Component | Series Reactor | SERIES | input | MODEL.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | SERMOD
8652 | DNOM Component | Series Reactor | SERIES | input | MODEL.LIMVALUE | The value of the limit | Float |  | Amps or kVA | Amps or kVA | SERMOD
8653 | DNOM Component | Series Reactor | SERIES | input | MODEL.NAME | Associated series reactor model name. | String
8654 | DNOM Component | Series Reactor | SERIES | input | MODEL.NUMLIMIT | The number of operation limits | Integer |  |  |  | SERMOD
8655 | DNOM Component | Series Reactor | SERIES | input | MODEL.R | Nominal resistance | Float |  | Ohms | Ohms | SERMOD
8656 | DNOM Component | Series Reactor | SERIES | input | MODEL.X | Nominal reactance | Float |  | Ohms | Ohms | SERMOD
8657 | DNOM Component | Series Reactor | SERIES |  | ITOC | Phase C current injected at to end of line into the line | Float |  | Amps | Amps
8658 | DNOM Component | Series Reactor | SERIES |  | ITON | Phase N current injected at to end of line into the line | Float |  | Amps | Amps
8659 | DNOM Component | Series Reactor | SERIES |  | LIMFLAGS | Number of limit violations | Integer
8660 | DNOM Component | Series Reactor | SERIES | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8661 | DNOM Component | Series Reactor | SERIES |  | LOSS | Total line loss (Loss Analysis application results) | Float |  | kVA | kVA
8662 | DNOM Component | Series Reactor | SERIES | input | MODEL | Pointer to the reactor model | String
8663 | DNOM Component | Series Reactor | SERIES | input | NAME | Object name | String |  |  |  | DNMOBJ
8664 | DNOM Component | Series Reactor | SERIES | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8665 | DNOM Component | Series Reactor | SERIES | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8666 | DNOM Component | Series Reactor | SERIES | input | NOMVOLT | Nominal voltage level (kV line to ground). | Float
8667 | DNOM Component | Series Reactor | SERIES | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8668 | DNOM Component | Series Reactor | SERIES |  | PQFROMA | Phase A power injected at from end of line into the line | Float |  | kVA | KVA
8669 | DNOM Component | Series Reactor | SERIES |  | PQFROMB | Phase B power injected at from end of line into the line | Float |  | kVA | KVA
8670 | DNOM Component | Series Reactor | SERIES |  | PQFROMC | Phase C power injected at from end of line into the line | Float |  | kVA | KVA
8671 | DNOM Component | Series Reactor | SERIES |  | PQFROMN | Phase N power injected at from end of line into the line | Float |  | kVA | KVA
8672 | DNOM Component | Series Reactor | SERIES |  | PQTOA | Phase A power injected at to end of line into the line | Float |  | kVA | KVA
8673 | DNOM Component | Series Reactor | SERIES |  | PQTOB | Phase B power injected at to end of line into the line | Float |  | kVA | KVA
8674 | DNOM Component | Series Reactor | SERIES |  | PQTOC | Phase C power injected at to end of line into the line | Float |  | kVA | KVA
8675 | DNOM Component | Series Reactor | SERIES |  | PQTON | Phase N power injected at to end of line into the line | Float |  | kVA | KVA
8676 | DNOM Component | Series Reactor | SERIES |  | REACTORHASMANFLOWLIM | Indicates the manual flow limit | Boolean
8677 | DNOM Component | Series Reactor | SERIES |  | REACTORMANFLOWLIM | Manual flow limit | String
8678 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJAVAILCAPAMP1 | Level 1 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
8679 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJAVAILCAPAMP2 | Level 2 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
8680 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJAVAILCAPAMP3 | Level 3 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
8681 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJAVAILCAPAMP4 | Level 4 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
8682 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJAVAILCAPAMP5 | Level 5 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
8683 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJFLOWA | Phase A calculated Amps plus reserved capacity on phase A. | String |  | Amps | Amps
8684 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJFLOWB | Phase B calculated Amps plus reserved capacity on phase B. | String |  | Amps | Amps
8685 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJFLOWC | Phase C calculated Amps plus reserved capacity on phase C. | String |  | Amps | Amps
8686 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJLOADING1 | Percentage loading using level 1 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
8687 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJLOADING2 | Percentage loading using level 2 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
8688 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJLOADING3 | Percentage loading using level 3 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
8689 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJLOADING4 | Percentage loading using level 4 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
8690 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYADJLOADING5 | Percentage loading using level 5 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
8691 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYAMPA | Reserved capacity on phase A due to reserved capacity objects. | String |  | Amps | Amps
8692 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYAMPB | Reserved capacity on phase B due to reserved capacity objects. | String |  | Amps | Amps
8693 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYAMPC | Reserved capacity on phase C due to reserved capacity objects. | String |  | Amps | Amps
8694 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYDERATEDLIMITLOADING1 | Percentage loading using de-rated level 1 Amp limit and maximum calculated phase amps. | String |  | % | %
8695 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYDERATEDLIMITLOADING2 | Percentage loading using de-rated level 2 Amp limit and maximum calculated phase amps. | String |  | % | %
8696 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYDERATEDLIMITLOADING3 | Percentage loading using de-rated level 3 Amp limit and maximum calculated phase amps. | String |  | % | %
8697 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYDERATEDLIMITLOADING4 | Percentage loading using de-rated level 4 Amp limit and maximum calculated phase amps. | String |  | % | %
8698 | DNOM Component | Series Reactor | SERIES |  | RESERVEDCAPACITYDERATEDLIMITLOADING5 | Percentage loading using de-rated level 5 Amp limit and maximum calculated phase amps. | String |  | % | %
8699 | DNOM Component | Series Reactor | SERIES | input | SERDERATEDLIM1 | Series derated limit 1 | String
8700 | DNOM Component | Series Reactor | SERIES | input | SERDERATEDLIM2 | Series derated limit 2 | String
8701 | DNOM Component | Series Reactor | SERIES | input | SERDERATEDLIM3 | Series derated limit 3 | String
8702 | DNOM Component | Series Reactor | SERIES | input | SERDERATEDLIM4 | Series derated limit 4 | String
8703 | DNOM Component | Series Reactor | SERIES | input | SERDERATEDLIM5 | Series derated limit 5 | String
8704 | DNOM Component | Series Reactor | SERIES | input | SERLIM1 | Level 1 Limit A | String
8705 | DNOM Component | Series Reactor | SERIES | input | SERLIM1NAME | Level 1 Limit Name | String
8706 | DNOM Component | Series Reactor | SERIES | input | SERLIM1SEASON | Level 1 limit season name. | String
8707 | DNOM Component | Series Reactor | SERIES | input | SERLIM2 | Level 2 Limit A | String
8708 | DNOM Component | Series Reactor | SERIES | input | SERLIM2NAME | Level 2 Limit Name | String
8709 | DNOM Component | Series Reactor | SERIES | input | SERLIM2SEASON | Level 2 limit season name. | String
8710 | DNOM Component | Series Reactor | SERIES | input | SERLIM3 | Level 3 Limit A | String
8711 | DNOM Component | Series Reactor | SERIES | input | SERLIM3NAME | Level 3 Limit Name | String
8712 | DNOM Component | Series Reactor | SERIES | input | SERLIM3SEASON | Level 3 limit season name. | String
8713 | DNOM Component | Series Reactor | SERIES | input | SERLIM4 | Level 4 Limit A | String
8714 | DNOM Component | Series Reactor | SERIES | input | SERVCNTR.NAME | Service center name. | String
8715 | DNOM Component | Series Reactor | SERIES | input | SERLIM4NAME | Level 4 Limit Name | String
8716 | DNOM Component | Series Reactor | SERIES | input | SERLIM4SEASON | Level 4 limit season name. | String
8717 | DNOM Component | Series Reactor | SERIES | input | SERLIM5 | Level 5 Limit A | String
8718 | DNOM Component | Series Reactor | SERIES | input | SERLIM5NAME | Level 5 Limit Name | String
8719 | DNOM Component | Series Reactor | SERIES | input | SERLIM5SEASON | Level 5 limit season name. | String
8720 | DNOM Component | Series Reactor | SERIES | input | SERNOMVOLT | Nominal kV rating | Float
8721 | DNOM Component | Series Reactor | SERIES | output | TONODEAMPA | To end phase A current (magnitude and angle). | Float | DPF | Amps | Amps
8722 | DNOM Component | Series Reactor | SERIES | output | TONODEAMPB | To end phase B current (magnitude and angle). | Float | DPF | Amps | Amps
8723 | DNOM Component | Series Reactor | SERIES | output | TONODEAMPC | To end phase C current (magnitude and angle). | Float | DPF | Amps | Amps
8724 | DNOM Component | Series Reactor | SERIES | output | TONODEAMPN | To end phase N current (magnitude and angle). | Float | DPF | Amps | Amps
8725 | DNOM Component | Series Reactor | SERIES | output | TONODEAMPNEUT | Vector Summation of the To end phase A,B,C current flows (magnitude and angle) | Float | DPF
8726 | DNOM Component | Series Reactor | SERIES | output | VOLTANDANGLEANA | From end phase A voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
8727 | DNOM Component | Series Reactor | SERIES | output | VOLTANDANGLEANB | From end phase B voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
8728 | DNOM Component | Series Reactor | SERIES | output | VOLTANDANGLEANC | From end phase C voltage (magnitude on configurable voltage base and angle). | Float | DPF | Volt | Volt
8729 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.AENDDT | Season end date | String |  |  |  | SEASON
8730 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8731 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.ASTARTDT | Season start date | String |  |  |  | SEASON
8732 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.DESCRIPT | Season description | String |  |  |  | SEASON
8733 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.ID | Season unique ID | String |  |  |  | DNMOBJ
8734 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
8735 | DNOM Component | Series Reactor | SERIES | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
8736 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.ID | ID of the schedule | String |  |  |  | DNMOBJ
8737 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8738 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8739 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8740 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8741 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8742 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8743 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8744 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8745 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8746 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8747 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8748 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8749 | DNOM Component | Series Reactor | SERIES | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
8750 | Global Object | Series Reactor Model | SERMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8751 | Global Object | Series Reactor Model | SERMOD |  | LIMITEVENT | A flag indicating operational limit event | Boolean
8752 | Global Object | Series Reactor Model | SERMOD |  | LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term). | String
8753 | Global Object | Series Reactor Model | SERMOD | input | LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String
8754 | Global Object | Series Reactor Model | SERMOD | input | LIMTEMP | Array of temporary schedules | String
8755 | Global Object | Series Reactor Model | SERMOD |  | LIMUNIT | Enumerated limit units, 1 = amps, 2 = kVA. | Integer
8756 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8757 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
8758 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8759 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8760 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
8761 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8762 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.NAME | Name of the object | String |  |  |  | DNMOBJ
8763 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8764 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8765 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8766 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES.SERNOMVOLT | Nominal rating | Float |  | kV | kV | SERIES
8767 | Global Object | Series Reactor Model | SERMOD |  | LIMVALUE | The value of the limit (in amps or kVA). | Float
8768 | Global Object | Series Reactor Model | SERMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
8769 | Global Object | Series Reactor Model | SERMOD |  | NUMLIMIT | The number of operation limits. | Integer
8770 | Global Object | Series Reactor Model | SERMOD |  | R | Nominal resistance (ohms). | Float
8771 | Global Object | Series Reactor Model | SERMOD |  | X | Nominal reactance (ohms). | Float
8772 | DNOM Component | Shunt Impedance | SHIMP | input | ADDRESS.NOAPPSTR | Address. | String
8773 | DNOM Component Placement | Series Placement | SERPLE | input | SERIES | Pointer to the associated series reactor | String
8774 | DNOM Component | Protection Settings Group Template | SGTEMPLATE | input | ID | Template ID | String |  |  |  | DNOMOBJ
8775 | DNOM Component | Protection Settings Group Template | SGTEMPLATE | input | NAME | Template name | String
8776 | DNOM Component | Protection Settings Group Template | SGTEMPLATE | input | NUMSETTINGGROUPS | Number of settings groups associated with the template | Integer
8777 | DNOM Component | Protection Settings Group Template | SGTEMPLATE | input | SETTINGGROUPS | Pointer to the associated settings group | String
8778 | DNOM Component | Protection Settings Group Template | SGTEMPLATE | input | SGTDESCRIPTION | Template description | String |  |  |  | DNOMOBJ
8779 | DNOM Component | Shunt Impedance | SHIMP | input | ALTID | Returns the ADDRESS | String
8780 | DNOM Component | Shunt Impedance | SHIMP | output | AMPANDANGLEA | Phase A current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
8781 | DNOM Component | Shunt Impedance | SHIMP | output | AMPANDANGLEB | Phase B current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
8782 | DNOM Component | Shunt Impedance | SHIMP | output | AMPANDANGLEC | Phase C current (magnitude and angle in degrees). | Float | DPF | Amps | Amps
8783 | DNOM Component | Shunt Impedance | SHIMP | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8784 | DNOM Component | Shunt Impedance | SHIMP | input | CAPAUTOMANUAL | Flag indicating if the device is auto or manual. | String
8785 | DNOM Component | Shunt Impedance | SHIMP | input | CAPAUTOMANUALA | Flag indicating if the device is auto or manual for phase A. | String
8786 | DNOM Component | Shunt Impedance | SHIMP | input | CAPAUTOMANUALB | Flag indicating if the device is auto or manual for phase B. | String
8787 | DNOM Component | Shunt Impedance | SHIMP | input | CAPAUTOMANUALC | Flag indicating if the device is auto or manual for phase C. | String
8788 | DNOM Component | Shunt Impedance | SHIMP |  | CAPAUTOMANUALMEASQUAL | Auto/Manual status measurement quality | String
8789 | DNOM Component | Shunt Impedance | SHIMP |  | CAPAUTOMANUALMEASQUALA | Quality of the phase A Auto/Manual status measurement | String
8790 | DNOM Component | Shunt Impedance | SHIMP |  | CAPAUTOMANUALMEASQUALANY | Auto control status | String
8791 | DNOM Component | Shunt Impedance | SHIMP |  | CAPAUTOMANUALMEASQUALB | Quality of the phase B Auto/Manual status measurement | String
8792 | DNOM Component | Shunt Impedance | SHIMP |  | CAPAUTOMANUALMEASQUALC | Quality of the phase C Auto/Manual status measurement | String
8793 | DNOM Component | Shunt Impedance | SHIMP | output | CAPAVGCALVOL | The capacitor's average calculated voltage in heuristic LVM application. | Float
8794 | DNOM Component | Shunt Impedance | SHIMP | output | CAPAVGLOWVOL | The capacitor's lowest average voltage in heuristic LVM application. | Float
8795 | DNOM Component | Shunt Impedance | SHIMP | output | CAPAVGLOWVOLCOMP | The capacitor's lowest average component voltage in heuristic LVM application. | Float
8796 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCOMMSTATUS | Communication status | String
8797 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCONTROLSYSTEM | Capacity control system | String |  | enumeration | enumeration
8798 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRL | Capacitor control system (0 - None, 1 - RCCS Caps, 2-WAY Caps Control System) | Enumeration
8799 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAIL | Control Available status measurement | String
8800 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILA | Control Available status measurement of phase A | String
8801 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILB | Control Available status measurement of phase B | String
8802 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILC | Control Available status measurement of phase C | String
8803 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILMEASQUAL | Control Available status measurement quality | String
8804 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILMEASQUALA | Quality of the phase A Control Available status measurement | String
8805 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILMEASQUALANY | Capacitor control available measurement status and quality | String
8806 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILMEASQUALB | Quality of the phase B Control Available status measurement | String
8807 | DNOM Component | Shunt Impedance | SHIMP |  | CAPCTRLAVAILMEASQUALC | Quality of the phase C Control Available status measurement | String
8808 | DNOM Component | Shunt Impedance | SHIMP |  | CAPDPFLOCALMODE | A flag to indicate that the DPF was solved in the local mode. | Boolean
8809 | DNOM Component | Shunt Impedance | SHIMP | output | CAPESTPF | The capacitor's estimated PF in heuristic LVM application. | Float
8810 | DNOM Component | Shunt Impedance | SHIMP | output | CAPEVALUATED | Flag indiating if the HLVM is evaluated. | Boolean
8811 | DNOM Component | Shunt Impedance | SHIMP | input | CAPHASLOCAL | Whether the device has local control capability | Boolean
8812 | DNOM Component | Shunt Impedance | SHIMP | input | CAPHASREMOTE | Whether the device has remote control capability | Boolean
8813 | DNOM Component | Shunt Impedance | SHIMP | input | CAPHLEVMANOVER | Flag indicating that a manual entry value has been set for the high voltage override. | Boolean
8814 | DNOM Component | Shunt Impedance | SHIMP | input | CAPHLLEVMANOVER | Flag indicating the local controller has a manual entry voltage override. | Boolean
8815 | DNOM Component | Shunt Impedance | SHIMP | input | CAPHOURMANENABLE | Flag indicating that a manual entry value has been set for the time interval between consecutive switching operations. | Boolean
8816 | DNOM Component | Shunt Impedance | SHIMP | input | CAPISOPEN | Flag indicating if the shunt is opened. | Boolean
8817 | DNOM Component | Shunt Impedance | SHIMP | input | CAPLLEVMANOVER | Flag indicating that a manual entry value has been set for the low voltage override. | Boolean
8818 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANNOMSIZE | Manual entry nominal size (kVAr / phase). | Float
8819 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANNOMSIZEENABLED | Flag indicating the nominal size has an manual entry override. | Boolean
8820 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANSCADADSO | DSO status is "SCADA decides" (used for manual entry) | Boolean
8821 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANSWITCOSTOPT | Manual override value of capacitor switching cost | Float
8822 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANUSERDSODISABLED | Flag indicating if "DSO status" is "User disable". (used for manual entry) | Boolean
8823 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMANUSERDSOENABLED | Flag indicating if "DSO status" is "User enable". (used for manual entry) | Boolean
8824 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMAXSWMANENABLE | Flag indicating that a manual entry value has been set for the maximum number of daily switching operations. | Boolean
8825 | DNOM Component | Shunt Impedance | SHIMP |  | CAPMODELSIZE | Capacitor model size | String
8826 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMONIDURATION | Capacitor switching monitored duration (in hours). | Integer |  | Hour | Hour
8827 | DNOM Component | Shunt Impedance | SHIMP | output | CAPMONIENDTIM | Latest Monitor ending time. | String |  | #N/A | #N/A
8828 | DNOM Component | Shunt Impedance | SHIMP | output | CAPMONIENDTIM_TICKS | Latest Monitor ending time. | String
8829 | DNOM Component | Shunt Impedance | SHIMP | output | CAPMONIOPERATIONS | The current number of switching operations since last monintor started. | Integer |  | #N/A | #N/A
8830 | DNOM Component | Shunt Impedance | SHIMP | output | CAPMONISTARTTIM | Latest Monitor starting time. | String |  | #N/A | #N/A
8831 | DNOM Component | Shunt Impedance | SHIMP | output | CAPMONISTARTTIM_TICKS | Latest Monitor starting time. | String
8832 | DNOM Component | Shunt Impedance | SHIMP | input | CAPMULTSTEP | Whether the capacitor has the multi-step capability | Boolean
8833 | DNOM Component | Shunt Impedance | SHIMP | input | CAPNUMDAILYSWITCHOPS | The current number of daily switching operations (count is reset at midnight). | Integer
8834 | DNOM Component | Shunt Impedance | SHIMP | input | CAPONOFFLMANENABLE | Flag indicating that a manual entry value has been set for the On or Off level control value. | Boolean
8835 | DNOM Component | Shunt Impedance | SHIMP | output | CAPPFCOMP | The capacitor's power factor component in heuristic LVM application | Float
8836 | DNOM Component | Shunt Impedance | SHIMP | output | CAPPFMAX | The capacitor's max target PF in heuristic LVM application. | Float
8837 | DNOM Component | Shunt Impedance | SHIMP | output | CAPPFMIN | The capacitor's min target PF in heuristic LVM application. | Float
8838 | DNOM Component | Shunt Impedance | SHIMP | input | CAPPHASEIND | Capacitor phase indicator | Boolean
8839 | DNOM Component | Shunt Impedance | SHIMP |  | CAPREMOTELOCALMEASQUAL | Local/Remote status measurement quality | String
8840 | DNOM Component | Shunt Impedance | SHIMP |  | CAPREMOTELOCALMEASQUALA | Quality of the phase A Local/Remote status measurement | String
8841 | DNOM Component | Shunt Impedance | SHIMP |  | CAPREMOTELOCALMEASQUALANY | Capacitor remote/local measurement status and quality | String
8842 | DNOM Component | Shunt Impedance | SHIMP |  | CAPREMOTELOCALMEASQUALB | Quality of the phase B Local/Remote status measurement | String
8843 | DNOM Component | Shunt Impedance | SHIMP |  | CAPREMOTELOCALMEASQUALC | Quality of the phase C Local/Remote status measurement | String
8844 | DNOM Component | Shunt Impedance | SHIMP | input | CAPSCADADSO | DSO status is "SCADA decides" | Boolean
8845 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSELFORPLAN | Flag indicating if the HLVM plan is generated. | Boolean
8846 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSOLVEDSTEP | Current capacitor position (step). | Integer | DPF | #N/A | #N/A
8847 | DNOM Component | Shunt Impedance | SHIMP | input | CAPSTATUS | Current operation status (enabled/disabled, on/off). | String
8848 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUAL | Quality of the capacitor status measurement | String
8849 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUALA | Quality of the capacitor phase A status measurement | String
8850 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUALANY | Capacitor state measurement status and quality | String
8851 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUALANYID | ID of the capacitor status measurement point | String
8852 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUALB | Quality of the capacitor phase B status measurement | String
8853 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTATUSMEASQUALC | Quality of the capacitor phase C status measurement | String
8854 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTATUSPHASEA | Flag indicating if the phase A status is closed or open. | String
8855 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTATUSPHASEB | Flag indicating if the phase B status is closed or open. | String
8856 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTATUSPHASEC | Flag indicating if the phase C status is closed or open. | String
8857 | DNOM Component | Shunt Impedance | SHIMP | input | CAPSTEP | Current capacitor step value | Integer
8858 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTEPA | Phase A current (final) step for powerflow solution if phases are switched independently. | Integer
8859 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTEPB | Phase B current (final) step for powerflow solution if phases are switched independently. | Integer
8860 | DNOM Component | Shunt Impedance | SHIMP | output | CAPSTEPC | Phase C current (final) step for powerflow solution if phases are switched independently. | Integer
8861 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUAL | Quality of the capacitor current step measurement | String
8862 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUALA | Quality of the capacitor phase A current step measurement | String
8863 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUALANY | Capacitor step measurement status and quality | String
8864 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUALANYID | ID of the capacitor step measurement point | String
8865 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUALB | Quality of the capacitor phase B current step measurement | String
8866 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSTEPMEASQUALC | Quality of the capacitor phase C current step measurement | String
8867 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERCUTOUTMEASQUAL | Supervisory Cutout status measurement quality | String
8868 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERCUTOUTMEASQUALA | Quality of the phase A Supervisory Cutout status measurement | String
8869 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERCUTOUTMEASQUALB | Quality of the phase B Supervisory Cutout status measurement | String
8870 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERCUTOUTMEASQUALC | Quality of the phase C Supervisory Cutout status measurement | String
8871 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERVISORYCUTOUT | Supervisory Cutout status measurement | String
8872 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERVISORYCUTOUTA | Supervisory Cutout status measurement of phase A | String
8873 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERVISORYCUTOUTB | Supervisory Cutout status measurement of phase B | String
8874 | DNOM Component | Shunt Impedance | SHIMP |  | CAPSUPERVISORYCUTOUTC | Supervisory Cutout status measurement of phase C | String
8875 | DNOM Component | Shunt Impedance | SHIMP | input | CAPSWITCOSTOPTMANENABLE | Flag indicating the capacitor switching cost has an manual entry override | Boolean
8876 | DNOM Component | Shunt Impedance | SHIMP | input | CAPTIMELASTSWTCH | Time of last capacitor switching operation. | String
8877 | DNOM Component | Shunt Impedance | SHIMP | output | CAPTIMELASTSWTCH_TICKS | The time of the last switching operation. | String
8878 | DNOM Component | Shunt Impedance | SHIMP | output | CAPTOTALOBJ | The capacitor's total objective in heuristic LVM application. | Float
8879 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
8880 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8881 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8882 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8883 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.NAME | Name of the object | String |  |  |  | DNMOBJ
8884 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.NUMSHIMP | The number of shunt objects contained in the bank | Integer |  |  |  | SHPBK
8885 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.OFSEQBK | Dynamic array of shunt impedance pointers off sequence | Integer |  |  |  | SHPBK
8886 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK.ONSEQBK | Dynamic array of shunt impedance pointers on sequence | Integer |  |  |  | SHPBK
8887 | DNOM Component | Shunt Impedance | SHIMP | output | CAPTOTVOLCHA | Total voltage change for voltage monitoring. | Float
8888 | DNOM Component | Shunt Impedance | SHIMP | output | CAPTOTVOLVIO | Total voltage violation for voltage monitoring. | Float
8889 | DNOM Component | Shunt Impedance | SHIMP | input | CAPUSERDSODISABLED | Flag indicating if "DSO status" is "User disable". | Boolean
8890 | DNOM Component | Shunt Impedance | SHIMP | input | CAPUSERDSOENABLED | Flag indicating if "DSO status" is "User enable". | Boolean
8891 | DNOM Component | Shunt Impedance | SHIMP | output | CAPVRCOMP | The capacitor's voltage reduction component in heuristic LVM application | Float
8892 | DNOM Component | Shunt Impedance | SHIMP | input | CBANK | Pointer to the associated shunt impedance bank | String
8893 | DNOM Component | Shunt Impedance | SHIMP | input | CELLSIZE | Cell size (kVAR). | Float
8894 | DNOM Component | Shunt Impedance | SHIMP | input | CONSSWIT | Time interval between consecutive switching operations (hours). | Float
8895 | DNOM Component | Shunt Impedance | SHIMP | input | CONTROL | Control capability. | Integer
8896 | DNOM Component | Shunt Impedance | SHIMP | input | CTRLOVERTYPE | Local Control override type (none, voltage, time or temperature) | Integer
8897 | DNOM Component | Shunt Impedance | SHIMP |  | DELTACAPACITORAMPA | Delta capacitor current phase A | String
8898 | DNOM Component | Shunt Impedance | SHIMP |  | DELTACAPACITORAMPB | Delta capacitor current phase B | String
8899 | DNOM Component | Shunt Impedance | SHIMP |  | DELTACAPACITORAMPC | Delta capacitor current phase C | String
8900 | DNOM Component | Shunt Impedance | SHIMP | input | DEVICEDSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String
8901 | DNOM Component | Shunt Impedance | SHIMP | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
8902 | DNOM Component | Shunt Impedance | SHIMP | input | DNOMTABNAME | The DNOM table name of the shunt. | String
8903 | DNOM Component | Shunt Impedance | SHIMP | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
8904 | DNOM Component | Shunt Impedance | SHIMP | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
8905 | DNOM Component | Shunt Impedance | SHIMP |  | DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration
8906 | DNOM Component | Shunt Impedance | SHIMP | input | DSOSHIMPCONTROLENABLED | DSO status, such as User Disabled or SCADA Decides | String
8907 | DNOM Component | Shunt Impedance | SHIMP | input | DYNFEEDERNAME | Dynamic (currently energizing) feeder name. | String
8908 | DNOM Component | Shunt Impedance | SHIMP | input | DYNSTATIONNAME | Dynamic (currently energizing) station name. | String
8909 | DNOM Component | Shunt Impedance | SHIMP | input | FEEDERMAIN | Flag indicating if the capacitor is on feeder main. | Boolean
8910 | DNOM Component | Shunt Impedance | SHIMP | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
8911 | DNOM Component | Shunt Impedance | SHIMP | input | GROUNDED | Flag indicating that the capacitor is grounded | Boolean |  |  |  | SHUNT
8912 | DNOM Component | Shunt Impedance | SHIMP |  | HAS_REGULATION_MEAS | A flag indicating that the shunt impedance has the regulation measurement | Boolean
8913 | DNOM Component | Shunt Impedance | SHIMP |  | HAS_REMOTEENABLED_MEAS | A flag indicating that the shunt impedance has the remote enabled measurement | Boolean
8914 | DNOM Component | Shunt Impedance | SHIMP |  | HAS_STATUS_MEAS | A flag indicating that the shunt impedance has the status measurement | Boolean
8915 | DNOM Component | Shunt Impedance | SHIMP | input | HASMANUALENTRY | If one or some fields of shunt has(have) value override. | Boolean
8916 | DNOM Component | Shunt Impedance | SHIMP | input | HLEVOVER | High voltage override value (per unit volts). | Float
8917 | DNOM Component | Shunt Impedance | SHIMP | input | HLLEVOVER | Flag indicating the local controller has an override such as voltage. | Boolean
8918 | DNOM Component | Shunt Impedance | SHIMP | output | HLVMELIGIBLE | Flag indicating if HVM is eligible. | Boolean
8919 | DNOM Component | Shunt Impedance | SHIMP | input | HTLEVOVER | High time/temperature override value. | Float
8920 | DNOM Component | Shunt Impedance | SHIMP | input | ID | Object unique ID | String |  |  |  | DNMOBJ
8921 | DNOM Component | Shunt Impedance | SHIMP |  | IFLOWA | Phase A output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
8922 | DNOM Component | Shunt Impedance | SHIMP |  | IFLOWB | Phase B output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
8923 | DNOM Component | Shunt Impedance | SHIMP |  | IFLOWC | Phase C output current (referenced into the load, out of the bus) | Float |  | Amps | Amps
8924 | DNOM Component | Shunt Impedance | SHIMP | input | ISDYNFEEDERLOOPED | Flag indicating if the dynamic feeder is Looped | Boolean
8925 | DNOM Component | Shunt Impedance | SHIMP |  | LIMFLAGS | Number of limit violations | Integer
8926 | DNOM Component | Shunt Impedance | SHIMP | input | LLEVOVER | Low voltage override value (per unit volts). | Float
8927 | DNOM Component | Shunt Impedance | SHIMP | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
8928 | DNOM Component | Shunt Impedance | SHIMP | input | LOCLCTRL | Local controller type. | Integer
8929 | DNOM Component | Shunt Impedance | SHIMP |  | LOSS | Total line loss (Loss Analysis application results) | Float |  | kVA | kVA
8930 | DNOM Component | Shunt Impedance | SHIMP | input | LTLEVOVER | Low time/temperature override value. | Float
8931 | DNOM Component | Shunt Impedance | SHIMP | output | LVMNOTELIGIBLECOUNT | LVM not eligible counter. | Integer |  | #N/A | #N/A
8932 | DNOM Component | Shunt Impedance | SHIMP | input | MANCONSSWIT | Manually entered value for the time interval between consecutive switching operations. | Float
8933 | DNOM Component | Shunt Impedance | SHIMP | input | MANHLEVOVER | Manually entered value for the high voltage override. | Float
8934 | DNOM Component | Shunt Impedance | SHIMP | input | MANHLLEVOVER | Flag indicating if manual entry the status of voltage override. | Boolean
8935 | DNOM Component | Shunt Impedance | SHIMP | input | MANLLEVOVER | Manually entered value for the low voltage override. | Float
8936 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.CLOSESW | Limit on switching electrically close capacitors (ohms separation) | Float |  |  |  | SHPMOD
8937 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
8938 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.INDPHOPS | Flag indicaitng that multi-phase device has independent phase operation (true - phases operate independently) | Boolean |  |  |  | SHPMOD
8939 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.LIMNAME | An array of limit names | String |  |  |  | SHPMOD
8940 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.LIMUNIT | Limit unit enumeration (1- Amp, 2 - KVA, 3 - MVA) | Enumeration |  |  |  | SHPMOD
8941 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.LIMVALUE | An array of limit values | Integer |  |  |  | SHPMOD
8942 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.NAME | Name of associated shunt impedance model. | String
8943 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.NUMLIMIT | The number of operation limits | Integer |  |  |  | SHPMOD
8944 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.PLOSS | Real power loss | Integer |  | kW | kW | SHPMOD
8945 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL.SWITCOST | Default cost of performing a switching operation | Float |  | $/operation | $/operation | SHPMOD
8946 | DNOM Component | Shunt Impedance | SHIMP | input | MANMAXSWIT | Manually entered value for the maximum number of daily switching operations. | Float
8947 | DNOM Component | Shunt Impedance | SHIMP | input | MANOFFLEVEL | Manually entered value for the off level control value. | Float
8948 | DNOM Component | Shunt Impedance | SHIMP | input | MANONLEVEL | Manually entered value for the on level control value. | Float
8949 | DNOM Component | Shunt Impedance | SHIMP | input | MAXSWIT | Maximum number of daily switching operations. | Integer
8950 | DNOM Component | Shunt Impedance | SHIMP | input | MODEL | Pointer to the associated shunt impedance model | String
8951 | DNOM Component | Shunt Impedance | SHIMP | input | NAME | Object name | String |  |  |  | DNMOBJ
8952 | DNOM Component | Shunt Impedance | SHIMP | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8953 | DNOM Component | Shunt Impedance | SHIMP | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
8954 | DNOM Component | Shunt Impedance | SHIMP | input | NOMVOLT | Nominal voltage level (kV line to ground). | Float
8955 | DNOM Component | Shunt Impedance | SHIMP | input | NORMOPENPHASES | Normal open phases | String
8956 | DNOM Component | Shunt Impedance | SHIMP | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
8957 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
8958 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8959 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8960 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8961 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8962 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8963 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8964 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8965 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8966 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8967 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8968 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8969 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8970 | DNOM Component | Shunt Impedance | SHIMP | input | NUMSTEPS | The number of steps (1 for most capacitors). | Integer
8971 | DNOM Component | Shunt Impedance | SHIMP | input | OFFLEVEL | Off level for locally controlled capacitors. | Float
8972 | DNOM Component | Shunt Impedance | SHIMP | input | ONLEVEL | On level for locally controlled capacitors. | Float
8973 | DNOM Component | Shunt Impedance | SHIMP | input | OPENFIX | Fixed capacitor initial status (true = open/off). | Boolean
8974 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
8975 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
8976 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
8977 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
8978 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
8979 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
8980 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
8981 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
8982 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
8983 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
8984 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
8985 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
8986 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
8987 | DNOM Component | Shunt Impedance | SHIMP | input | OVERSHED | Pointer to the override time/temperature on/off schedule | String
8988 | DNOM Component | Shunt Impedance | SHIMP | input | PERMCTRLLEV1 | Permissive control level 1 | Float
8989 | DNOM Component | Shunt Impedance | SHIMP | input | PERMCTRLLEV2 | Permissive control level 2 | Float
8990 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPASSOCIATEDSWITCH | The name (or ID if the name is not provided) of the associated switching device. | String
8991 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPBANK | The name (or ID if the name is not provided) of the capacitor bank to which this capacitor belongs. | String
8992 | DNOM Component | Shunt Impedance | SHIMP | input | NEXTONSHIMP | The name (or ID if the name is not provided) of the next on capacitor in the capacitor bank, based on the capacitor bank on sequence and the open/closed status of the capacitors in the capacitor bank. | String
8993 | DNOM Component | Shunt Impedance | SHIMP | input | NEXTOFFSHIMP | The name (or ID if the name is not provided) of the next off capacitor in the capacitor bank, based on the capacitor bank off sequence and the open/closed status of the capacitors in the capacitor bank. | String
8994 | DNOM Component | Shunt Impedance | SHIMP | input | ISNEXTONOFFSHIMP | Indicates if this is the next on/off capacitor in the capacitor bank, based on the capacitor bank on/off sequence and the open/closed status of the capacitors in the capacitor bank. | Boolean
8995 | DNOM Component | Shunt Impedance | SHIMP | input | PERMCTRLTYPE | Local control permissive type (none, time or temperature) | Integer
8996 | DNOM Component | Shunt Impedance | SHIMP | input | PERMSHED | Pointer to the permissive time/temperature on/off schedule | String
8997 | DNOM Component | Shunt Impedance | SHIMP | output | PFCOMPTIME | Latest power flow solution time. | String | DPF | #N/A | #N/A
8998 | DNOM Component | Shunt Impedance | SHIMP | input | PHSENSED | Regulation node phases that are sensed. | Integer
8999 | DNOM Component | Shunt Impedance | SHIMP | input | PNOMA | Nominal phase A real power loss. | Float
9000 | DNOM Component | Shunt Impedance | SHIMP | input | PNOMB | Nominal phase B real power loss. | Float
9001 | DNOM Component | Shunt Impedance | SHIMP | input | PNOMC | Nominal phase C real power loss. | Float
9002 | DNOM Component | Shunt Impedance | SHIMP |  | POSSUSPECT | Flag indicating that the local controlled capacitor position is suspect due to a hunting problem | Boolean
9003 | DNOM Component | Shunt Impedance | SHIMP |  | PQFLOWA | Phase A output real power (referenced into the load, out of the bus) | Float |  | kW | kW
9004 | DNOM Component | Shunt Impedance | SHIMP |  | PQFLOWB | Phase B output real power (referenced into the load, out of the bus) | Float |  | kW | kW
9005 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9006 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
9007 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9008 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9009 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9010 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9011 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.NAME | Name of the object | String |  |  |  | DNMOBJ
9012 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9013 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9014 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9015 | DNOM Component | Shunt Impedance | SHIMP |  | PQFLOWC | Phase C output real power (referenced into the load, out of the bus) | Float |  | kW | kW
9016 | DNOM Component | Shunt Impedance | SHIMP | input | QNOMA | Nominal Phase A reactive power value. | Float
9017 | DNOM Component | Shunt Impedance | SHIMP | input | QNOMB | Nominal Phase B reactive power value. | Float
9018 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
9019 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
9020 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
9021 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
9022 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
9023 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9024 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9025 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9026 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
9027 | DNOM Component | Shunt Impedance | SHIMP | input | QNOMC | Nominal Phase C reactive power value. | Float
9028 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9029 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9030 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9031 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9032 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9033 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.NAME | Name of the object | String |  |  |  | DNMOBJ
9034 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9035 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9036 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9037 | DNOM Component | Shunt Impedance | SHIMP | input | REGBR | Pointer to the regulation branch (Amp or VAR local control) | String
9038 | DNOM Component | Shunt Impedance | SHIMP | input | REGBRDIR | Branch flow direction for local regulation. | Integer
9039 | DNOM Component | Shunt Impedance | SHIMP | input | REGEND | Branch flow end for local regulation. | Integer
9040 | DNOM Component | Shunt Impedance | SHIMP | input | REGNODE | Pointer to the associated regulation node | String
9041 | DNOM Component | Shunt Impedance | SHIMP | input | REGTF | Associated transformer with bushing | String
9042 | DNOM Component | Shunt Impedance | SHIMP | input | SERVCNTR.NAME | Service center name. | String
9043 | DNOM Component | Shunt Impedance | SHIMP | input | REGUSEUNREGULATEDNODE | Flag indicating the capacitor uses the unregulated node voltage | Boolean
9044 | DNOM Component | Shunt Impedance | SHIMP |  | REMOTEPHASEA | Remote control of phase A | String
9045 | DNOM Component | Shunt Impedance | SHIMP |  | REMOTEPHASEB | Remote control of phase B | String
9046 | DNOM Component | Shunt Impedance | SHIMP |  | REMOTEPHASEC | Remote control of phase C | String
9047 | DNOM Component | Shunt Impedance | SHIMP | input | RGROUND | Grounding resistance (ohms). | Float
9048 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPAREANAME | Device's area name | String
9049 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPCONNECTION | Wye or delta connection type. | String
9050 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPCONSSWIT | Tim interval (hours) between consecutive switching operations | Float
9051 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPCONSSWITMIN | Tim interval (minutes) between consecutive switching operations | Float
9052 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPCONTROLSCHEME | Control scheme (fixed/local/remote/remote_local). | String
9053 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPCTLSCHM | Capacitor control scheme | String
9054 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPDECSTEP | Value to enable/disable "decrease step" button on the device toolbar according to current status. | String
9055 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPDSOSCADA | Value to enable/disable "scada decides" button on the device toolbar according to current status. | String
9056 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPDSOUSEROFF | Value to enable/disable "DSO disable" button on the device toolbar according to current status. | String
9057 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPDSOUSERON | Value to enable/disable "DSO enable" button on the device toolbar according to current status. | String
9058 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPGROUNDED | Flag indicating a grounded connection (true = grounded). | String
9059 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPHIGHCONTROLLEVEL | Shunt impedance high control level | String
9060 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPINCSTEP | Value to enable/disable "increase step" button on the device toolbar according to current status. | String
9061 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPKVAR | SHIMP total reactive power (kVAR). | Float
9062 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPLOCALREMOTE | Value to enable/disable "toggle local/remote" button on the device toolbar according to current status. | String
9063 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPLOCCONTTYPE | Local control type. | String
9064 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPLOWCONTROLLEVEL | Shunt impedance low control level | String
9065 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPMANOPERABLE | Value to enable/disable “toggle operable” button on the device toolbar according to current status, also used for manual entry. | Boolean
9066 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPMAXSWIT | Maximum number of daily switching operations (can be a manually entered value). | Float
9067 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPMODSCHED1 | Shimp model schedule name 1 | String
9068 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPMODSCHED2 | Shimp model schedule name 2 | String
9069 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPMODSCHED3 | Shimp model schedule name 3 | String
9070 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPMODSCHED4 | Shimp model schedule name 4 | String
9071 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMLOSSA | SHIMP Nominal Power Loss in Watts(phase A) | Float
9072 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMLOSSB | SHIMP Nominal Power Loss in Watts(phase B) | Float
9073 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMLOSSC | SHIMP Nominal Power Loss in Watts(phase C) | Float
9074 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMQA | Phase A nominal VAR injection (kVAR). | Float
9075 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMQB | Phase B nominal VAR injection (kVAR). | Float
9076 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMQC | Phase C nominal VAR injection (kVAR). | Float
9077 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPNOMVOLT | Nominal Voltage. | Float
9078 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPNOMVOVERHIGHLEVEL | Nominal voltage override high level | String
9079 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPNOMVOVERLOWLEVEL | Nominal voltage override low level | String
9080 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPOFFLEVEL | Off level for locally controlled. | Float
9081 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPONLEVEL | On level for locally controlled capacitors. | Float
9082 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPOPERABLE | Value to enable/disable "toggle operable" button on the device toolbar according to current status. | Boolean
9083 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPOPERMODE | Current operation mode (including fixed capacitors). | String
9084 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTIA | Phase A current | Float | DPF | Amps | Amps
9085 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTIAANGLE | Phase A current angle in degrees | Float | DPF | Degree | Degree
9086 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTIB | Phase B current | Float | DPF | Amps | Amps
9087 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTIBANGLE | Phase B current angle in degrees | Float | DPF | Degree | Degree
9088 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTIC | Phase C current | Float | DPF | Amps | Amps
9089 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTICANGLE | Phase C current angle in degrees | Float | DPF | Degree | Degree
9090 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTLOSSW | Total real power loss (kW). | Float | DPF | kW | kW
9091 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTPA | Phase A real power output (loss - kW). | Float | DPF | kW | kW
9092 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTPB | Phase B real power output (loss - kW). | Float | DPF | kW | kW
9093 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTPC | Phase C real power output (loss - kW). | Float | DPF | kW | kW
9094 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTQA | Phase A reactive power output (kVAR). | Float | DPF | kVAR | kVAR
9095 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTQB | Phase B reactive power output (kVAR). | Float | DPF | kVAR | kVAR
9096 | DNOM Component | Shunt Impedance | SHIMP | output | SHIMPOUTQC | Phase C reactive power output (kVAR). | Float | DPF | kVAR | kVAR
9097 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPOVERSCHEDULE | Override schedule | String
9098 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPPERMSCHEDULE | Permission schedule | String
9099 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPPHASESENSED | Sensed phased for locally controlled capacitors (amps, Power Factor, Voltage, or VAR). | String
9100 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPPOSVALID | Position Validation | String
9101 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPREGBR | Regulation Branch ID | String
9102 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGBRDIR | For VAR, amp, or power factor locally controlled shunt impedances, the flow direction (enumeration). The field has the following values: Out of Device (value 1), Into Device (value 2). | String
9103 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGBREND | For VAR, amp, or power factor locally controlled shunt impedances, the end of the branch that is regulated (enumeration). The field has the following values: Primary side, Secondary side, and Tertiary Side (only if the branch is a Power transformer). | String
9104 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGBRID | ID of the regulation branch | String
9105 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGBRTYPE | Type of the regulation branch (e.g., line) | String
9106 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPREGNODE | Regulation node ID (for local voltage controlled capacitors). | String
9107 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPREGSCHEDULE | Regulation schedule (for clock controlled capacitors). | String
9108 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGTFNODE | A flag indicating that the shunt impedance regulation is enabled | Boolean
9109 | DNOM Component | Shunt Impedance | SHIMP |  | SHIMPREGTFNODENAME | Transformer ID with bushing | String
9110 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPREMOTE | The device's control mode (remote or local) | String
9111 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPREMOTELOCAL | Flag indicating if the shimp has both remote and local control capability. | Boolean
9112 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSCADACTRLAVAIL | Flag indicating if the capacitor is control available. | Boolean
9113 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSCADACTRLAVAILSTR | Text indicating if the capacitor is control available. | String
9114 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSCADASETONOFF | Value to enable/disable “Scada control” button on the device toolbar according to current status, also used for manual entry. | Boolean
9115 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSETONOFF | Value to enable/disable "toggle On/Off" button on the device toolbar according to current status. | String
9116 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSIZE | The capacitor nominal reactive power size (kVAR). | String
9117 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSTATUS | Bitmask for recording shunt impedance statuses | Integer
9118 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSTATUS2 | Bitmask for manual entries and other boolean parameters | Integer
9119 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPSTATUS3 | Bitmask for recording shunt impedance statuses BlockStateControls (flag indicating that state controls will be blocked) and DeviceDisabled (flag indicating that the device is disabled) in dynamics | Integer
9120 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPTIMEDELAY | Switching operation time delay for locally controlled capacitors. | Float
9121 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPVOLTREGTYPE | Voltage is measurements line to line or line to ground (true = line to line). | String
9122 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPVOVERHIGHLEVEL | Voltage Override High Limit | String
9123 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPVOVERLOWLEVEL | Voltage Override Low Limit | String
9124 | DNOM Component | Shunt Impedance | SHIMP | input | SHIMPVVCELIGIBLE | Flag indicating whether the device is eligible for LVM optimization | Boolean
9125 | DNOM Component | Shunt Impedance | SHIMP | input | STEPINIT | Current step (0 or 1 for a one step capacitor). | Integer
9126 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.ID | ID of the schedule | String |  |  |  | DNMOBJ
9127 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
9128 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
9129 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
9130 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
9131 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
9132 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
9133 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
9134 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
9135 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
9136 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
9137 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.YUNITONE | Y1 axis units | String |  |  |  | SCHED
9138 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
9139 | DNOM Component | Shunt Impedance | SHIMP | input | STEPINITA | Phase A initial step. | Integer
9140 | DNOM Component | Shunt Impedance | SHIMP | input | STEPINITB | Phase B initial step. | Integer
9141 | DNOM Component | Shunt Impedance | SHIMP | input | STEPINITC | Phase C initial step. | Integer
9142 | DNOM Component | Shunt Impedance | SHIMP | input | STEPSIZE | Step size for multi-step capacitors (kVAR). | Float
9143 | DNOM Component | Shunt Impedance | SHIMP | input | TIMESCHD | Pointer to the on/off schedule for clock controlled banks | String
9144 | DNOM Component | Shunt Impedance | SHIMP | input | TMDELAY | Controller time delay before switching operation (seconds) | Float
9145 | DNOM Component | Shunt Impedance | SHIMP | input | VARSUPPORT | Indicates if the capacitor is VAR support | Boolean
9146 | DNOM Component | Shunt Impedance | SHIMP | output | VOLTANDANGLEANA | Phase A voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
9147 | DNOM Component | Shunt Impedance | SHIMP | output | VOLTANDANGLEANB | Phase B voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
9148 | DNOM Component | Shunt Impedance | SHIMP | output | VOLTANDANGLEANC | Phase C voltage (magnitude on configurable voltage base and angle in degrees). | Float | DPF | Volt | Volt
9149 | DNOM Component | Shunt Impedance | SHIMP | input | VREGLINE | Voltage sensing for local voltage controlled shunt impedances (true = line-to-line, false = line-to-ground). | Boolean
9150 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9151 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.CELLSIZE | Cell size (kVAR) | Float |  |  |  | SHIMP
9152 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.CONSSWIT | Time interval between consecutive switching operations (hours) | Float |  |  |  | SHIMP
9153 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.CONTROL | Control capability | Integer |  |  |  | SHIMP
9154 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.CTRLOVERTYPE | Local Control override type (none, voltage, time or temperature) | Integer |  |  |  | SHIMP
9155 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9156 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9157 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9158 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
9159 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.HLEVOVER | High voltage override value (per unit volts) | Float |  |  |  | SHIMP
9160 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.HLLEVOVER | Flag indicating the local controller has an override such as voltage | Boolean |  |  |  | SHIMP
9161 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.HTLEVOVER | High time/temperature override value | Float |  |  |  | SHIMP
9162 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9163 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.LLEVOVER | Low voltage override value (per unit volts) | Float |  |  |  | SHIMP
9164 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.LOCLCTRL | Local controller type | Integer |  |  |  | SHIMP
9165 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.LTLEVOVER | Low time/temperature override value | Float |  |  |  | SHIMP
9166 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.MAXSWIT | Maximum number of daily switching operations | Integer |  |  |  | SHIMP
9167 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.NAME | Name of the object | String |  |  |  | DNMOBJ
9168 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9169 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9170 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9171 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.NUMSTEPS | The number of steps (1 for most capacitors) | Integer |  |  |  | SHIMP
9172 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.OFFLEVEL | Off level for locally controlled capacitors | Float |  |  |  | SHIMP
9173 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.ONLEVEL | On level for locally controlled capacitors | Float |  |  |  | SHIMP
9174 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.OPENFIX | Fixed capacitor initial status (true = open/off) | Boolean |  |  |  | SHIMP
9175 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PERMCTRLLEV1 | Permissive control level 1 | Float |  |  |  | SHIMP
9176 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PERMCTRLLEV2 | Permissive control level 1 | Float |  |  |  | SHIMP
9177 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PERMCTRLTYPE | Local control permissive type (none, time or temperature) | Integer |  |  |  | SHIMP
9178 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | SHIMP
9179 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PNOMA | Nominal phase A real power loss | Float |  |  |  | SHIMP
9180 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PNOMB | Nominal phase B real power loss | Float |  |  |  | SHIMP
9181 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.PNOMC | Nominal phase C real power loss | Float |  |  |  | SHIMP
9182 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.QNOMA | Nominal Phase A reactive power value | Float |  |  |  | SHIMP
9183 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.QNOMB | Nominal Phase B reactive power value | Float |  |  |  | SHIMP
9184 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.QNOMC | Nominal Phase C reactive power value | Float |  |  |  | SHIMP
9185 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.REGBRDIR | Branch flow direction for local regulation | Integer |  |  |  | SHIMP
9186 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.REGEND | Branch flow end for local regulation | Integer |  |  |  | SHIMP
9187 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.RGROUND | Grounding resistance (ohms) | Float |  |  |  | SHIMP
9188 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.SHIMPNOMVOLT | Nominal Voltage | Float |  |  |  | SHIMP
9189 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.SHIMPSTATUS | Bitmask for recording shunt impedance statuses | Integer |  |  |  | SHIMP
9190 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.STEPINIT | Current step (0 or 1 for a one step capacitor) | Integer |  |  |  | SHIMP
9191 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.STEPINITA | Phase A initial step | Integer |  |  |  | SHIMP
9192 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.STEPINITB | Phase B initial step | Integer |  |  |  | SHIMP
9193 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.STEPINITC | Phase C initial step | Integer |  |  |  | SHIMP
9194 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.STEPSIZE | Step size for multi-step capacitors (kVAR) | Float |  |  |  | SHIMP
9195 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.TMDELAY | Controller time delay before switching operation (seconds) | Float |  |  |  | SHIMP
9196 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.VREGLINE | Voltage sensing for local voltage controlled shunt impedances (true = line-to-line, false = line-to-ground) | Boolean |  |  |  | SHIMP
9197 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
9198 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP.XGROUND | Grounding reactance (ohms) | Float |  |  |  | SHIMP
9199 | DNOM Component | Shunt Impedance | SHIMP | input | WYE | Flag indicating that the shunt device is wye connected | Boolean |  |  |  | SHUNT
9200 | DNOM Component | Shunt Impedance | SHIMP | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
9201 | DNOM Component | Shunt Impedance | SHIMP | input | XGROUND | Grounding reactance (ohms). | Float
9202 | DNOM Component | Shunt Impedance | SHIMP | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
9203 | DNOM Component Placement | Shunt Impedance | SHIMP |  | MANUALEXCLUSIONFLAG | Flag indicating that the device is manually excluded for LVM | Boolean
9204 | DNOM Component Placement | Shunt Impedance Label Placement | SHLBPL | input | SHUNTIMP | Pointer to the associated shunt impedance (capacitor) | String
9205 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9206 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.CELLSIZE | Cell size (kVAR) | Float |  |  |  | SHIMP
9207 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.CONSSWIT | Time interval between consecutive switching operations (hours) | Float |  |  |  | SHIMP
9208 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.CONTROL | Control capability | Integer |  |  |  | SHIMP
9209 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.CTRLOVERTYPE | Local Control override type (none, voltage, time or temperature) | Integer |  |  |  | SHIMP
9210 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9211 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9212 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9213 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
9214 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.HLEVOVER | High voltage override value (per unit volts) | Float |  |  |  | SHIMP
9215 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.HLLEVOVER | Flag indicating the local controller has an override such as voltage | Boolean |  |  |  | SHIMP
9216 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.HTLEVOVER | High time/temperature override value | Float |  |  |  | SHIMP
9217 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9218 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.LLEVOVER | Low voltage override value (per unit volts) | Float |  |  |  | SHIMP
9219 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.LOCLCTRL | Local controller type | Integer |  |  |  | SHIMP
9220 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.LTLEVOVER | Low time/temperature override value | Float |  |  |  | SHIMP
9221 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.MAXSWIT | Maximum number of daily switching operations | Integer |  |  |  | SHIMP
9222 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.NAME | Name of the object | String |  |  |  | DNMOBJ
9223 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9224 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9225 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9226 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.NUMSTEPS | The number of steps (1 for most capacitors) | Integer |  |  |  | SHIMP
9227 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.OFFLEVEL | Off level for locally controlled capacitors | Float |  |  |  | SHIMP
9228 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.ONLEVEL | On level for locally controlled capacitors | Float |  |  |  | SHIMP
9229 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.OPENFIX | Fixed capacitor initial status (true = open/off) | Boolean |  |  |  | SHIMP
9230 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PERMCTRLLEV1 | Permissive control level 1 | Float |  |  |  | SHIMP
9231 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PERMCTRLLEV2 | Permissive control level 1 | Float |  |  |  | SHIMP
9232 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PERMCTRLTYPE | Local control permissive type (none, time or temperature) | Integer |  |  |  | SHIMP
9233 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | SHIMP
9234 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PNOMA | Nominal phase A real power loss | Float |  |  |  | SHIMP
9235 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PNOMB | Nominal phase B real power loss | Float |  |  |  | SHIMP
9236 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.PNOMC | Nominal phase C real power loss | Float |  |  |  | SHIMP
9237 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.QNOMA | Nominal Phase A reactive power value | Float |  |  |  | SHIMP
9238 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.QNOMB | Nominal Phase B reactive power value | Float |  |  |  | SHIMP
9239 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.QNOMC | Nominal Phase C reactive power value | Float |  |  |  | SHIMP
9240 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.REGBRDIR | Branch flow direction for local regulation | Integer |  |  |  | SHIMP
9241 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.REGEND | Branch flow end for local regulation | Integer |  |  |  | SHIMP
9242 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.RGROUND | Grounding resistance (ohms) | Float |  |  |  | SHIMP
9243 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.SHIMPNOMVOLT | Nominal Voltage | Float |  |  |  | SHIMP
9244 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.SHIMPSTATUS | Bitmask for recording shunt impedance statuses | Integer |  |  |  | SHIMP
9245 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.STEPINIT | Current step (0 or 1 for a one step capacitor) | Integer |  |  |  | SHIMP
9246 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.STEPINITA | Phase A initial step | Integer |  |  |  | SHIMP
9247 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.STEPINITB | Phase B initial step | Integer |  |  |  | SHIMP
9248 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.STEPINITC | Phase C initial step | Integer |  |  |  | SHIMP
9249 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.STEPSIZE | Step size for multi-step capacitors (kVAR) | Float |  |  |  | SHIMP
9250 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.TMDELAY | Controller time delay before switching operation (seconds) | Float |  |  |  | SHIMP
9251 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.VREGLINE | Voltage sensing for local voltage controlled shunt impedances (true = line-to-line, false = line-to-ground) | Boolean |  |  |  | SHIMP
9252 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
9253 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK.XGROUND | Grounding reactance (ohms) | Float |  |  |  | SHIMP
9254 | DNOM Component | Shunt Impedance Bank | SHPBK | input | ID | Object unique ID | String |  |  |  | DNMOBJ
9255 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.ID | ID of the schedule | String |  |  |  | DNMOBJ
9256 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
9257 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
9258 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
9259 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
9260 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
9261 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
9262 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
9263 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
9264 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
9265 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
9266 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.YUNITONE | Y1 axis units | String |  |  |  | SCHED
9267 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
9268 | DNOM Component | Shunt Impedance Bank | SHPBK | input | NAME | Object name | String |  |  |  | DNMOBJ
9269 | DNOM Component | Shunt Impedance Bank | SHPBK |  | NUMSHIMP | The number of shunt objects contained in the bank | Integer
9270 | DNOM Component | Shunt Impedance Bank | SHPBK |  | OFSEQBK | Dynamic array of shunt impedance pointers off sequence | Integer
9271 | DNOM Component | Shunt Impedance Bank | SHPBK |  | ONSEQBK | Dynamic array of shunt impedance pointers on sequence | Integer
9272 | DNOM Component | Shunt Impedance Bank | SHPBK | input | SHTIMPBK | Dynamic array of shunt impedance pointers | String
9273 | DNOM Component | Shunt Impedance Bank | SHPBK |  | SHTIMPSWT | Pointer to the associated switch | String
9274 | Global Object | Shunt Impedance Model | SHPMOD | input | ALDARRAY | Associated typical load shapes. | String
9275 | Global Object | Shunt Impedance Model | SHPMOD |  | CLOSESW | Limit on switching electrically close capacitors (ohms separation). | Float
9276 | Global Object | Shunt Impedance Model | SHPMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
9277 | Global Object | Shunt Impedance Model | SHPMOD |  | INDPHOPS | Flag indicaitng that multi-phase device has independent phase operation (true - phases operate independently) | Boolean
9278 | Global Object | Shunt Impedance Model | SHPMOD |  | LIMNAME | An array of limit names | String
9279 | Global Object | Shunt Impedance Model | SHPMOD |  | LIMUNIT | Limit unit enumeration (1- Amp, 2 - KVA, 3 - MVA) | Enumeration
9280 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
9281 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
9282 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
9283 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
9284 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
9285 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
9286 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
9287 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
9288 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
9289 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
9290 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
9291 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
9292 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
9293 | Global Object | Shunt Impedance Model | SHPMOD |  | LIMVALUE | An array of limit values | Integer
9294 | Global Object | Shunt Impedance Model | SHPMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
9295 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9296 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.CELLSIZE | Cell size (kVAR) | Float |  |  |  | SHIMP
9297 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.CONSSWIT | Time interval between consecutive switching operations (hours) | Float |  |  |  | SHIMP
9298 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.CONTROL | Control capability | Integer |  |  |  | SHIMP
9299 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.CTRLOVERTYPE | Local Control override type (none, voltage, time or temperature) | Integer |  |  |  | SHIMP
9300 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9301 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9302 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9303 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
9304 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.HLEVOVER | High voltage override value (per unit volts) | Float |  |  |  | SHIMP
9305 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.HLLEVOVER | Flag indicating the local controller has an override such as voltage | Boolean |  |  |  | SHIMP
9306 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.HTLEVOVER | High time/temperature override value | Float |  |  |  | SHIMP
9307 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9308 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.LLEVOVER | Low voltage override value (per unit volts) | Float |  |  |  | SHIMP
9309 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.LOCLCTRL | Local controller type | Integer |  |  |  | SHIMP
9310 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.LTLEVOVER | Low time/temperature override value | Float |  |  |  | SHIMP
9311 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.MAXSWIT | Maximum number of daily switching operations | Integer |  |  |  | SHIMP
9312 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.NAME | Name of the object | String |  |  |  | DNMOBJ
9313 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9314 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9315 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9316 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.NUMSTEPS | The number of steps (1 for most capacitors) | Integer |  |  |  | SHIMP
9317 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.OFFLEVEL | Off level for locally controlled capacitors | Float |  |  |  | SHIMP
9318 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.ONLEVEL | On level for locally controlled capacitors | Float |  |  |  | SHIMP
9319 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.OPENFIX | Fixed capacitor initial status (true = open/off) | Boolean |  |  |  | SHIMP
9320 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PERMCTRLLEV1 | Permissive control level 1 | Float |  |  |  | SHIMP
9321 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PERMCTRLLEV2 | Permissive control level 1 | Float |  |  |  | SHIMP
9322 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PERMCTRLTYPE | Local control permissive type (none, time or temperature) | Integer |  |  |  | SHIMP
9323 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | SHIMP
9324 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PNOMA | Nominal phase A real power loss | Float |  |  |  | SHIMP
9325 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PNOMB | Nominal phase B real power loss | Float |  |  |  | SHIMP
9326 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.PNOMC | Nominal phase C real power loss | Float |  |  |  | SHIMP
9327 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.QNOMA | Nominal Phase A reactive power value | Float |  |  |  | SHIMP
9328 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.QNOMB | Nominal Phase B reactive power value | Float |  |  |  | SHIMP
9329 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.QNOMC | Nominal Phase C reactive power value | Float |  |  |  | SHIMP
9330 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.REGBRDIR | Branch flow direction for local regulation | Integer |  |  |  | SHIMP
9331 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.REGEND | Branch flow end for local regulation | Integer |  |  |  | SHIMP
9332 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.RGROUND | Grounding resistance (ohms) | Float |  |  |  | SHIMP
9333 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.SHIMPNOMVOLT | Nominal Voltage | Float |  |  |  | SHIMP
9334 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.SHIMPSTATUS | Bitmask for recording shunt impedance statuses | Integer |  |  |  | SHIMP
9335 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.STEPINIT | Current step (0 or 1 for a one step capacitor) | Integer |  |  |  | SHIMP
9336 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.STEPINITA | Phase A initial step | Integer |  |  |  | SHIMP
9337 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.STEPINITB | Phase B initial step | Integer |  |  |  | SHIMP
9338 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.STEPINITC | Phase C initial step | Integer |  |  |  | SHIMP
9339 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.STEPSIZE | Step size for multi-step capacitors (kVAR) | Float |  |  |  | SHIMP
9340 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.TMDELAY | Controller time delay before switching operation (seconds) | Float |  |  |  | SHIMP
9341 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.VREGLINE | Voltage sensing for local voltage controlled shunt impedances (true = line-to-line, false = line-to-ground) | Boolean |  |  |  | SHIMP
9342 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
9343 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP.XGROUND | Grounding reactance (ohms) | Float |  |  |  | SHIMP
9344 | Global Object | Shunt Impedance Model | SHPMOD |  | NUMLIMIT | The number of operation limits. | Integer
9345 | DNOM Group Object | Shunt | SHUNT | input | TERM. | Enumeration of shunt device terminal | Enumeration
9346 | DNOM Group Object | Shunt | SHUNT | input | TERM.NODE | Shunt device terminal node | Enumeration
9347 | Global Object | Shunt Impedance Model | SHPMOD |  | NUMOPSCH | Number of operation schedules | Integer
9348 | Global Object | Shunt Impedance Model | SHPMOD |  | PLOSS | Real power loss | Integer
9349 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9350 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9351 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9352 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.ID | ID of the object | String |  |  |  | DNMOBJ
9353 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.NAME | Object name | String |  |  |  | DNMOBJ
9354 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.PHASING | Sensor phases | String |  |  |  | SENSOR
9355 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION.SENSORTYPE | Sensor type | Enumeration |  |  |  | SENSOR
9356 | Global Object | Shunt Impedance Model | SHPMOD | input | SWCSTSCH | Pointer to the cost biasing schedule | String
9357 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9358 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9359 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9360 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.ID | ID of the object | String |  |  |  | DNMOBJ
9361 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.NAME | Object name | String |  |  |  | DNMOBJ
9362 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.PHASING | Sensor phases | String |  |  |  | SENSOR
9363 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION.SENSORTYPE | Sensor type | Enumeration |  |  |  | SENSOR
9364 | DNOM Component | Splice Box | SPLBOX | input | ADDRESS.NOAPPSTR | Address of splice box. | String
9365 | Global Object | Shunt Impedance Model | SHPMOD |  | SWITCOST | Default cost of performing a switching operation ($/operation). | Float
9366 | DNOM Component Placement | Shunt Impedance Placement | SHPPLE | input | SHUNTIMP | Pointer to the associated shunt impedance (capacitor) | String
9367 | DNOM Group Object | Shunt | SHUNT | input | GROUNDED | Flag indicating that the shunt device is grounded | Boolean
9368 | DNOM Group Object | Shunt | SHUNT | input | WYE | Flag indicating that the shunt device is wye connected | Boolean
9369 | DNOM Component Placement | Sensor Label Placement | SLLBPL | input | SENSORLOCATION | Pointer to the associated sensor | String
9370 | DNOM Component Placement | Sensor Placement | SLPLE | input | SENSORLOCATION | Pointer to the associated sensor | String
9371 | DNOM Component | Splice Box | SPLBOX | input | ALTERNATENAME | Alternate Name. | String
9372 | DNOM Component | Splice Box | SPLBOX | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
9373 | DNOM Component | Splice Box | SPLBOX | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9374 | DNOM Component | Splice Box | SPLBOX | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
9375 | DNOM Component | Splice Box | SPLBOX | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
9376 | DNOM Component | Splice Box | SPLBOX | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9377 | DNOM Component | Splice Box | SPLBOX | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9378 | DNOM Component | Splice Box | SPLBOX | input | ENUMTYPE | Splice box type. 1= standard, 2 = others. | Integer
9379 | DNOM Component | Splice Box | SPLBOX | input | ID | Object unique ID | String |  |  |  | DNMOBJ
9380 | DNOM Component | Splice Box | SPLBOX | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
9381 | DNOM Component | Splice Box | SPLBOX | input | NAME | Object name | String |  |  |  | DNMOBJ
9382 | DNOM Component | Splice Box | SPLBOX | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
9383 | DNOM Component | Splice Box | SPLBOX | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
9384 | DNOM Component | Splice Box | SPLBOX | input | NUMOBJ | The number of objects in the splice box. | Integer
9385 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
9386 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
9387 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
9388 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
9389 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.ID | ID of the node | String |  |  |  | DNMOBJ
9390 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9391 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9392 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9393 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
9394 | DNOM Component | Splice Box | SPLBOX |  | OBJINDEX | - | -
9395 | DNOM Component | Splice Box | SPLBOX |  | OBJTYPE | - | -
9396 | DNOM Component | Splice Box | SPLBOX | input | REFDRAW | Reference Drawing. | String
9397 | DNOM Component | Splice Box | SPLBOX | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
9398 | DNOM Component | Splice Box | SPLBOX | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
9399 | DNOM Component | Service Point | SRVCPT | input | CNCTNODE | Pointer to the associated connection node | String
9400 | DNOM Component | Service Point | SRVCPT | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9401 | DNOM Component | Service Point | SRVCPT | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9402 | DNOM Component | Service Point | SRVCPT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
9403 | DNOM Component | Service Point | SRVCPT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
9404 | DNOM Component | Service Point | SRVCPT | input | NAME | Object name | String |  |  |  | DNMOBJ
9405 | DNOM Component | Service Point | SRVCPT |  | SPNUMCST | Customer count | Integer
9406 | DNOM Component | Service Point | SRVCPT |  | SPPRIM | Flag indicating the service point represents a primary meter customer (true = primary, false = secondary) | Boolean
9407 | DNOM Component | Service Point | SRVCPT | input | SRVPTAMICALLS | AMI signal count on the service point (on OMS server only) | String
9408 | DNOM Component | Service Point | SRVCPT | input | SRVPTCUSTCALLS | Call count on the service point (on OMS server only) | String
9409 | DNOM Component | Service Point | SRVCPT | input | SRVPTTF | ID of the transformer that the service point is associated with | String
9410 | DNOM Component | Service Point | SRVCPT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
9411 | DNOM Component | Service Point | SRVCPT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
9412 | DNOM Component | Switchable Section Output | SSTOUT |  | IAPERCNT | Phase A current loading percentage. Calculated by dividing the phase A net injection Amps by the the lowest ampacity limit of backbone devices. | Float
9413 | DNOM Component | Switchable Section Output | SSTOUT |  | IAPKPERC | Phase A peak current loading in percentage | Integer
9414 | DNOM Component | Switchable Section Output | SSTOUT |  | IBPERCNT | Phase B current loading percentage. Calculated by dividing the phase B net injection Amps by the the lowest ampacity limit of backbone devices. | Float
9415 | DNOM Component | Switchable Section Output | SSTOUT |  | IBPKPERC | Phase B peak current loading in percentage | Integer
9416 | DNOM Component | Switchable Section Output | SSTOUT |  | ICPERCNT | Phase C current loading percentage. Calculated by dividing the phase C net injection Amps by the the lowest ampacity limit of backbone devices. | Float
9417 | DNOM Component | Switchable Section Output | SSTOUT |  | ICPKPERC | Phase C peak current loading in percentage | Integer
9418 | DNOM Component | Switchable Section Output | SSTOUT |  | INETA | Phase A section net injection | Float |  | Amps | Amps
9419 | DNOM Component | Switchable Section Output | SSTOUT |  | INETAPK | Phase A peak section net injection (calculated from the TC function) | Float |  | Amps | Amps
9420 | DNOM Component | Switchable Section Output | SSTOUT |  | INETB | Phase B section net injection | Float |  | Amps | Amps
9421 | DNOM Component | Switchable Section Output | SSTOUT |  | INETBPK | Phase B peak section net injection (calculated from the TC function) | Float |  | Amps | Amps
9422 | DNOM Component | Switchable Section Output | SSTOUT |  | INETC | Phase C section net injection | Float |  | Amps | Amps
9423 | DNOM Component | Switchable Section Output | SSTOUT |  | INETCPK | Phase C peak section net injection (calculated from the TC function) | Float |  | Amps | Amps
9424 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETA | Phase A section net load | Float |  | kVA | kVA
9425 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETAPK | Phase A peak section net load (calculated from the TC function) | Float |  | kVA | kVA
9426 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETB | Phase B section net load | Float |  | kVA | kVA
9427 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETBPK | Phase B peak section net load (calculated from the TC function) | Float |  | kVA | kVA
9428 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETC | Phase C section net load | Float |  | kVA | kVA
9429 | DNOM Component | Switchable Section Output | SSTOUT |  | SNETCPK | Phase C peak section net load (calculated from the TC function) | Float |  | kVA | kVA
9430 | DNOM Component | Station Internal Input Component | STATINPUTINT | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
9431 | DNOM Component | Station Internal Input Component | STATINPUTINT | input | STNINPUTID | Station internal input component ID. | String
9432 | DNOM Component | Station Internal Input Component | STATINPUTINT | input | STNINPUTNAME | Station internal input component type name. Return “SWITCH” for a switch, “TAPCHR” for a transformer, CAPACITOR for a capacitor. | String
9433 | DNOM Component | Station Internal Component | STATINT | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
9434 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | DATECREATED | The created datetime of the station pedigree file . | String |  | #N/A | #N/A
9435 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | DATEMODIFIED | The modified datetime of the station pedigree file . | String |  | #N/A | #N/A
9436 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | ERRORCNT | Total number of errors during the model file’s conversion | Integer
9437 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | FATALERRCNT | Total number of fatal errors during the model file’s conversion | Integer
9438 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | NAME | The name of the station pedigree file . | String |  | #N/A | #N/A | DNMOBJ
9439 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | OWNER | The owner of the station pedigree file . | String |  | #N/A | #N/A
9440 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | PATH | The path of the station pedigree file . | String |  | #N/A | #N/A
9441 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | SIZE | File size in kB | String |  | kB | kB
9442 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | STATIONPEDIGREEERRINFO | Conversion history information | String
9443 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | STATIONPEDIGREEERRORS | Total number of errors during the model file’s conversion | String
9444 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | STATIONPEDIGREEFATALS | Total number of fatal errors during the model file’s conversion | String
9445 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | STATIONPEDIGREEFILESIZE | The size of the station pedigree file . | String |  | #N/A | Bytes
9446 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | STATIONPEDIGREEWARNINGS | Total number of warnings during the model file’s conversion | String
9447 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE | output | VERSION | The version of the station pedigree file . | String |  | #N/A | #N/A
9448 | DNOM Component | Station Pedigree File Info | STATIONPEDIGREEFILE |  | WARNINGCNT | Total number of warnings during the model file’s conversion | Integer
9449 | DNAF Object | Substation | SUB |  | LVMSOLUTIONMIXED | Specifies whether the LVM solution includes plans for mixed problem formulations | Boolean
9450 | DNOM Component | Substation | SUB | input | _KEY | The record key for manual entry. | String
9451 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMDESC | The AFR problem formulation description. | String | AFR | #N/A | #N/A
9452 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMFLIMLEVEL | The AFR flow violation limits level. | String | AFR | #N/A | #N/A
9453 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMNAME | The AFR problem formulation name. | String | AFR | #N/A | #N/A
9454 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMRESPDIST | Whether use dist limits for AFR | String | AFR | #N/A | #N/A
9455 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMRESPTRANS | Whether use trans limits for AFR | String | AFR | #N/A | #N/A
9456 | DNOM Component | Substation | SUB | output | ACTIVEAFRPROBFORMVLIMLEVEL | The AFR voltage violation limits level. | String | AFR | #N/A | #N/A
9457 | DNOM Component | Substation | SUB | output | ACTIVEDEMANDDIFF | Total real power demand difference between calculated and measured values | String |  | MW | MW
9458 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMDESC | The FISR problem formulation description. | String | FISR | #N/A | #N/A
9459 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMFLIMLEVEL | The FISR flow violation limits level. | String | FISR | #N/A | #N/A
9460 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMNAME | The FISR problem formulation name. | String | FISR | #N/A | #N/A
9461 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMRESPDIST | Whether use dist limits for FISR | String | FISR | #N/A | #N/A
9462 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMRESPTRANS | Whether use trans limits for FISR | String | FISR | #N/A | #N/A
9463 | DNOM Component | Substation | SUB | output | ACTIVEFISRPROBFORMVLIMLEVEL | The FISR voltage violation limits level. | String | FISR | #N/A | #N/A
9464 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORDESC | The POS problem formulation description. | String | PLOS | #N/A | #N/A
9465 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORMFLIMLEVEL | The POS flow violation limits level. | String | PLOS | #N/A | #N/A
9466 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORMNAME | The POS problem formulation name. | String | PLOS | #N/A | #N/A
9467 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORMRESPDIST | Whether use dist limits for POS | String | PLOS | #N/A | #N/A
9468 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORMRESPTRANS | Whether use trans limits for POS | String | PLOS | #N/A | #N/A
9469 | DNOM Component | Substation | SUB | output | ACTIVEPLORSPROBFORMVLIMLEVEL | The POS voltage violation limits level. | String | PLOS | #N/A | #N/A
9470 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMDESC | The LVM problem formulation description. | String | LVM | #N/A | #N/A
9471 | DNOM Component | Substation | SUB | input | ADDRESS.NOAPPSTR | Address. | String
9472 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMFLIMLEVEL | The LVM flow violation limits level. | String | LVM | #N/A | #N/A
9473 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMNAME | The LVM problem formulation name. | String | LVM | #N/A | #N/A
9474 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMRESPDIST | Whether use dist limits for VCC. | String | LVM | #N/A | #N/A
9475 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMRESPTRANS | Whether use trans limits for LVM. | String | LVM | #N/A | #N/A
9476 | DNOM Component | Substation | SUB | output | ACTIVEVVCPROBFORMVLIMLEVEL | The LVMvoltage violation limits level. | String | LVM | #N/A | #N/A
9477 | DNOM Component | Substation | SUB | input | ACTLSCALERUSED | Load scaling factor | Float
9478 | DNOM Component | Substation | SUB | input | ADDRESS | Address | String
9479 | DNOM Component | Substation | SUB |  | AFRAUTOENABLEDTEXT | LVM auto enabled text | String
9480 | DNOM Component | Substation | SUB | input | AFRCLOSEDLOOP | Flag indicating if the station is running AFR in closed loop mode | Boolean
9481 | DNOM Component | Substation | SUB | input | AFROVERLOADPLANEXEC | Overload Plan Execution Mode for AFR | Integer
9482 | DNOM Component | Substation | SUB | output | AFRPEAKTIME | Latest AFR peak evaluation time. | String | AFR | #N/A | #N/A
9483 | DNOM Component | Substation | SUB | output | AFRPEAKTIME_TICKS | Peak AFR evaluatiion time (over the look ahead window). | Struct TM
9484 | DNOM Component | Substation | SUB | input | AFRPROFORMINDEX | The AFR problem formulation index | Integer
9485 | DNOM Component | Substation | SUB | input | AFRPROFORMNAME | The AFR problem formulation name | Integer
9486 | DNOM Component | Substation | SUB | output | AFRSTATIONEXETIME | Latest AFR execution time. | String | AFR | #N/A | #N/A
9487 | DNOM Component | Substation | SUB | output | AFRSTATIONEXETIME_TICKS | Latest AFR excution time | Struct TM
9488 | DNOM Component | Substation | SUB | output | AFRSTATIONLASTSOLUTIONID | The last solution id for AFR. | String | AFR | #N/A | #N/A
9489 | DNOM Component | Substation | SUB | output | AFRSTATIONTIME | Latest AFR solution time. | String | AFR | #N/A | #N/A
9490 | DNOM Component | Substation | SUB | output | AFRSTATIONTIME_TICKS | Latest AFR solved time. | Struct TM
9491 | DNOM Component | Substation | SUB | output | AFRSTATUS | Latest AFR solution status. | String | AFR | #N/A | #N/A
9492 | DNOM Component | Substation | SUB |  | AFRSTATUSCODE | AFR status code | String
9493 | DNOM Component | Substation | SUB | output | AGGREGATIONACTIVEDEMAND | Total DPF calculated real power demand at the load side (secondary) | String | DPF | MW | MW
9494 | DNOM Component | Substation | SUB | output | AGGREGATIONACTIVEDEMANDHIGHLOW | Total DPF calculated real power demand at the source side (primary) and at the load side (secondary) | String | DPF | MW | MW
9495 | DNOM Component | Substation | SUB | output | AGGREGATIONACTIVELOSS | Total DPF calculated real power loss | String | DPF | MVAR | MVAR
9496 | DNOM Component | Substation | SUB | output | AGGREGATIONCAPACITORMVAROFFLINE | The calculated offline capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. As opposed to the calculation for online capacitor reactive power, the offline calculation only includes disconnected remote capacitors. | String | MVAR | MVAR | MVAR
9497 | DNOM Component | Substation | SUB | output | AGGREGATIONCAPACITORMVARONLINE | The calculated online capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. This includes connected fixed and remote capacitors as well as all local capacitors. | String | MVAR | MVAR | MVAR
9498 | DNOM Component | Substation | SUB | output | AGGREGATIONCAPACITORMVARTOTAL | The total capacitor reactive power, which is the sum of the online and offline capacitor reactive power for each aggregation object. | String | MVAR | MVAR | MVAR
9499 | DNOM Component | Substation | SUB | output | AGGREGATIONDERACTIVEDEMAND | Calculated DER/DG real power injection in MW | Float | DPF | MW | MW
9500 | DNOM Component | Substation | SUB | output | AGGREGATIONDERREACTIVEDEMAND | Calculated DER/DG reactive power injection in MVAR | Float | DPF | MVAR | MVAR
9501 | DNOM Component | Substation | SUB | output | AGGREGATIONNATIVEACTIVEDEMAND | Calculated native real power demand in MW | Float | DPF | MW | MW
9502 | DNOM Component | Substation | SUB | output | AGGREGATIONNATIVEREACTIVEDEMAND | Calculated native reactive power demand in MVAR | Float | DPF | MVAR | MVAR
9503 | DNOM Component | Substation | SUB | output | AGGREGATIONPOWERFACTOR | Calculated power factor at the load side | String | DPF
9504 | DNOM Component | Substation | SUB | output | AGGREGATIONPOWERFACTORHIGHLOW | Calculated power factor at the source side (primary) and at the load side (secondary) | String | DPF
9505 | DNOM Component | Substation | SUB | output | AGGREGATIONREACTIVEDEMAND | Total DPF calculated reactive power demand at the load side (secondary) | String | DPF | MVAR | MVAR
9506 | DNOM Component | Substation | SUB | output | AGGREGATIONREACTIVEDEMANDHIGHLOW | Total DPF calculated reactive power demand at the source side (primary) and at the load side (secondary) | String | DPF | MVAR | MVAR
9507 | DNOM Component | Substation | SUB | output | AGGREGATIONREACTIVELOSS | Total DPF calculated reactive power loss | String | DPF | MVAR | MVAR
9508 | DNOM Component | Substation | SUB | output | ALLSUBTFENGZ | Substation power transformer energization status | String | DPF | #N/A | #N/A
9509 | DNOM Component | Substation | SUB | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
9510 | DNOM Component | Substation | SUB | input | ALTNAME | Alternate name | String
9511 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGECALCAMPWEIGHTALLBUS | Weighted calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9512 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGECALCAMPWEIGHTMVBUS | Weighted calculated average voltage in per unit. Only station MV buses are accounted. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9513 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGECALCNOWEIGHTALLBUS | Calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. | Float | DPF | p.u. | p.u.
9514 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGECALCNOWEIGHTMVBUS | Calculated average voltage in per unit. Only station MV buses are accounted. | Float | DPF | p.u. | p.u.
9515 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9516 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGEMEASAMPWEIGHTMVBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9517 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGEMEASNOWEIGHTALLBUS | Weighted measured average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9518 | DNOM Component | Substation | SUB | output | AREAAVRAGEVOLTAGEMEASNOWEIGHTMVBUS | Measured average voltage, station bus only, in per unit | Float | DPF | p.u. | p.u.
9519 | DNOM Component | Substation | SUB | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9520 | DNOM Component | Substation | SUB | input | AREANAME | Associated operational area/division. | String
9521 | DNOM Component | Substation | SUB | output | AUTOTFVOLTDROPCOUNT | The amount of the auto transformer which voltage drop exceeded limit | Integer
9522 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGECALCAMPWEIGHTALLBUS | Weighted calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9523 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGECALCAMPWEIGHTMVBUS | Weighted calculated average voltage in per unit. Only station MV buses are accounted. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9524 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGECALCNOWEIGHTALLBUS | Calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. | Float | DPF | p.u. | p.u.
9525 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGECALCNOWEIGHTMVBUS | Calculated average voltage in per unit. Only station MV buses are accounted. | Float | DPF | p.u. | p.u.
9526 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9527 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGEMEASAMPWEIGHTMVBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9528 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGEMEASNOWEIGHTALLBUS | Weighted measured average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9529 | DNOM Component | Substation | SUB | output | AVRAGEVOLTAGEMEASNOWEIGHTMVBUS | Measured average voltage, station bus only, in per unit | Float | DPF | p.u. | p.u.
9530 | DNOM Component | Substation | SUB |  | BLAABSOLUTECONVP | Absolute flow convergence (real power) | Float
9531 | DNOM Component | Substation | SUB |  | BLAABSOLUTECONVQ | Absolute flow convergence (reactive power) | Float
9532 | DNOM Component | Substation | SUB | output | BLAMAXFEEDERMISMATCH | The biggest current mismatch at feeder heads. | Float | DPF | amps | amps
9533 | DNOM Component | Substation | SUB | input | BLAMAXITER | The maximum number of power flow iterations. | Integer
9534 | DNOM Component | Substation | SUB | output | BLANUMOFMEASIL | Number of measurement islands | Integer | DPF | #N/A | #N/A
9535 | DNOM Component | Substation | SUB |  | BLAPERCENTCONVP | Percent flow convergence (real power) | Float
9536 | DNOM Component | Substation | SUB |  | BLAPERCENTCONVQ | Percent flow convergence (reactive power) | Float
9537 | DNOM Component | Substation | SUB | output | BLASTATIONERRORCOUNT | The number of measurement island error. | Integer | DPF | count | count
9538 | DNOM Component | Substation | SUB |  | BLASTATUSFROMMEASILP | Last DPF/BLA solution status from the measurement island for balancing real power | String
9539 | DNOM Component | Substation | SUB |  | BLASTATUSFROMMEASILQ | Last DPF/BLA solution status from the measurement island for balancing reactive power | String
9540 | DNOM Component | Substation | SUB |  | BLASTATUSFROMMEASILS | Last DPF/BLA solution status from the measurement island for balancing apparent power | String
9541 | DNOM Component | Substation | SUB | output | BLASTATUSISLDOWNCHK | The status of the less accurate downstream island. | Boolean | DPF | #N/A | #N/A
9542 | DNOM Component | Substation | SUB | output | BLASTATUSP | Last DPF/BLA solution status for balancing real power. | Boolean | DPF | #N/A | #N/A
9543 | DNOM Component | Substation | SUB | output | BLASTATUSQ | Last DPF/BLA solution status for balancing reactive power. | Boolean | DPF | #N/A | #N/A
9544 | DNOM Component | Substation | SUB | output | BLAWORSTFEEDERNAME | The name of feeder which has the biggest current mismatch at feeder head. | String | DPF | #N/A | #N/A
9545 | DNOM Component | Substation | SUB |  | BLAWORSTISLANDIDX | Measurement Island with worst mismatch index | String
9546 | DNOM Component | Substation | SUB | output | BLAWORSTISLANDNAME | Measurement Island with Highest Flow Mismatch | String | DPF | #N/A | #N/A
9547 | DNOM Component | Substation | SUB |  | BLAWORSTISLANDVAL | Measurement Island with worst mismatch value | String
9548 | DNOM Component | Substation | SUB | input | BLKREG | Block regulators flag | Boolean
9549 | DNOM Component | Substation | SUB | input | BLOCKREG | Block regulators flag. | Boolean
9550 | DNOM Component | Substation | SUB |  | BUSMANCOUNT | Number of bus manual inputs | Integer
9551 | DNOM Component | Substation | SUB | input | BUSVOLTLIMITS | The count of enabled manual override for voltage limit | Integer
9552 | DNOM Component | Substation | SUB | output | BUSVOLTMISMATCH | Specifies whether bus voltage mismatch exists | Boolean
9553 | DNOM Component | Substation | SUB |  | CAPMANCOUNT | Number of capacitor manual inputs | Integer
9554 | DNOM Component | Substation | SUB | input | CAPMANUALINPUT | Capacitor Manual inputed paramters count | Integer
9555 | DNOM Component | Substation | SUB | input | CRC | CRC | Integer
9556 | DNOM Component | Substation | SUB | output | CURRENTLVMTHROTTLINGDELAY | Current LVM throttling delay in seconds | String
9557 | DNOM Component | Substation | SUB |  | DASTATUSMEAS | DA status measurement Id | String
9558 | DNOM Component | Substation | SUB | input | DERKVAR3PHASE | Reactive power output by the DERs | String |  | kVAR | kVAR
9559 | DNOM Component | Substation | SUB | input | DERKW3PHASE | Real power output by the DERs | String |  | kW | kW
9560 | DNOM Component | Substation | SUB | input | DERPF | DER power factor | String
9561 | DNOM Component | Substation | SUB | input | DERPGENMAX | Maximum real power generation by the DERs | String |  | kW | kW
9562 | DNOM Component | Substation | SUB | input | DERQGENMAX | Maximum reactive power generation by DERs | String |  | KVAR | KVAR
9563 | DNOM Component | Substation | SUB | input | DERQGENMIN | Minimum reactive power generation by DERs | String |  | KVAR | KVAR
9564 | DNOM Component | Substation | SUB | input | DESCRIPT | Station description | String
9565 | DNOM Component | Substation | SUB | input | DISABLEDNAF | Whether the DNAF application is disabled in the substation. | Boolean
9566 | DNOM Component | Substation | SUB | input | DISCONNECTEDDISTTF | Disconnected distribution transformer count | Integer
9567 | DNOM Component | Substation | SUB |  | DISTTFMANCOUNT | Number of distribution transformer manual inputs | Integer
9568 | DNOM Component | Substation | SUB | output | DISTTFVOLTDROPCOUNT | The amount of the distribution transformer which voltage drop exceeded limit | Integer
9569 | DNOM Component | Substation | SUB | input | DNAFALRMAMIMISMTACHENABLED | Indicate if the AMI (load point) voltage mismatch alarm is enabled | Boolean
9570 | DNOM Component | Substation | SUB | input | DNAFALRMCAPPOSENABLED | Indicate if the capacitor position alarm is enabled | Boolean
9571 | DNOM Component | Substation | SUB | input | DNAFALRMFLOWVIOENABLED | Indicate if the power flow violation alarm is enabled | Boolean
9572 | DNOM Component | Substation | SUB | input | DNAFALRMHIGHVOLTENABLED | Indicate if the high voltage alarm is enabled | Boolean
9573 | DNOM Component | Substation | SUB | input | DNAFALRMIMBFLOWENABLED | Indicate if the power flow imbalance alarm is enabled | Boolean
9574 | DNOM Component | Substation | SUB | input | DNAFALRMIMBVOLTENABLED | Indicate if the voltage imbalance alarm is enabled | Boolean
9575 | DNOM Component | Substation | SUB | input | DNAFALRMLOWVOLTENABLED | Indicate if the low voltage alarm is enabled | Boolean
9576 | DNOM Component | Substation | SUB |  | DNAFAUTOENABLEDAPPS | Auto enabling bitmask (all apps) | Integer
9577 | DNOM Component | Substation | SUB | input | DNAFCAPABLE | Whether the substation is DNAF capable. | Boolean
9578 | DNOM Component | Substation | SUB | input | DNAFDCEVERSIONFORDPF | DCE parameters version for DPF | String
9579 | DNOM Component | Substation | SUB | input | DNAFDCEVERSIONFORPRV | DCE parameters version for PRV | String
9580 | DNOM Component | Substation | SUB | input | DNAFDPFENABLED | Indicate if the DPF application is enabled | Boolean
9581 | DNOM Component | Substation | SUB | input | DNAFENABLED | Whether the DNAF application is enabled in the substation. | Boolean
9582 | DNOM Component | Substation | SUB | input | DNAFENABLEDAFALARMS | Bitmaks that indicates if the AF alarm is enabled | Integer
9583 | DNOM Component | Substation | SUB | input | DNAFENABLEDAPPS | DNAF control flag bitmask that indicates if the DPF application is enabled | Integer
9584 | DNOM Component | Substation | SUB | input | DNAFENABLEDFIALARMS | Bitmaks that indicates if the FI alarm is enabled | Integer
9585 | DNOM Component | Substation | SUB |  | DNAFENABLEDFLALARMS | DNAF enabled FL alarms | String
9586 | DNOM Component | Substation | SUB | input | DNAFENABLEDPFALARMS | Bitmaks that indicates if the power flow alarm is enabled | Integer
9587 | DNOM Component | Substation | SUB | input | DNAFENABLEDPVALARMS | Bitmaks that indicates if the PV alarm is enabled | Integer
9588 | DNOM Component | Substation | SUB | input | DNAFENABLEDVVALARMS | Bitmaks that indicates if the VV alarm is enabled | Integer
9589 | DNOM Component | Substation | SUB | input | DNAFLASTMODIFIEDFORDPF | DCE parameters' last modified date for DPF | String
9590 | DNOM Component | Substation | SUB | input | DNAFLASTMODIFIEDFORPRV | DCE parameters' last modified date for PRV | String
9591 | DNOM Component | Substation | SUB | input | DNAFLVMENABLED | Indicate if the LVM is enabled | Boolean |  | #N/A | #N/A
9592 | DNOM Component | Substation | SUB | output | DNAFLVMHISTORY | the time since last time LVM was solved(or solved-no plans) | Struct TM |  | #N/A | #N/A
9593 | DNOM Component | Substation | SUB | input | DNAFPRVENABLED | Indicate if the PRV is enabled | Boolean
9594 | DNOM Component | Substation | SUB | input | DNAFREVISIONNUMFORDPF | DCE parameter revision number for DPF | Integer
9595 | DNOM Component | Substation | SUB | input | DNAFREVISIONNUMFORPRV | DCE parameter revision number for PRV | Integer
9596 | DNOM Component | Substation | SUB | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
9597 | DNOM Component | Substation | SUB | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9598 | DNOM Component | Substation | SUB | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9599 | DNOM Component | Substation | SUB | output | DPFITERATIONS | Number of iterations for the latest DPF solution. | Integer | DPF | count | count
9600 | DNOM Component | Substation | SUB | output | DPFREFBUSES | DPF energizing station list. | String | DPF | #N/A | #N/A
9601 | DNOM Component | Substation | SUB | input | DSOGROUP.AFRCLOSEDLOOP | Flag indicating if the station is running AFR in closed loop mode | Boolean |  |  |  | DSOGRP
9602 | DNOM Component | Substation | SUB | input | DSOGROUP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9603 | DNOM Component | Substation | SUB | input | DSOGROUP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9604 | DNOM Component | Substation | SUB | input | DSOGROUP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9605 | DNOM Component | Substation | SUB | input | DSOGROUP.FISRCLOSEDLOOP | Flag indicating if the station is running FISR in closed loop mode | Boolean |  |  |  | DSOGRP
9606 | DNOM Component | Substation | SUB | input | DSOGROUP.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9607 | DNOM Component | Substation | SUB | input | DSOGROUP.LVMCLOSEDLOOP | Flag indicating if the station is running LVM in closed loop mode | Boolean |  |  |  | DSOGRP
9608 | DNOM Component | Substation | SUB | input | DSOGROUP.LVMHEURISTIC | A flag indicating that heuristic LVM solution is used | Boolean |  |  |  | DSOGRP
9609 | DNOM Component | Substation | SUB | input | DSOGROUP.NAME | Associated station group - used for real time LVM application. | String |  |  |  | DNMOBJ
9610 | DNOM Component | Substation | SUB | input | DSOGROUP.NUMOBJFUNCSCH | Number of objective function schedules | Integer |  |  |  | DSOGRP
9611 | DNOM Component | Substation | SUB |  | DPFREFBUSESFORCE | DPF reference bus force | String
9612 | DNOM Component | Substation | SUB | output | DPFSTATUS | Latest DPF solution status. | String | DPF | #N/A | #N/A
9613 | DNOM Component | Substation | SUB |  | DPFSTATUSCODE | DPF status code | String
9614 | DNOM Component | Substation | SUB | output | DPFVIOLEXISTS | Whether there is any violation exists for the station. | Boolean | DPF | #N/A | #N/A
9615 | DNOM Component | Substation | SUB | input | DSODISABLED | Whether the substation disables DSO. | Boolean
9616 | DNOM Component | Substation | SUB | input | DSOENABLED | Whether the substation enables DSO.. | Boolean
9617 | DNOM Component | Substation | SUB | input | DSOGROUP | Pointer to the associated Distribution System Optimizer | String
9618 | DNOM Component | Substation | SUB | output | DSOGROUPNAME | Name of the optimization group the station belongs to | String
9619 | DNOM Component | Substation | SUB | input | DSOOBJFUNCT | Default Objective Function used in real-time optimization applications | String
9620 | DNOM Component | Substation | SUB | input | DUPTOPOB | Flag indicating that the station has duplicate topology objects most likely due to multi-phase transformer bank fed from different stations. | Boolean
9621 | DNOM Component | Substation | SUB | input | EMSNAME | SCADA station name (eight-character maximum). | String
9622 | DNOM Component | Substation | SUB |  | FAULTLOCATIONMANCOUNT | Number of fault location manual inputs | Integer
9623 | DNOM Component | Substation | SUB | input | FAULTLOCATIONMANUALINPUT | Fault Location Manual inputed paramters count | Integer
9624 | DNOM Component | Substation | SUB | output | FAULTTEMPLINE | The id of component that is instantiated from the placement of a temporary ground object. | String | DPF | #N/A | #N/A
9625 | DNOM Component | Substation | SUB |  | FEEDERMANCOUNT | Number of feeder manual inputs | Integer
9626 | DNOM Component | Substation | SUB | input | FEEDERMANUALINPUT | Feeder Manual inputed paramters count | Integer
9627 | DNOM Component | Substation | SUB |  | FISRAUTOENABLEDTEXT | LVM auto enabled text | String
9628 | DNOM Component | Substation | SUB | output | FISRCAPEAKTIME | Latest FISRCA peak evaluation time. | String | FISRCA | #N/A | #N/A
9629 | DNOM Component | Substation | SUB | output | FISRCAPEAKTIME_TICKS | Peak FISRCA evaluatiion time (over the look ahead window). | Struct TM
9630 | DNOM Component | Substation | SUB |  | FISRCAPROFORMINDEX | Number of FISRCA problem formulation indices | Integer
9631 | DNOM Component | Substation | SUB | output | FISRCASTATIONEXETIME | Latest FISRCA execution time | String
9632 | DNOM Component | Substation | SUB | output | FISRCASTATIONEXETIME_TICKS | Latest FISRCA excution time | Struct TM
9633 | DNOM Component | Substation | SUB | output | FISRCASTATIONLASTSOLUTIONID | The last solution id for FISRCA. | String | FISRCA | #N/A | #N/A
9634 | DNOM Component | Substation | SUB | output | FISRCASTATIONTIME | Latest FISRCA solution time. | String | FISRCA | #N/A | #N/A
9635 | DNOM Component | Substation | SUB | output | FISRCASTATIONTIME_TICKS | Latest FISRCA solved time | Struct TM
9636 | DNOM Component | Substation | SUB | output | FISRCASTATUS | Latest FISRCA solution status. | String | FISRCA | #N/A | #N/A
9637 | DNOM Component | Substation | SUB |  | FISRCASTATUSCODE | FISRCA status code | String
9638 | DNOM Component | Substation | SUB | input | FISRCLOSEDLOOP | Flag indicating if the station is running FISR in closed loop mode | Boolean
9639 | DNOM Component | Substation | SUB | input | FISRLOSSVOLTPLANEXEC | Loss of voltage plan execution mode for FISR | Integer
9640 | DNOM Component | Substation | SUB | output | FISRPEAKTIME | Latest FISR peak evaluation time. | String | FISR | #N/A | #N/A
9641 | DNOM Component | Substation | SUB | output | FISRPEAKTIME_TICKS | Peak FISR evaluatiion time (over the look ahead window). | Struct TM
9642 | DNOM Component | Substation | SUB | input | FISRPERMFAULTPLANEXEC | Permanent Fault Plan Execution Mode for FISR | Integer
9643 | DNOM Component | Substation | SUB | input | FISRPROFORMINDEX | The FISR problem formulation index | Integer
9644 | DNOM Component | Substation | SUB | input | FISRPROFORMNAME | The FISR problem formulation name | Integer
9645 | DNOM Component | Substation | SUB | output | FISRSTATIONEXETIME | Latest FISR execution time. | String | FISR | #N/A | #N/A
9646 | DNOM Component | Substation | SUB | output | FISRSTATIONEXETIME_TICKS | Latest FISR excution time | Struct TM
9647 | DNOM Component | Substation | SUB | output | FISRSTATIONLASTSOLUTIONID | The last solution id for FISR. | String | FISR | #N/A | #N/A
9648 | DNOM Component | Substation | SUB | output | FISRSTATIONTIME | Latest FISR solution time. | String | FISR | #N/A | #N/A
9649 | DNOM Component | Substation | SUB | output | FISRSTATIONTIME_TICKS | Latest FISR solved time | Struct TM
9650 | DNOM Component | Substation | SUB | output | FISRSTATUS | Latest FISR solution status. | String | FISR | #N/A | #N/A
9651 | DNOM Component | Substation | SUB |  | FISRSTATUSCODE | FISR status code | String
9652 | DNOM Component | Substation | SUB | output | FLSTATIONEXETIME | Latest FL execution time. | String | FL | #N/A | #N/A
9653 | DNOM Component | Substation | SUB | output | FLSTATIONEXETIME_TICKS | Lastest FL execution time. | Struct TM
9654 | DNOM Component | Substation | SUB | output | FLSTATIONTIME | Latest FL solution time. | String | FL | #N/A | #N/A
9655 | DNOM Component | Substation | SUB | output | FLSTATIONTIME_TICKS | Latest FL solved time. | Struct TM
9656 | DNOM Component | Substation | SUB | output | FLSTATUS | Latest FL solution status. | String | FL | #N/A | #N/A
9657 | DNOM Component | Substation | SUB |  | FLSTATUSCODE | FL status code | String
9658 | DNOM Component | Substation | SUB | output | FSDAPPENABLED | Specifies whether the FSD application is enabled | Boolean
9659 | DNOM Component | Substation | SUB | input | FSDPLANEXEC | FSD plan execution mode (1 = semi-automatic, 2 = closed loop) | Integer
9660 | DNOM Component | Substation | SUB | output | FSDPROBLEMFORMULATIONENABLED | Specifies whether the FSD application problem formulation is selected for the substation | Boolean
9661 | DNOM Component | Substation | SUB | input | FSDPROFORMINDEX | FSD problem formulation index | Integer
9662 | DNOM Component | Substation | SUB | input | FUTURE | Station has future equipment flag | Boolean
9663 | DNOM Component | Substation | SUB |  | GENERATORMANCOUNT | Number of generator manual inputs | Integer
9664 | DNOM Component | Substation | SUB | input | GENERATORMANUALINPUT | Generator manual inputed parameter count | Integer
9665 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGECALCAMPWEIGHTALLBUS | Weighted calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9666 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGECALCAMPWEIGHTMVBUS | Weighted calculated average voltage in per unit. Only station MV buses are accounted. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
9667 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGECALCNOWEIGHTALLBUS | Calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. | Float | DPF | p.u. | p.u.
9668 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGECALCNOWEIGHTMVBUS | Calculated average voltage in per unit. Only station MV buses are accounted. | Float | DPF | p.u. | p.u.
9669 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9670 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGEMEASAMPWEIGHTMVBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9671 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGEMEASNOWEIGHTALLBUS | Weighted measured average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
9672 | DNOM Component | Substation | SUB | output | GROUPAVRAGEVOLTAGEMEASNOWEIGHTMVBUS | Measured average voltage, station bus only, in per unit | Float | DPF | p.u. | p.u.
9673 | DNOM Component | Substation | SUB | output | HASAFRPLANS | If station has AFR plan. | Boolean | AFR | #N/A | #N/A
9674 | DNOM Component | Substation | SUB | output | HASFISRCAPLANS | If station has FISRCA plan. | Boolean | FISRCA | #N/A | #N/A
9675 | DNOM Component | Substation | SUB | output | HASFISRPLANS | If station has FISR plan. | Boolean | FISR | #N/A | #N/A
9676 | DNOM Component | Substation | SUB | output | HASMAN_FDR_BUS_HV | Feeder bus HV violation limit (p.u.) manual value is auto, inherited or manual | String
9677 | DNOM Component | Substation | SUB | output | HASMAN_FDR_BUS_LV | Feeder bus LV violation limit (p.u.) manual value is auto, inherited or manual | String
9678 | DNOM Component | Substation | SUB | output | HASMAN_FDR_BUSOPT_HV | Feeder bus HV optimization limit (p.u.) manual value is auto, inherited or manual | String
9679 | DNOM Component | Substation | SUB | output | HASMAN_FDR_BUSOPT_LV | Feeder bus LV optimization limit (p.u.) manual value is auto, inherited or manual | String
9680 | DNOM Component | Substation | SUB | output | HASMAN_FDR_FLOW | Feeder devices flow limit % of nominal manual value is auto, inherited or manual | String
9681 | DNOM Component | Substation | SUB | output | HASMAN_FDR_LOAD_HV | Feeder load HV violation limit (p.u.) manual value is auto, inherited or manual | String
9682 | DNOM Component | Substation | SUB | output | HASMAN_FDR_LOAD_LV | Feeder load LV violation limit (p.u.) manual value is auto, inherited or manual | String
9683 | DNOM Component | Substation | SUB | input | HASMAN_FDR_LOADOPT_HV | Flag indicating feeder load HV optimization limit value is auto, inherited or manual | String
9684 | DNOM Component | Substation | SUB | input | HASMAN_FDR_LOADOPT_LV | Flag indicating feeder load LV optimization limit value is auto, inherited or manual | String
9685 | DNOM Component | Substation | SUB | output | HASMAN_FDR_LOADSCALING | Feeder load scaling factor manual value is auto, inherited or manual | String
9686 | DNOM Component | Substation | SUB | output | HASMAN_FDR_LVM_MAX_PF | feeder LVM maxinum PF target manual value is auto, inherited or manual | String
9687 | DNOM Component | Substation | SUB | output | HASMAN_FDR_LVM_MIN_PF | feeder LVM mininum PF target manual value is auto, inherited or manual | String
9688 | DNOM Component | Substation | SUB | input | HASMAN_REA_FL_FAULT_IMP | Specifies whether the station has manual FL fault impedance reactance override value | Boolean | DPF
9689 | DNOM Component | Substation | SUB | input | HASMAN_REA_PRV_FAULT_IMP | Specifies whether the station has manual PRV fault impedance reactance override value | Boolean | DPF
9690 | DNOM Component | Substation | SUB | input | HASMAN_REA_SCC_FAULT_IMP | Specifies whether the station has manual SCC fault impedance reactance override value | Boolean | DPF
9691 | DNOM Component | Substation | SUB | input | HASMAN_RES_FL_FAULT_IMP | Specifies whether the station has manual FL fault impedance resistance override value | Boolean | DPF
9692 | DNOM Component | Substation | SUB | input | HASMAN_RES_PRV_FAULT_IMP | Specifies whether the station has manual PRV fault impedance resistance override value | Boolean | DPF
9693 | DNOM Component | Substation | SUB | input | HASMAN_RES_SCC_FAULT_IMP | Specifies whether the station has manual SCC fault impedance resistance override value | Boolean | DPF
9694 | DNOM Component | Substation | SUB | output | HASMAN_SUB_FREQUENCY | Specifies whether a manually entered frequency value exists for a substation | String
9695 | DNOM Component | Substation | SUB | output | HASMAN_SUB_LVM_MAX_PF | Station LVM maxinum PF target manual value is auto, inherited or manual | String
9696 | DNOM Component | Substation | SUB | output | HASMAN_SUB_LVM_MIN_PF | Station LVM mininum PF target manual value is auto, inherited or manual | String
9697 | DNOM Component | Substation | SUB | output | HASMAN_SUB_TEMP | substation embient temperature manual value is auto, inherited or manual | String
9698 | DNOM Component | Substation | SUB | output | HASMAN_TRANS_FLOW | Transformer flow limit % of nominal manual value is auto, inherited or manual | String
9699 | DNOM Component | Substation | SUB | output | HASMANUALENTRY | Flag indicating if the substation has manual override parameters | Boolean
9700 | DNOM Component | Substation | SUB | output | HASNP | Indicates if the station has network protectors | Boolean
9701 | DNOM Component | Substation | SUB | output | HASPLORSPLANS | If station has POS plan. | Boolean | PLOS | #N/A | #N/A
9702 | DNOM Component | Substation | SUB |  | HASTHIRDPARTY | Flag indicating that the substation has devices that are owned by a third-party company downstream | Boolean
9703 | DNOM Component | Substation | SUB | output | HASVVCPLANS | If station has LVM plan. | Boolean | LVM | #N/A | #N/A
9704 | DNOM Component | Substation | SUB |  | HIGHESTPHANGLEDIFF | Maximum phase angle difference for the substation (%) | Float
9705 | DNOM Component | Substation | SUB | input | ID | Object unique ID | String |  |  |  | DNMOBJ
9706 | DNOM Component | Substation | SUB | output | ISDERGATEWAYCONTROLLED | Specifies whether the substation has DERs that are controlled by the 2030.5 Gateway | Boolean
9707 | DNOM Component | Substation | SUB | input | ISDISTSUBSTATION | Whether the substation is a distribution substation. | Boolean
9708 | DNOM Component | Substation | SUB | input | ISMBLSUB | Flag indicating this is a mobile substation. | Boolean
9709 | DNOM Component | Substation | SUB | input | ISMOBILESUB | Flag indicating this is a mobile substation. | Boolean
9710 | DNOM Component | Substation | SUB | input | ISRTAFRVALID | Specifies whether AFR is enabled for RT | Boolean
9711 | DNOM Component | Substation | SUB | input | ISRTDPFVALID | Specifies whether DPF is enabled for RT | Boolean
9712 | DNOM Component | Substation | SUB | input | ISRTFISRVALID | Specifies whether FISR is enabled for RT | Boolean
9713 | DNOM Component | Substation | SUB | input | ISRTFLVALID | Specifies whether FL is enabled for RT | Boolean
9714 | DNOM Component | Substation | SUB | input | ISRTLVMVALID | Specifies whether LVM is enabled for RT | Boolean
9715 | DNOM Component | Substation | SUB | input | ISRTPRVVALID | Specifies whether PRV is enabled for RT | Boolean
9716 | DNOM Component | Substation | SUB | input | ISRTSCCVALID | Specifies whether SCC is enabled for RT | Boolean
9717 | DNOM Component | Substation | SUB | input | ISSIMDPFVALID | Specifies whether DPF is enabled for SIM | Boolean
9718 | DNOM Component | Substation | SUB | input | ISSIMFLVALID | Specifies whether FL is enabled for SIM | Boolean
9719 | DNOM Component | Substation | SUB | input | ISSTAFRVALID | Specifies whether AFR is enabled for ST | Boolean
9720 | DNOM Component | Substation | SUB | input | ISSTDPFVALID | Specifies whether DPF is enabled for ST | Boolean
9721 | DNOM Component | Substation | SUB | input | ISSTFISRCAVALID | Specifies whether FISRCA is enabled for RT | Boolean
9722 | DNOM Component | Substation | SUB | input | ISSTFISRVALID | Specifies whether FISR is enabled for ST | Boolean
9723 | DNOM Component | Substation | SUB | input | ISSTFLVALID | Specifies whether FL is enabled for ST | Boolean
9724 | DNOM Component | Substation | SUB | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
9725 | DNOM Component | Substation | SUB | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
9726 | DNOM Component | Substation | SUB | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
9727 | DNOM Component | Substation | SUB | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
9728 | DNOM Component | Substation | SUB | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
9729 | DNOM Component | Substation | SUB | input | JUNCCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
9730 | DNOM Component | Substation | SUB | input | ISSTLVMVALID | Specifies whether LVM is enabled for ST | Boolean
9731 | DNOM Component | Substation | SUB | input | ISSTPLOSVALID | Specifies whether PLOS is enabled for ST | Boolean
9732 | DNOM Component | Substation | SUB | input | ISSTPRVVALID | Specifies whether PRV is enabled for ST | Boolean
9733 | DNOM Component | Substation | SUB | input | ISSTSCCVALID | Specifies whether SCC is enabled for ST | Boolean
9734 | DNOM Component | Substation | SUB | input | ISSUBFED | Flag indicating that the substation is fed from another distribution substation and does not have a reference bus interface (True = subfed). This flag MUST be set for a station which is sub-fed. Not setting this flag for a sub-fed station will result in slower NTP processing. | Boolean
9735 | DNOM Component | Substation | SUB | input | ISSUBFEDSUB | Flag indicating that the substation is fed from another distribution substation and does not have a reference bus interface (True = subfed). | Boolean
9736 | DNOM Component | Substation | SUB | input | ISTRNSSB | Transmission only station flag | Boolean
9737 | DNOM Component | Substation | SUB | input | JUNCCONT | The number of Junctions. | String
9738 | DNOM Component | Substation | SUB |  | LINEMANCOUNT | Number of line manual inputs | Integer
9739 | DNOM Component | Substation | SUB |  | LINEMANUALINPUT | Number of manual inputs for lines | String
9740 | DNOM Component | Substation | SUB | output | LINEVOLTDROPCOUNT | The amount of line which voltage drop exceeded the limit | Integer
9741 | DNOM Component | Substation | SUB | output | LKAHDEVALTIME | Look ahead evalution time | Struct TM
9742 | DNOM Component | Substation | SUB | output | LKAHDFLVTVIOL | Status of voltage/flow violations for each hour | Integer
9743 | DNOM Component | Substation | SUB |  | LOADCATMANCOUNT | Number of load category manual inputs | Integer
9744 | DNOM Component | Substation | SUB | input | LOADCATMANUALINPUT | LOADCATEGPRY Manual inputed paramters count | Integer
9745 | DNOM Component | Substation | SUB | input | LOADINGPERC | Manual entry value of load scaling factor. | Float
9746 | DNOM Component | Substation | SUB |  | LOADMANCOUNT | Number of load manual inputs | Integer
9747 | DNOM Component | Substation | SUB | input | LOADMANUALINPUT | Load Manual inputed paramters count | Integer
9748 | DNOM Component | Substation | SUB | input | LOADSHEDUPDATETIME | Load shed update time | String
9749 | DNOM Component | Substation | SUB | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
9750 | DNOM Component | Substation | SUB | output | LOOKAHEADSTATIONTIME | Latest look ahead funcion solved time | Struct TM
9751 | DNOM Component | Substation | SUB | output | LOOKAHEADSTATIONTIME_TICKS | Latest look ahead funcion solved time | Struct TM
9752 | DNOM Component | Substation | SUB | output | LOOKAHEADSTATUS | The look ahead solution status | String
9753 | DNOM Component | Substation | SUB |  | LOOKAHEADSTATUSCODE | Look ahead status code | String
9754 | DNOM Component | Substation | SUB | input | LSCALER | Load scaling factor | Float
9755 | DNOM Component | Substation | SUB |  | LVMAUTOENABLEDTEXT | LVM auto enabled text | String
9756 | DNOM Component | Substation | SUB | output | LVMCAPOPERATIONS | Counter for "Capacitor Opeartions" in LVM | Integer |  | #N/A | #N/A
9757 | DNOM Component | Substation | SUB | output | LVMCAPOPERATIONSEXC | Flag if the ounter for "Capacitor Opeartions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9758 | DNOM Component | Substation | SUB | input | LVMCLOSEDLOOP | Flag indicating if the station is running LVM in closed loop mode | Boolean
9759 | DNOM Component | Substation | SUB | output | LVMCONSDISSOLS | Counter for "Consecutive Discarded Solutions" in LVM | Integer |  | #N/A | #N/A
9760 | DNOM Component | Substation | SUB | output | LVMCONSDISSOLSEXC | Flag if the counter for "Consecutive Discarded Solutions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9761 | DNOM Component | Substation | SUB | output | LVMCONSINFSOLS | Counter for "Consecutive Infeasible Solutions" in LVM | Integer |  | #N/A | #N/A
9762 | DNOM Component | Substation | SUB | output | LVMCONSINFSOLSEXC | Flag if the counter for "Consecutive Infeasible Solutions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9763 | DNOM Component | Substation | SUB | output | LVMDAILYDISSOLS | Counter for "Daily Discarded Solutions" in LVM | Integer |  | #N/A | #N/A
9764 | DNOM Component | Substation | SUB | output | LVMDAILYDISSOLSEXC | Flag if the counter for "Daily Discarded Solutions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9765 | DNOM Component | Substation | SUB | output | LVMDAILYINFSOLS | Counter for "Daily Infeasible Solutions" in LVM | Integer |  | #N/A | #N/A
9766 | DNOM Component | Substation | SUB | output | LVMDAILYINFSOLSEXC | Flag if the counter for "Daily Infeasible Solutions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9767 | DNOM Component | Substation | SUB |  | LVMDASUPPORTMODE | LVM is currently in Distribution Automation support mode (0 - none, 1 - FISR, 2 - AFR) | Integer
9768 | DNOM Component | Substation | SUB | output | LVMEXEMODE | LVM execution mode | String
9769 | DNOM Component | Substation | SUB |  | LVMFAILSAFEACTIVE | Specifies whether a failsafe LVM problem formulation is applied. | Boolean
9770 | DNOM Component | Substation | SUB | input | LVMFAILSAFEREASON | This flag determines the LVM failsafe condition reason 1=Bus Voltage Mismatch, 2=DPF Solution State, 3=Bus Voltage Mismatch and DPF Solution State. | Integer
9771 | DNOM Component | Substation | SUB | input | LVMFAILSAFEREVERSALMETHOD | This flag determines whether LVM automatically reverts the problem formulation to the one used before the heuristic failsafe problem formulation. 0=Manual Reversion, 1=Automatic Reversion. | Integer
9772 | DNOM Component | Substation | SUB | output | LVMLTCOPERATIONS | Counter for "LTC & Regulators Opeartions" in LVM | Integer |  | #N/A | #N/A
9773 | DNOM Component | Substation | SUB | output | LVMLTCOPERATIONSEXC | Flag if the countER for "LTC & Regulators Opeartions" exceed the max value in LVM | Boolean |  | #N/A | #N/A
9774 | DNOM Component | Substation | SUB | input | LVMPLANEXEC | Plan Execution Mode for LVM | Integer
9775 | DNOM Component | Substation | SUB | output | LVMPROFILEDATA | LVM profile data | Integer
9776 | DNOM Component | Substation | SUB | input | LVMPROFORMINDEX | Index of the LVM problem formulation used for the station | Integer
9777 | DNOM Component | Substation | SUB |  | LVMPROFORMNAME | Name of the LVM problem formulation | String
9778 | DNOM Component | Substation | SUB | output | LVMPROFORMNAMES | The active problem formulations names for LVM. | String |  | #N/A | #N/A
9779 | DNOM Component | Substation | SUB | input | LVMSOLUTIONTYPE | Indicates the applied LVM approach: Optimization LVM, Heuristic LVM, or Fixed Regulation LVM | Integer
9780 | DNOM Component | Substation | SUB | output | LVMSTATUS | VVC solution status | String
9781 | DNOM Component | Substation | SUB |  | LVMSTATUSMEAS | LVM status measurement Id | String
9782 | DNOM Component | Substation | SUB | output | LVMTHROTTLINGSTATUS | Indicates whether real/reactive power throttling is enabled (Yes/No) | Boolean
9783 | DNOM Component | Substation | SUB | input | MAN_FDR_BUS_HV | Feeder bus HV violation limit (p.u.) manual override value | Float
9784 | DNOM Component | Substation | SUB | input | MAN_FDR_BUS_LV | Feeder bus LV violation limit (p.u.) manual override value | Float
9785 | DNOM Component | Substation | SUB | input | MAN_FDR_BUSOPT_HV | Feeder bus HV optimization limit (p.u.) manual override value | Float
9786 | DNOM Component | Substation | SUB | input | MAN_FDR_BUSOPT_LV | Feeder bus LV optimization limit (p.u.) manual override value | Float
9787 | DNOM Component | Substation | SUB | input | MAN_FDR_FLOW | Feeder devices flow limit % of nominal manual override value | Float
9788 | DNOM Component | Substation | SUB | input | MAN_FDR_LOAD_HV | Feeder load HV violation limit (p.u.) manual override value | Float
9789 | DNOM Component | Substation | SUB | input | MAN_FDR_LOAD_LV | Feeder load LV violation limit (p.u.) manual override value | Float
9790 | DNOM Component | Substation | SUB | input | MAN_FDR_LOADOPT_HV | Feeder load HV optimization limit (p.u.) manual override value | Float
9791 | DNOM Component | Substation | SUB | input | MAN_FDR_LOADOPT_LV | Feeder load LV optimization limit (p.u.) manual override value | Float
9792 | DNOM Component | Substation | SUB | input | MAN_FDR_LOADSCALING | Feeder load scaling factor manual override value | Float
9793 | DNOM Component | Substation | SUB | input | MAN_FDR_LVM_MAX_PF | Feeder LVM maxinum PF target manual override value | Float
9794 | DNOM Component | Substation | SUB | input | MAN_FDR_LVM_MIN_PF | Feeder LVM mininum PF target manual override value | Float
9795 | DNOM Component | Substation | SUB | input | MAN_REA_FL_FAULT_IMP | Station manual FL fault impedance reactance override value | Float | DPF | ohms | ohms
9796 | DNOM Component | Substation | SUB | input | MAN_REA_PRV_FAULT_IMP | Station manual PRV fault impedance reactance override value | Float | DPF | ohms | ohms
9797 | DNOM Component | Substation | SUB | input | MAN_REA_SCC_FAULT_IMP | Station manual SCC fault impedance reactance override value | Float | DPF | ohms | ohms
9798 | DNOM Component | Substation | SUB | input | MAN_RES_FL_FAULT_IMP | Station manual FL fault impedance resistance override value | Float | DPF | ohms | ohms
9799 | DNOM Component | Substation | SUB | input | MAN_RES_PRV_FAULT_IMP | Station manual PRV fault impedance resistance override value | Float | DPF | ohms | ohms
9800 | DNOM Component | Substation | SUB | input | MAN_RES_SCC_FAULT_IMP | Station manual SCC fault impedance resistance override value | Float | DPF | ohms | ohms
9801 | DNOM Component | Substation | SUB | input | MAN_SUB_FREQUENCY | The manually entered frequency value for a substation | Boolean
9802 | DNOM Component | Substation | SUB | input | MAN_SUB_LVM_MAX_PF | Station LVM maxinum PF target manual override value | Float
9803 | DNOM Component | Substation | SUB | input | MAN_SUB_LVM_MIN_PF | Station LVM mininum PF target manual override value | Float
9804 | DNOM Component | Substation | SUB | input | MAN_SUB_TEMP | Substation embient temperature manual override value | Float
9805 | DNOM Component | Substation | SUB | input | MAN_TRANS_FLOW | Transformer flow limit % of nominal manual override value | Float
9806 | DNOM Component | Substation | SUB | input | MANBLKREG | Block regulators flag. | Boolean
9807 | DNOM Component | Substation | SUB | input | MANDNAFENABLED | Disable DNAF flag. | Boolean
9808 | DNOM Component | Substation | SUB | input | MANDSOENABLED | Disable only DSO flag. | Boolean
9809 | DNOM Component | Substation | SUB | input | MANMODELQUALITYREVIEWED | Manual Model Quality Review Flag | Boolean |  | #N/A | #N/A
9810 | DNOM Component | Substation | SUB | input | MANVREDSTAT | Voltage reduction flag. | Boolean
9811 | DNOM Component | Substation | SUB | output | MATCHNTPDPFREFBUSES | Whether the NTP and DPF reference bus is matched. | Boolean | DPF | #N/A | #N/A
9812 | DNOM Component | Substation | SUB | output | MAXVMEASMISMATCH | Maximim voltage mismatch (at station internal buses) | Float
9813 | DNOM Component | Substation | SUB | output | MAXVMEASMISMATCHEXCD | Maximim voltage mismatch that exceeds the limit | Float
9814 | DNOM Component | Substation | SUB | input | MBGEOMNM | Name of the geometry that is adjusted for the mobile substation. | String
9815 | DNOM Component | Substation | SUB | input | MBNEARSB | Name of the nearest substation. | String
9816 | DNOM Component | Substation | SUB | input | MBSUBXPS | Current x coordinate position. | Float
9817 | DNOM Component | Substation | SUB | input | MBSUBYPS | Current y coordinate position. | Float
9818 | DNOM Component | Substation | SUB | input | METUNITS | Metric units flag used mainly in line model processing for impedance and admittance | Boolean
9819 | DNOM Component | Substation | SUB | output | MOBILESUBCONNECTED | Flag indicating the station has been connected to another station. | String | NTP | #N/A | #N/A
9820 | DNOM Component | Substation | SUB | input | NAME | Object name | String |  |  |  | DNMOBJ
9821 | DNOM Component | Substation | SUB | output | NTPREFBUSES | NTP energizing station list. | String | NTP | #N/A | #N/A
9822 | DNOM Component | Substation | SUB |  | NUMABTOT | The total number of abnormal conditions including switch statuses and temporary modifications for the sub-transmission network and outside the distribution fence | Integer
9823 | DNOM Component | Substation | SUB | output | NUMAFRPLAN | The number of plan for AFR. | Integer | AFR | count | count
9824 | DNOM Component | Substation | SUB | output | NUMAFRSOLUTION | The number of control solution for AFR. | Integer | AFR | count | count
9825 | DNOM Component | Substation | SUB | input | NUMAUTOSWCLOSED | The number of the closed automated switch. | Integer
9826 | DNOM Component | Substation | SUB | input | NUMAUTOSWOPEN | The number of the open automated switch. | Integer
9827 | DNOM Component | Substation | SUB | output | NUMBLASWCHECK | The number of devices which have a potential inconsistency issue for the station. | Integer
9828 | DNOM Component | Substation | SUB | input | NUMCABINET | The number of cabinets. | Integer
9829 | DNOM Component | Substation | SUB | input | NUMCOMPSWT | The number of composite switches. | Integer
9830 | DNOM Component | Substation | SUB | input | NUMCUT | The number of cuts. | Integer
9831 | DNOM Component | Substation | SUB | input | NUMDBANK | The number of duct banks. | Integer
9832 | DNOM Component | Substation | SUB | output | NUMDEENG | Number of de-energized customers. | Integer | NTP | count | count
9833 | DNOM Component | Substation | SUB | input | NUMDISTTF | The number of distributed transformers. | Integer
9834 | DNOM Component | Substation | SUB | input | NUMFDR | The number of feeders. | Integer
9835 | DNOM Component | Substation | SUB | output | NUMFISRCASOLUTION | The number of control solution for FISRCA. | Integer | FISRCA | count | count
9836 | DNOM Component | Substation | SUB | output | NUMFISRPLAN | The number of plan for FISR. | Integer | FISR | count | count
9837 | DNOM Component | Substation | SUB | output | NUMFISRSOLUTION | The number of control solution for FISR. | Integer | FISR | count | count
9838 | DNOM Component | Substation | SUB | input | NUMFLTIND | The number of fault detectors. | Integer
9839 | DNOM Component | Substation | SUB | input | NUMGEN | The number of generators. | Integer
9840 | DNOM Component | Substation | SUB | input | NUMGRND | The number of groundings. | Integer
9841 | DNOM Component | Substation | SUB | input | NUMINTFC | The number of interfaces. | Integer
9842 | DNOM Component | Substation | SUB | input | NUMLINE | The number of lines. | Integer
9843 | DNOM Component | Substation | SUB | input | NUMLOAD | The number of loads. | Integer
9844 | DNOM Component | Substation | SUB | input | NUMLOADSHEDACTIVE | Number of active load shed devices | String
9845 | DNOM Component | Substation | SUB | input | NUMLOADSHEDDEVICES | Number of load shed devices | String
9846 | DNOM Component | Substation | SUB | input | NUMLOADSHEDDISABLED | Number of disabled load shed devices | String
9847 | DNOM Component | Substation | SUB | input | NUMLOADSHEDENABLED | Number of enabled load shed devices | String
9848 | DNOM Component | Substation | SUB | input | NUMMANHOLE | The number of manholes. | Integer
9849 | DNOM Component | Substation | SUB | input | NUMMEAS | The number of measurements. | Integer
9850 | DNOM Component | Substation | SUB | input | NUMNODE | The number of nodes. | Integer
9851 | DNOM Component | Substation | SUB | output | NUMPLORSPLAN | The number of plan for POS. | Integer | PLOS | count | count
9852 | DNOM Component | Substation | SUB | output | NUMPLORSSOLUTION | The number of control solution for POS. | Integer | PLOS | count | count
9853 | DNOM Component | Substation | SUB | input | NUMPOWTF | The number of power transformers. | Integer
9854 | DNOM Component | Substation | SUB | input | NUMREGDT | The number of regular day types. | Integer
9855 | DNOM Component | Substation | SUB | input | NUMSERIES | The number of series reactors. | Integer
9856 | DNOM Component | Substation | SUB | input | NUMSHIMP | The number of shunt impedances. | Integer
9857 | DNOM Component | Substation | SUB | input | NUMSVC | The number of SVCs. | Integer
9858 | DNOM Component | Substation | SUB | input | NUMSWT | The number of switches. | Integer
9859 | DNOM Component | Substation | SUB | input | NUMTF | The number of transformers. | Integer
9860 | DNOM Component | Substation | SUB | input | NUMTMPGRND | The number of temporary groundings. | Integer
9861 | DNOM Component | Substation | SUB | input | NUMTMPSWT | The number of temporary switches. | Integer
9862 | DNOM Component | Substation | SUB | output | NUMVVCSOLUTION | The number of control solution for LVM. | Integer | LVM | count | count
9863 | DNOM Component | Substation | SUB |  | OLDLVMPROFORMINDEX | Index of the LVM problem formulation that was specified in the DNAF System Configuration display for the station before applying a failsafe problem formulation. Used for HLVM Failsafe reversion. | Integer |  | #NA | #NA
9864 | DNOM Component | Substation | SUB | input | PAREANME | Associated permission area name. | String
9865 | DNOM Component | Substation | SUB | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
9866 | DNOM Component | Substation | SUB | output | PFEXECUTIONREASON | Reason for latest DPF execution: 0 – Not defined 1 – Periodic 2 – Periodic BLA Check 3 – Event 4 – User Request 5 – SCADA Rate of Change 6 – Voltage Quality 7 – Fast Trigger 11 – Tap Position Change | Integer | DPF
9867 | DNOM Component | Substation | SUB | output | DPFREQUESTID | DPF request ID | String | DPF | #N/A | #N/A
9868 | DNOM Component | Substation | SUB | output | PFSTATIONEVALCONVERGEDTIME | Latest converged DPF solution time. | String | DPF | #N/A | #N/A
9869 | DNOM Component | Substation | SUB | output | PFSTATIONEVALCONVERGEDTIME_TICKS | The Latest solution time Distribution Power Flow was converged | Struct TM
9870 | DNOM Component | Substation | SUB | output | PFSTATIONEXETIME | Latest DPF execution time. | String | DPF | #N/A | #N/A
9871 | DNOM Component | Substation | SUB | output | PFSTATIONEXETIME_TICKS | The Latest Time Distribution Power Flow was executed. | Struct TM
9872 | DNOM Component | Substation | SUB | output | PFSTATIONTIME | Latest DPF solution time. | String | DPF | #N/A | #N/A
9873 | DNOM Component | Substation | SUB | output | PFSTATIONTIME_TICKS | The Latest Time Distribution Power Flow was solved | Struct TM
9874 | DNOM Component | Substation | SUB | output | PFSTATIONTIMEONLY | Time Distribution Power Flow was last solved. | String | DPF | #N/A | #N/A
9875 | DNOM Component | Substation | SUB | output | PFSTATIONTIMEONLY_TICKS | The Latest Time Distribution Power Flow was solved | Struct TM
9876 | DNOM Component | Substation | SUB |  | PLORSPROFORMINDEX | Number of PLOS problem formulation indices | Integer
9877 | DNOM Component | Substation | SUB | output | PLORSSTATIONLASTSOLUTIONID | The last solution id for POS. | String | PLOS | #N/A | #N/A
9878 | DNOM Component | Substation | SUB | output | POSPEAKTIME | Latest POS peak evaluation time. | String | PLOS | #N/A | #N/A
9879 | DNOM Component | Substation | SUB | output | POSPEAKTIME_TICKS | Peak PLORS evaluatiion time (over the look ahead window). | Struct TM
9880 | DNOM Component | Substation | SUB | output | POSSTATIONEXETIME | Latest POS execution time. | String | PLOS | #N/A | #N/A
9881 | DNOM Component | Substation | SUB | output | POSSTATIONEXETIME_TICKS | Latest Planned Outage REquest/Switching Orders Creation excution time | Struct TM
9882 | DNOM Component | Substation | SUB | output | POSSTATIONTIME | Latest POS solution time. | String | PLOS | #N/A | #N/A
9883 | DNOM Component | Substation | SUB | input | POWERTFS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
9884 | DNOM Component | Substation | SUB | input | POWERTFS.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
9885 | DNOM Component | Substation | SUB | input | POWERTFS.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | TF
9886 | DNOM Component | Substation | SUB | input | POWERTFS.DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean |  |  |  | TF
9887 | DNOM Component | Substation | SUB | input | POWERTFS.DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer |  |  |  | TF
9888 | DNOM Component | Substation | SUB | input | POWERTFS.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
9889 | DNOM Component | Substation | SUB | input | POWERTFS.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
9890 | DNOM Component | Substation | SUB | input | POWERTFS.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | TF
9891 | DNOM Component | Substation | SUB | input | POWERTFS.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | TF
9892 | DNOM Component | Substation | SUB | input | POWERTFS.FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float |  |  |  | TF
9893 | DNOM Component | Substation | SUB | input | POWERTFS.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
9894 | DNOM Component | Substation | SUB | input | POWERTFS.GROUNDPR | Primary grounded flag | Boolean |  |  |  | TF
9895 | DNOM Component | Substation | SUB | input | POWERTFS.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | TF
9896 | DNOM Component | Substation | SUB | input | POWERTFS.GROUNDTE | Tertiary grounded flag | Boolean |  |  |  | TF
9897 | DNOM Component | Substation | SUB | input | POWERTFS.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
9898 | DNOM Component | Substation | SUB | input | POWERTFS.LVMPROFORMINDEX | LVM problem formulation index | Integer |  |  |  | TF
9899 | DNOM Component | Substation | SUB | input | POWERTFS.MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer |  |  |  | TF
9900 | DNOM Component | Substation | SUB | input | POWERTFS.MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  |  |  | TF
9901 | DNOM Component | Substation | SUB | input | POWERTFS.NAME | Name of the object | String |  |  |  | DNMOBJ
9902 | DNOM Component | Substation | SUB | input | POWERTFS.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9903 | DNOM Component | Substation | SUB | input | POWERTFS.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
9904 | DNOM Component | Substation | SUB | input | POWERTFS.NOMCCUST | The number of nominally connected customers | Integer |  |  |  | TF
9905 | DNOM Component | Substation | SUB | input | POWERTFS.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
9906 | DNOM Component | Substation | SUB | input | POWERTFS.PRIMGNDR | Primary grounding branch resistance | Float |  | Ohms | Ohms | TF
9907 | DNOM Component | Substation | SUB | input | POWERTFS.PRIMGNDX | Primary grounding branch reactance | Float |  | Ohms | Ohms | TF
9908 | DNOM Component | Substation | SUB | input | POWERTFS.PRIMWIND | Primary winding connection type | Integer |  |  |  | TF
9909 | DNOM Component | Substation | SUB | input | POWERTFS.REGULATIONMARGIN | Regulation margin | Float |  |  |  | TF
9910 | DNOM Component | Substation | SUB | input | POWERTFS.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | TF
9911 | DNOM Component | Substation | SUB | input | POWERTFS.SEC1GNDR | Secondary grounding branch resistance | Float |  | Ohms | Ohms | TF
9912 | DNOM Component | Substation | SUB | input | POWERTFS.SEC1GNDX | Secondary grounding branch reactance | Float |  | Ohms | Ohms | TF
9913 | DNOM Component | Substation | SUB | input | POWERTFS.SEC2GNDR | Tertiary grounding branch resistance | Float |  | Ohms | Ohms | TF
9914 | DNOM Component | Substation | SUB | input | POWERTFS.SEC2GNDX | Tertiary grounding branch reactance | Float |  | Ohms | Ohms | TF
9915 | DNOM Component | Substation | SUB | input | POWERTFS.SECWIND | Secondary winding connection type | Integer |  |  |  | TF
9916 | DNOM Component | Substation | SUB | input | POWERTFS.TERTWIND | Tertiary winding connection type | Integer |  |  |  | TF
9917 | DNOM Component | Substation | SUB | input | POWERTFS.TFLOADED | Connected load flag | Boolean |  |  |  | TF
9918 | DNOM Component | Substation | SUB | input | POWERTFS.TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean |  |  |  | TF
9919 | DNOM Component | Substation | SUB | input | POWERTFS.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | TF
9920 | DNOM Component | Substation | SUB | input | POWERTFS.VOLTPR | Primary voltage (kV line to ground) | Float |  | kV | kV | TF
9921 | DNOM Component | Substation | SUB | input | POWERTFS.VOLTSC | Secondary voltage (kV line to ground) | Float |  | kV | kV | TF
9922 | DNOM Component | Substation | SUB | input | POWERTFS.VOLTTE | Tertiary voltage (kV line to ground) | Float |  | kV | kV | TF
9923 | DNOM Component | Substation | SUB | output | POSSTATIONTIME_TICKS | Latest Planned Outage REquest/Switching Orders Creation solved time | Struct TM
9924 | DNOM Component | Substation | SUB | output | POSSTATUS | Latest POS solution status. | String | PLOS | #N/A | #N/A
9925 | DNOM Component | Substation | SUB |  | POSSTATUSCODE | PLOS status code | String
9926 | DNOM Component | Substation | SUB |  | POWERTFCOUNT | The number of power transformers in the substation | String
9927 | DNOM Component | Substation | SUB |  | POWERTFMANCOUNT | Number of power transformer manual inputs | Integer
9928 | DNOM Component | Substation | SUB | input | POWERTFMANUALINPUT | Power transformer Manual inputed paramters count | Integer
9929 | DNOM Component | Substation | SUB | input | POWERTFS | Array of power transformers | String
9930 | DNOM Component | Substation | SUB | output | POWERTFVOLTDROPCOUNT | The amount of the power transformer which voltage drop exceeded limit | Integer
9931 | DNOM Component | Substation | SUB | output | PRVSTATIONEXETIME | Latest PRV execution time. | String | PRV | #N/A | #N/A
9932 | DNOM Component | Substation | SUB | output | PRVSTATIONEXETIME_TICKS | Latest PRV execution time. | Struct TM
9933 | DNOM Component | Substation | SUB | output | PRVSTATIONTIME | Latest PRV solution time. | String | PRV | #N/A | #N/A
9934 | DNOM Component | Substation | SUB | output | PRVSTATIONTIME_TICKS | Latest PRV solved time | Struct TM
9935 | DNOM Component | Substation | SUB | output | PRVSTATUS | Latest PRV solution status. | String | PRV | #N/A | #N/A
9936 | DNOM Component | Substation | SUB |  | PRVSTATUSCODE | Protection validation status code | String
9937 | DNOM Component | Substation | SUB | output | REACTIVEDEMANDDIFF | Total reactive power demand difference between calculated and measured values | String |  | MVAR | MVAR
9938 | DNOM Component | Substation | SUB |  | REFERENCEBUSMANCOUNT | Number of reference bus manual inputs | Integer
9939 | DNOM Component | Substation | SUB | input | REFERENCEBUSMANUALINPUT | Reference bus Manual inputed paramters count | Integer
9940 | DNOM Component | Substation | SUB | output | REGULATORVOLTDROPCOUNT | The amount of the regulator which voltage drop exceeded limit | Integer
9941 | DNOM Component | Substation | SUB | input | RTCLIENT | Flag indicting if the server is running in real-time mode. | Boolean
9942 | DNOM Component | Substation | SUB | input | RULESETNAME | Applied rule set name | String
9943 | DNOM Component | Substation | SUB | input | SAVECASEPATH | SaveCase file path. | String
9944 | DNOM Component | Substation | SUB | output | SCADAACTIVEDEMAND | Total measured real power load | String |  | MW | MW
9945 | DNOM Component | Substation | SUB |  | SCADAAFRENABLED | SCADA AFR enabled | Boolean
9946 | DNOM Component | Substation | SUB |  | SCADAFISRENABLED | SCADA FISR enabled | Boolean
9947 | DNOM Component | Substation | SUB |  | SCADALVMENABLED | SCADA LVM enabled | Boolean
9948 | DNOM Component | Substation | SUB | output | SCADAPOWERFACTOR | Measured power factor | String
9949 | DNOM Component | Substation | SUB | output | SCADAREACTIVEDEMAND | Total measured reactive power load | String |  | MVAR | MVAR
9950 | DNOM Component | Substation | SUB | output | SCCSTATIONEXETIME | Latest Short Circuit Calculation (SCC) excution time | Struct TM
9951 | DNOM Component | Substation | SUB | output | SCCSTATIONEXETIME_TICKS | Latest Short Circuit Calculation (SCC) excution time | Struct TM
9952 | DNOM Component | Substation | SUB | output | SCCSTATIONTIME | Latest Short Circuit Calculation (SCC) solved time | Struct TM
9953 | DNOM Component | Substation | SUB | output | SCCSTATIONTIME_TICKS | Latest Short Circuit Calculation (SCC) solved time | Struct TM
9954 | DNOM Component | Substation | SUB | output | SCCSTATUS | SCC Solution quality flags | String | SCC | #N/A | #N/A
9955 | DNOM Component | Substation | SUB |  | SCCSTATUSCODE | SCC status code | String
9956 | DNOM Component | Substation | SUB | input | SCNEGSQR | Source negative sequence resistance (ohms) | Float
9957 | DNOM Component | Substation | SUB | input | SCNEGSQX | Source negative sequence reactance (ohms) | Float
9958 | DNOM Component | Substation | SUB | input | SCPOSSQR | Positive sequence resistance (ohms) | Float
9959 | DNOM Component | Substation | SUB | input | SCPOSSQX | Positive sequence reactance (ohms) | Float
9960 | DNOM Component | Substation | SUB | input | SCZOSSQR | Zero sequence resistance (ohms) | Float
9961 | DNOM Component | Substation | SUB | input | SCZOSSQX | Zero sequence reactance (ohms) | Float
9962 | DNOM Component | Substation | SUB |  | SERIESMANCOUNT | Series manual input count | Integer
9963 | DNOM Component | Substation | SUB |  | SERIESMANUALINPUT | Series manual input count | Integer
9964 | DNOM Component | Substation | SUB | input | SERVCNTR | Service center ID. | String
9965 | DNOM Component | Substation | SUB |  | SERVCNTRNAME | Service center name | String
9966 | DNOM Component | Substation | SUB | input | SETFP | State estimator values (MW) for power transformers. | String
9967 | DNOM Component | Substation | SUB | input | SETFQ | State estimator values (MVAR) for power transformers. | String
9968 | DNOM Component | Substation | SUB |  | SLSRULESET | SLS ruleset | String
9969 | DNOM Component | Substation | SUB |  | SRTINDEX | Used to transfer index information in serialized file | String
9970 | DNOM Component | Substation | SUB | output | STATIONEERRORCTPERBLA | Measurement Error Count from Last Solution | Integer | DPF | count | count
9971 | DNOM Component | Substation | SUB | input | STATIONFUTUREEQUIP | Station has future equipment flag | Boolean
9972 | DNOM Component | Substation | SUB |  | STATIONMANCOUNT | Number of station manual inputs | Integer
9973 | DNOM Component | Substation | SUB | input | STATIONWIDEMANUALINPUT | Station Manual inputed paramters count | Integer
9974 | DNOM Component | Substation | SUB | output | STEPTFVOLTDROPCOUNT | The amount of the step up down transformer which voltage drop exceeded limit | Integer
9975 | DNOM Component | Substation | SUB | output | STNEXCPTFLOWSORT | The highest loading in percent | Float | DPF | percent | percent
9976 | DNOM Component | Substation | SUB | output | STNEXCPTFLWIMBSORT | Highest phase flow imbalance. | Float | DPF | amps | amps
9977 | DNOM Component | Substation | SUB | output | STNEXCPTGRNDRTSORT | The highest ground return current in the breaker and recloser in percent | Float | DPF | percent | percent
9978 | DNOM Component | Substation | SUB | output | STNEXCPTNEUCURRTSORT | The highest neutral relay current in the breaker and recloser in percent | Float | PRV | percent | percent
9979 | DNOM Component | Substation | SUB | output | STNEXCPTVHISORT | The highest voltage in percent | Float | DPF | percent | percent
9980 | DNOM Component | Substation | SUB | output | STNEXCPTVIMBSORT | The highest voltage imbalance in percent | Float | DPF | percent | percent
9981 | DNOM Component | Substation | SUB | output | STNEXCPTVLOSORT | The lowest voltage in percent | Float | DPF | percent | percent
9982 | DNOM Component | Substation | SUB | output | SUBCAPAMARGINVIO | Station capacity margin violation | Boolean | DPF | #N/A | #N/A
9983 | DNOM Component | Substation | SUB | input | SUBDNAFDISABLED | Disable DNAF flags. | Boolean
9984 | DNOM Component | Substation | SUB | output | SUBDPFCONV | If the DPF converged. | Boolean | DPF | #N/A | #N/A
9985 | DNOM Component | Substation | SUB | input | SUBDSODISABLED | Disable DSO flag | Boolean
9986 | DNOM Component | Substation | SUB | output | SUBENERGZ1 | Energizing station. | String | NTP | #N/A | #N/A
9987 | DNOM Component | Substation | SUB | output | SUBENERGZ2 | Energizing station. | String | NTP | #N/A | #N/A
9988 | DNOM Component | Substation | SUB | output | SUBENERGZ3 | Energizing station. | String | NTP | #N/A | #N/A
9989 | DNOM Component | Substation | SUB | output | SUBENERGZ4 | Energizing station. | String | NTP | #N/A | #N/A
9990 | DNOM Component | Substation | SUB |  | SUBFLOWOVERLIMITPERCENT | Percent of highest flow over the corresponding limit level | Float
9991 | DNOM Component | Substation | SUB | output | SUBFLWIMBAL | Highest phase flow imbalance. | Float | DPF | amps | amps
9992 | DNOM Component | Substation | SUB | output | SUBGROUNDRETURN | Highest station ground trip return current (% of phase trip setting for breakers and reclosers). | Float | DPF | percent | percent
9993 | DNOM Component | Substation | SUB | output | SUBHASDUPLICATETOP | Whether there is duplicated topology. | Boolean | NTP | #N/A | #N/A
9994 | DNOM Component | Substation | SUB |  | SUBHIGHESTVOLTOVERPERCENT | Percent of highest voltage over nominal percent | Float
9995 | DNOM Component | Substation | SUB | output | SUBHIGHLOADDEVICE | Most heavily loaded branch ID | String | DPF
9996 | DNOM Component | Substation | SUB | output | SUBHIGHVOLT | Highest load or bus voltage in the substation (%). | Float | DPF | percent | percent
9997 | DNOM Component | Substation | SUB |  | SUBHIGHVOLTID | ID of the device with high voltage violation | String
9998 | DNOM Component | Substation | SUB |  | SUBHIGHVOLTVIOL | High voltage violation | Boolean
9999 | DNOM Component | Substation | SUB | output | SUBKVARLOSS | The total reactive loss of substation. Includes transformer losses, series reactor losses, shunt impedance losses, and feeder losses (line, series reactor, distribution transformer, regulator, and capacitor losses). | Float | DPF | kVAR | kVAR
10000 | DNOM Component | Substation | SUB | output | SUBKVARMISMATCH | Reactive power mismatch (kVAR) for the latest DPF solution. | Float | DPF | kVAR | kVAR
10001 | DNOM Component | Substation | SUB | output | SUBKWLOSS | The total active loss of substation. Includes transformer losses, series reactor losses, shunt impedance losses, and feeder losses (line, series reactor, distribution transformer, regulator, and capacitor losses). | Float | DPF | kW | kW
10002 | DNOM Component | Substation | SUB | output | SUBKWMISMATCH | Real power mismatch (kW) for the latest DPF solution. | Float | DPF
10003 | DNOM Component | Substation | SUB | output | SUBLARGESTVMMIDMISMATCHNODEID | ID of the node with the largest voltage mismatch from the final iteration of the latest DPF solution. | String | DPF
10004 | DNOM Component | Substation | SUB | output | SUBLARGESTVMMIDMISMATCHNODENAME | Name of the node with the largest voltage mismatch from the final iteration of the latest DPF solution. | String
10005 | DNOM Component | Substation | SUB |  | SUBLOWESTVOLTBELOWPERCENT | Percent of lowest voltage below norminal percent | Float
10006 | DNOM Component | Substation | SUB | output | SUBLOWVOLT | Lowest load or bus voltage in the substation (%). | Float | DPF | percent | percent
10007 | DNOM Component | Substation | SUB |  | SUBLOWVOLTID | ID of the device with low voltage violation | String
10008 | DNOM Component | Substation | SUB |  | SUBLOWVOLTVIOL | Low voltage violation | Boolean
10009 | DNOM Component | Substation | SUB | output | SUBNEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
10010 | DNOM Component | Substation | SUB | output | SUBNUMHIGHVOLTVIOLATION | The number of high voltage violations | Integer | DPF
10011 | DNOM Component | Substation | SUB | output | SUBNUMLOWVOLTVIOLATION | The number of low voltage violations | Integer | DPF
10012 | DNOM Component | Substation | SUB | output | SUBNUMOVERLOAD | The number of overloads | Integer | DPF
10013 | DNOM Component | Substation | SUB | output | SUBOVERLOAD | Highest station loading value (%). | Float | DPF | percent | percent
10014 | DNOM Component | Substation | SUB | output | SUBOVERLOADLEVEL | Station highest flow limit overload level. | Integer | DPF | percent | percent
10015 | DNOM Component | Substation | SUB | input | SUBPROBFORMLV1 | Used for exponential scaling of voltage flattening weight.Exponential weight = VF1 * exp (VF2) | Float
10016 | DNOM Component | Substation | SUB | input | SUBPROBFORMLV2 | Used for exponential scaling of voltage flattening weight.Exponential weight = VF1 * exp (VF2) | Float
10017 | DNOM Component | Substation | SUB | input | SUBPROBFORMPF1 | Used for exponential scaling of power factor weight. Exponential weight = PF1 * exp (PF2) | Float
10018 | DNOM Component | Substation | SUB | input | SUBPROBFORMPF2 | Used for exponential scaling of power factor weight. Exponential weight = PF1 * exp (PF2) | Float
10019 | DNOM Component | Substation | SUB | output | SUBPTKVARLOSS | The total reactive loss in power transformers. | Float | DPF | kVAR | kVAR
10020 | DNOM Component | Substation | SUB | output | SUBPTKWLOSS | The total active loss in power transformers. | Float | DPF | kW | kW
10021 | DNOM Component | Substation | SUB | output | SUBREGKVARLOSS | The total reactive loss in regulators. | Float | DPF | kVAR | kVAR
10022 | DNOM Component | Substation | SUB | output | SUBREGKWLOSS | The total active power loss in regulators. | Float | DPF | kW | kW
10023 | DNOM Component | Substation | SUB | output | SUBSERIESKVARLOSS | The total reactive loss in series. | Float | DPF | kVAR | kVAR
10024 | DNOM Component | Substation | SUB | output | SUBSERIESKWLOSS | The total active loss in series. | Float | DPF | kW | kW
10025 | DNOM Component | Substation | SUB | input | SUBTEMP | The temperature of the substation | Float
10026 | DNOM Component | Substation | SUB | output | SUBTOTALFEEDERKVARLOSS | The total reactive loss in feeders. | Float | DPF | kVAR | kVAR
10027 | DNOM Component | Substation | SUB | output | SUBTOTALFEEDERKWLOSS | The total active loss in the feeders. | Float | DPF | kW | kW
10028 | DNOM Component | Substation | SUB | output | SUBTRANSSTATLIST | List of all stations in the subtransmission network. | String | NTP | #N/A | #N/A
10029 | DNOM Component | Substation | SUB | input | SUBVALIDMEASEXIST | Flag indicating if there are any valid measurements in the substation. | Boolean
10030 | DNOM Component | Substation | SUB | output | SUBVLTIMBAL | Highest three-phase load imbalance (%). | Float | DPF | percent | percent
10031 | DNOM Component | Substation | SUB | output | SUBVOLTMISMATCH | Voltage mismatch (per unit) for the latest DPF solution. | Float | DPF | per unit | per unit
10032 | DNOM Component | Substation | SUB | output | SUSPECTCONTROLCNT | The count of suspect controls for substation | Integer
10033 | DNOM Component | Substation | SUB | output | SUSPECTLOADCNT | The number of suspect load. | Integer | DPF | count | count
10034 | DNOM Component | Substation | SUB | output | SUSPECTSOURCECNT | The count of suspect generators/energy resources for substation | Integer
10035 | DNOM Component | Substation | SUB | output | SUSPECTSOURCEVOLTCNT | The count of Suspect Voltage Source interfaces for substation | Integer
10036 | DNOM Component | Substation | SUB |  | SWITCHMANCOUNT | Number of switch manual inputs | Integer
10037 | DNOM Component | Substation | SUB | input | SWITCHMANUALINPUT | Switch Manual inputed paramters count | Integer
10038 | DNOM Component | Substation | SUB | input | SYMBTYPE | Station display type | Integer
10039 | DNOM Component | Substation | SUB | input | SYSTEMWIDEMANUALINPUT | System Manual inputed paramters count | Integer
10040 | DNOM Component | Substation | SUB | input | TAPCHANGERMANUALINPUT | Tap changer Manual inputed paramters count | Integer
10041 | DNOM Component | Substation | SUB |  | TAPMANCOUNT | Number of tap changer manual inputs | Integer
10042 | DNOM Component | Substation | SUB | output | TCPEAKTIME | Peak TC evaluatiion time (over the look ahead window) | Struct TM
10043 | DNOM Component | Substation | SUB | output | TCPEAKTIME_TICKS | Peak TC evaluatiion time (over the look ahead window) | Struct TM
10044 | DNOM Component | Substation | SUB | output | TCSTATIONEXETIME | Latest Transfer Capacity (TC) execution time. | Struct TM
10045 | DNOM Component | Substation | SUB | output | TCSTATIONEXETIME_TICKS | Latest Transfer Capacity (TC) execution time. | Struct TM
10046 | DNOM Component | Substation | SUB | output | TCSTATIONTIME | Latest Transfer Capacity (TC) solved time. | Struct TM
10047 | DNOM Component | Substation | SUB | output | TCSTATIONTIME_TICKS | Latest Transfer Capacity (TC) solved time. | Struct TM
10048 | DNOM Component | Substation | SUB | output | TCSTATUS | TC solution status | String
10049 | DNOM Component | Substation | SUB |  | TCSTATUSCODE
10050 | DNOM Component | Substation | SUB | input | TFINDEXS | Array of power transformer indexes | String
10051 | DNOM Component | Substation | SUB | output | TNSUBDPF | Whether the DPF has been run. | Boolean | DPF | #N/A | #N/A
10052 | DNOM Component | Substation | SUB | input | TNSUBMEASUREMENT | Flag indicating if there are any measurements in the substation. | Boolean
10053 | DNOM Component | Substation | SUB | output | TOTALSUBCUSTOUT | The number of customers that are not energized. | Integer | DPF | count | count
10054 | DNOM Component | Substation | SUB |  | TSTINDEX | Used to transfer TSTindex information in serialized file | String
10055 | DNOM Component | Substation | SUB |  | TSTVALUE | Used to transfer TSTvalue information in serialized file | String
10056 | DNOM Component | Substation | SUB | input | VALSTAT | The validation status for the station. | Integer
10057 | DNOM Component | Substation | SUB | input | VOLTAGEREDUCTION | Voltage reduction flag. | Boolean
10058 | DNOM Component | Substation | SUB | input | VREDSTAT | Voltage reduction flag. | Boolean
10059 | DNOM Component | Substation | SUB | output | VVCFLOWLIMITS | The flow violation limits strategy used in LVM. | String | LVM | #N/A | #N/A
10060 | DNOM Component | Substation | SUB | output | VVCPROBFORM | The name of LVM problem formulation. | String | LVM | #N/A | #N/A
10061 | DNOM Component | Substation | SUB | output | VVCSTATGROUP | The name of substation group. | String | LVM | #N/A | #N/A
10062 | DNOM Component | Substation | SUB | output | VVCSTATIONEXETIME | Latest LVM execution time. | String | LVM | #N/A | #N/A
10063 | DNOM Component | Substation | SUB | output | VVCSTATIONEXETIME_TICKS | Latest VVC excution time | Struct TM
10064 | DNOM Component | Substation | SUB | output | VVCSTATIONLASTSOLUTIONID | The last solution id for LVM. | String | LVM | #N/A | #N/A
10065 | DNOM Component | Substation | SUB |  | VVCSTATIONLASTTIMEHASPLAN_TICKS | Last LVM solution time | String
10066 | DNOM Component | Substation | SUB | output | VVCSTATIONTIME | Latest LVM solution time. | String | LVM | #N/A | #N/A
10067 | DNOM Component | Substation | SUB | output | VVCSTATIONTIME_TICKS | Latest VVC solved time. | Struct TM
10068 | DNOM Component | Substation | SUB | output | VVCSTATUS | Latest LVM solution status. | String | LVM | #N/A | #N/A
10069 | DNOM Component | Substation | SUB |  | VVCSTATUSCODE | LVM status code | String
10070 | DNOM Component | Substation | SUB | output | VVCVOLTLIMITS | The voltage violation limits strategy used in LVM. | String | LVM | #N/A | #N/A
10071 | DNOM Component | Substation | SUB | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
10072 | DNOM Component | Substation | SUB | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
10073 | DNOM Component | Substation | SUB | input | INT64_TEST1 | For testing purposes: INT64 support of DNOM. | String
10074 | DNOM Component | Substation | SUB | input | INT64_TEST2 | For testing purposes: INT64 support of DNOM. | String
10075 | DNOM Component | Substation | SUB | input | INT64_SIZETEST | For testing purposes: INT64 support of DNOM. | String
10076 | DNOM Component | Substation | SUB | input | INT64_TESTARRAY | For testing purposes: INT64 support of DNOM. | String
10077 | DNOM Component | Substation | SUB | input | MEASHASHSUM | Hash sum that is calculated based on sorted list of all measurements in the system during station conversion. DMS server remembers the last hash sum for a station when a full measurements data update is received from SCADA. After a model push, the DMS server re-requests the updated data from SCADA only if the measurements hash sum differs from the previous value. | Integer
10078 | DNOM Component | Substation | SUB | input | MOBILESUBADJACENTSTATION | Substation where the mobile substation is placed. | String
10079 | DNOM Component | Substation | SUB | input | MOBILESUBPLACED | Flag indicating that this mobile substation is placed. | Boolean
10080 | DNOM Component | Substation Output | SUBOUT |  | BLADPFIC | Total number of BLA/DPF iterations | Integer
10081 | DNOM Component | Substation Output | SUBOUT |  | FLOWVIOL | Flag indicating presence of flow violations (1 - true, 0 - false) | Integer
10082 | DNOM Component | Substation Output | SUBOUT |  | GNDRTNVIOL | Flag indicating presence of ground return current violations (1 - true, 0 - false) | Integer
10083 | DNOM Component | Substation Output | SUBOUT |  | HLIMVIOL | Flag indicating the presence of high voltage violations (1 - true, 0 - false) | Integer
10084 | DNOM Component | Substation Output | SUBOUT |  | LLIMVIOL | Flag indicating the presence of low voltage violations (1 - true, 0 - false) | Integer
10085 | DNOM Component | Substation Output | SUBOUT | output | NEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
10086 | DNOM Component | Substation Output | SUBOUT | output | NEUCURVIOL | Specifies whether the neutral current violation exists | Boolean | PRV
10087 | DNOM Component | Static VAR Compensator | SV | input | MODEL.CAPRATE | Capacitive rating | Integer |  | kVAR | kVAR | SVCMOD
10088 | DNOM Component | Static VAR Compensator | SV | input | MODEL.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10089 | DNOM Component | Static VAR Compensator | SV | input | MODEL.INDRATE | Inductive rating | Integer |  | kVAR | kVAR | SVCMOD
10090 | DNOM Component | Static VAR Compensator | SV | input | MODEL.LIMNAME | An array of limit names | String |  |  |  | SVCMOD
10091 | DNOM Component | Static VAR Compensator | SV | input | MODEL.LIMUNIT | An array of limit units (1 - Amp , 2 - KVA, 3 - MVA = 3) | Enumeration |  |  |  | SVCMOD
10092 | DNOM Component | Static VAR Compensator | SV | input | MODEL.LIMVALUE | An array of limit values | Integer |  |  |  | SVCMOD
10093 | DNOM Component | Static VAR Compensator | SV | input | MODEL.NUMLIMIT | The number of limits | Integer |  |  |  | SVCMOD
10094 | DNOM Component | Substation Output | SUBOUT |  | NUMABNRM | The number of abnormal conditions from the distribution network (outside the station fence) | Integer
10095 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
10096 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
10097 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
10098 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
10099 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
10100 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10101 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10102 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10103 | DNOM Component | Static VAR Compensator | SV | input | REGNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
10104 | DNOM Component | Substation Output | SUBOUT |  | NUMABTOT | The total number of abnormal conditions including switch statuses and temporary modifications for the sub-transmission network and outside the distribution fence | Integer
10105 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.ID | ID of the schedule | String |  |  |  | DNMOBJ
10106 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
10107 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
10108 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
10109 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
10110 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
10111 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
10112 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
10113 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
10114 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
10115 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
10116 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.YUNITONE | Y1 axis units | String |  |  |  | SCHED
10117 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
10118 | DNOM Component | Substation Output | SUBOUT |  | NUMDEENG | The number of deenergized (nominal) customers | Integer
10119 | DNOM Component | Substation Output | SUBOUT |  | NUMDPFIT | DPF iteration count (last BLA/DPF iteration) | Integer
10120 | DNOM Component | Substation Output | SUBOUT |  | VIMBVIOL | Flag indicating presence of load voltage imbalance violations (1 - true, 0 - false) | Integer
10121 | DNOM Component | Static VAR Compensator | SV |  | CTRLMODE | Enumeration of control mode {0 - SVC_Voltage, 1 - SVC_Var} | Enumeration |  | enumeration | enumeration
10122 | DNOM Component | Static VAR Compensator | SV |  | DNOMRECORDNAME | The DNOM record name | String
10123 | DNOM Component | Static VAR Compensator | SV |  | DNOMTABNAME | The DNOM table name | String
10124 | DNOM Component | Static VAR Compensator | SV |  | LIMFLAGS | Number of limit violation flags | Integer
10125 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10126 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.CTRLMODE | Enumeration of control mode {0 - SVC_Voltage, 1 - SVC_Var} | Enumeration |  |  |  | SV
10127 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10128 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10129 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10130 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
10131 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10132 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.NAME | Name of the object | String |  |  |  | DNMOBJ
10133 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10134 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10135 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10136 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
10137 | DNOM Component | Static VAR Compensator | SV | input | MODEL | Pointer to the associated model | String
10138 | DNOM Component | Static VAR Compensator | SV | input | REGNODE | Pointer to the associated regulation node | String
10139 | DNOM Component | Static VAR Compensator | SV | input | REGSCHD | Pointer to associated regulstion schedule | String
10140 | Global Object | Service Model | SVCMOD |  | CAPRATE | Capacitive rating | Integer
10141 | Global Object | Service Model | SVCMOD |  | INDRATE | Inductive rating | Integer
10142 | Global Object | Service Model | SVCMOD |  | LIMNAME | An array of limit names | String
10143 | Global Object | Service Model | SVCMOD |  | LIMUNIT | An array of limit units (1 - Amp , 2 - KVA, 3 - MVA = 3) | Enumeration
10144 | Global Object | Service Model | SVCMOD |  | LIMVALUE | An array of limit values | Integer
10145 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10146 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.CTRLMODE | Enumeration of control mode {0 - SVC_Voltage, 1 - SVC_Var} | Enumeration |  |  |  | SV
10147 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10148 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10149 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10150 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
10151 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10152 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.NAME | Name of the object | String |  |  |  | DNMOBJ
10153 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10154 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10155 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10156 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
10157 | Global Object | Service Model | SVCMOD |  | NUMLIMIT | The number of limits | Integer
10158 | DNOM Component Placement | Service Placement | SVCPLE | input | SVC | Pointer to the associated SVC | String
10159 | DNOM Component | Service Center | SVECTR | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
10160 | DNOM Component | Service Center | SVECTR | input | ID | Object unique ID | String |  |  |  | DNMOBJ
10161 | DNOM Component | Service Center | SVECTR | input | NAME | Object name | String |  |  |  | DNMOBJ
10162 | DNOM Component | Service Center | SVECTR | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10163 | DNOM Component | Service Center | SVECTR | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10164 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10165 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10166 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
10167 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.CURROPEN | Current open status | Boolean |  |  |  | SWT
10168 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
10169 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10170 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10171 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
10172 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10173 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10174 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.NAME | Name of the object | String |  |  |  | DNMOBJ
10175 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10176 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10177 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.NOPEN | Normally Open | Boolean |  |  |  | SWT
10178 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10179 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.REMOTE | Remote | Boolean |  |  |  | SWT
10180 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
10181 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
10182 | DNOM Component | Service Center | SVECTR | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10183 | DNOM Component | Service Center | SVECTR | input | SRVCNTERSUBNAME | Substation name | String
10184 | DNOM Component Placement | Service Label Placement | SVLBPL | input | SVC | Pointer to the associated SVC | String
10185 | DNOM Component | SVC Output | SVOUT |  | IFLOWA | Phase A current injected into the SVC | Float |  | Amps | Amps
10186 | DNOM Component | SVC Output | SVOUT |  | IFLOWB | Phase B current injected into the SVC | Float |  | Amps | Amps
10187 | DNOM Component | SVC Output | SVOUT |  | IFLOWC | Phase C current injected into the SVC | Float |  | Amps | Amps
10188 | DNOM Component | SVC Output | SVOUT |  | PQFLOWA | Phase A power injected into the SVC | Float |  | kVA | kVA
10189 | DNOM Component | SVC Output | SVOUT |  | PQFLOWB | Phase B power injected into the SVC | Float |  | kVA | kVA
10190 | DNOM Component | SVC Output | SVOUT |  | PQFLOWC | Phase C power injected into the SVC | Float |  | kVA | kVA
10191 | DNOM Component Placement | Switch Label Placement | SWLBPL | input | SWITCH | Pointer to the associated switch | String
10192 | Global Object | Switch Model | SWMOD | input | LIMSEAS.AENDDT | Season end date | String |  |  |  | SEASON
10193 | Global Object | Switch Model | SWMOD | input | LIMSEAS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10194 | Global Object | Switch Model | SWMOD | input | LIMSEAS.ASTARTDT | Season start date | String |  |  |  | SEASON
10195 | Global Object | Switch Model | SWMOD | input | LIMSEAS.DESCRIPT | Season description | String |  |  |  | SEASON
10196 | Global Object | Switch Model | SWMOD | input | LIMSEAS.ID | Season unique ID | String |  |  |  | DNMOBJ
10197 | Global Object | Switch Model | SWMOD | input | LIMSEAS.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
10198 | Global Object | Switch Model | SWMOD |  | BTMAPSCH | Name of the bitmap scheme (default is blank). | String
10199 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
10200 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
10201 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
10202 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
10203 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
10204 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
10205 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
10206 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
10207 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
10208 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
10209 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
10210 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
10211 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
10212 | Global Object | Switch Model | SWMOD |  | CTRLABLE | Flag indicating that the switching device is controllable | Boolean
10213 | Global Object | Switch Model | SWMOD |  | DMSRCTYP | DMS recloser type optionally used by the Limit Monitor application (0 - Unknown, 1 - Electronic, 2 - Hydraulic} | Enumeration
10214 | Global Object | Switch Model | SWMOD |  | ELBOWFLG | Flag indicating whether the switch is an elbow switch(True=elbow). | String
10215 | Global Object | Switch Model | SWMOD |  | GANGED | Flag indicating ganged operation | Boolean
10216 | Global Object | Switch Model | SWMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
10217 | Global Object | Switch Model | SWMOD |  | ISWTTYPE | Enumerated switch type 1 - OH Single Blade Switch 2 - UG Elbow Switch 3 - Fuse Switch 4 - Jumper 5 - Recloser 6 - Sectionalizer 7 - UG Multi Switch 8 - Automated Field Switch 9 - UG Feeder Switch 11 - Throwover - non Powell ESCO 12 - Throwover - Powell ESCO 13 - 3 Phase TX Switch | Integer
10218 | Global Object | Switch Model | SWMOD |  | LIMITEVENT | A flag indicating operational limit event | Boolean
10219 | Global Object | Switch Model | SWMOD |  | LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term). | String
10220 | Global Object | Switch Model | SWMOD | input | LIMSEAS | The name of an associated season when the limit is applicable. If no season is given, then the limit is applied for the entire year. | String
10221 | Global Object | Switch Model | SWMOD | input | LIMTEMPSCHED | An array of ampacity schedule | String
10222 | Global Object | Switch Model | SWMOD |  | LIMUNIT | Enumerated limit units, 1 = amps, 2 = kVA. | Integer
10223 | Global Object | Switch Model | SWMOD |  | LIMVALUE | The value of the limit (in amps or kVA). | Float
10224 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.ID | ID of the schedule | String |  |  |  | DNMOBJ
10225 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
10226 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
10227 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
10228 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
10229 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
10230 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
10231 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
10232 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
10233 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
10234 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
10235 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.YUNITONE | Y1 axis units | String |  |  |  | SCHED
10236 | Global Object | Switch Model | SWMOD | input | SWCSTSCH.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
10237 | Global Object | Switch Model | SWMOD |  | LOADBRK | Flag indicating switch has load break capability (true = has load break capability). | Boolean
10238 | Global Object | Switch Model | SWMOD |  | LOADBRKR | Load break rating (Amps per phase) | Float
10239 | Global Object | Switch Model | SWMOD |  | MDBTMASK | Emumeration (1 - Ganged operation, 2 - Switch has load break capability, 3 - Switch can be identified using only its ID, 4 - Switching device is telemetered, 5 - Switchind device is controllable, 6 - Elbow switch. | Integer
10240 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10241 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10242 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
10243 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.CURROPEN | Current open status | Boolean |  |  |  | SWT
10244 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
10245 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10246 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10247 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
10248 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10249 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10250 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.NAME | Name of the object | String |  |  |  | DNMOBJ
10251 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10252 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10253 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.NOPEN | Normally Open | Boolean |  |  |  | SWT
10254 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10255 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.REMOTE | Remote | Boolean |  |  |  | SWT
10256 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
10257 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
10258 | Global Object | Switch Model | SWMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
10259 | Global Object | Switch Model | SWMOD |  | NUMLIMIT | The number of operation limits. | Integer
10260 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10261 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10262 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10263 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10264 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10265 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10266 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.NAME | Name of the object | String |  |  |  | DNMOBJ
10267 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10268 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10269 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10270 | Global Object | Switch Model | SWMOD |  | RECTYPE | Recloser type description (optional). | String
10271 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10272 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10273 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10274 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10275 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10276 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10277 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.NAME | Name of the object | String |  |  |  | DNMOBJ
10278 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10279 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10280 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10281 | Global Object | Switch Model | SWMOD |  | REVERSIBLE | Flag indicating whether one recloser is reversible for current flow direction | Boolean
10282 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10283 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10284 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10285 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10286 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10287 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10288 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.NAME | Name of the object | String |  |  |  | DNMOBJ
10289 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10290 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10291 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10292 | Global Object | Switch Model | SWMOD |  | SIZE | Device size (most likely an amp rating). | Float
10293 | Global Object | Switch Model | SWMOD |  | SWCOST | Default cost of performing a switching operation ($/operation). | Float
10294 | Global Object | Switch Model | SWMOD | input | SWCSTSCH | Pointer to the cost biasing schedule | String
10295 | Global Object | Switch Model | SWMOD |  | TELEMETR | Flag indicating that the switching device is telemetered | Boolean
10296 | Global Object | Switch Model | SWMOD |  | UNIQUEID | Flag that indicates that the device has a unique name. | Boolean
10297 | DNOM Component Placement | Switch Polygon Placement | SWPOPL | input | SWITCH | Pointer to the associated switch | String
10298 | DNOM Component | Switchable Section | SWSECT | input | AREAIND | Integer (index) into station permission area list. | Integer
10299 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMA | ID of branch with the lowest phase A limit. | String
10300 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMB | ID of branch with the lowest phase B limit. | String
10301 | DNOM Component | Switchable Section | SWSECT | input | BRCHLIMC | ID of branch with the lowest phase C limit. | String
10302 | DNOM Component | Switchable Section | SWSECT | input | DNOMX | X coordinate | Float
10303 | DNOM Component | Switchable Section | SWSECT | input | DNOMY | Y coordinate | Float
10304 | DNOM Component | Switchable Section | SWSECT | output | IAPERCNT | Percent current loading by phase A. This is calculated by dividing the phase A net injection Amps by the the lowest ampacity limit of backbone devices. | Float | DPF
10305 | DNOM Component | Switchable Section | SWSECT | output | IBPERCNT | Percent current loading by phase B. This is calculated by dividing the phase B net injection Amps by the the lowest ampacity limit of backbone devices. | Float | DPF
10306 | DNOM Component | Switchable Section | SWSECT | output | ICPERCNT | Percent current loading by phase C. This is calculated by dividing the phase C net injection Amps by the the lowest ampacity limit of backbone devices. | Float | DPF
10307 | DNOM Component | Switchable Section | SWSECT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
10308 | DNOM Component | Switchable Section | SWSECT | input | LOWLIMA | Lowest phase A branch flow limit value (Amps). | Float
10309 | DNOM Component | Switchable Section | SWSECT | input | LOWLIMB | Lowest phase B branch flow limit value (Amps). | Float
10310 | DNOM Component | Switchable Section | SWSECT | input | LOWLIMC | Lowest phase C branch flow limit value (Amps). | Float
10311 | DNOM Component | Switchable Section | SWSECT | input | NAME | Object name | String |  |  |  | DNMOBJ
10312 | DNOM Component | Switchable Section | SWSECT | input | NTPFLAG | NTP flags(e.g. 1 = section is fully energized, 2 = partially energized, 4 = one or more temp grounds) | Integer
10313 | DNOM Component | Switchable Section | SWSECT | input | NUMCRCST | Number of critical customers. | Integer
10314 | DNOM Component | Switchable Section | SWSECT | input | NUMCUST3 | Number of three-phase customers. | Integer
10315 | DNOM Component | Switchable Section | SWSECT | input | NUMCUSTA | Number of phase A customers. | Integer
10316 | DNOM Component | Switchable Section | SWSECT | input | NUMCUSTB | Number of phase B customers. | Integer
10317 | DNOM Component | Switchable Section | SWSECT | input | NUMCUSTC | Number of phase C customers. | Integer
10318 | DNOM Component | Switchable Section | SWSECT | input | NUMTF3 | Number of three-phase distribution transformers. | Integer
10319 | DNOM Component | Switchable Section | SWSECT | input | NUMTFA | Number of phase A distribution transformers. | Integer
10320 | DNOM Component | Switchable Section | SWSECT | input | NUMTFB | Number of phase B distribution transformers. | Integer
10321 | DNOM Component | Switchable Section | SWSECT | input | NUMTFC | Number of phase C distribution transformers. | Integer
10322 | DNOM Component | Switchable Section | SWSECT | output | SNETA | Net phase A apparent power flow (kVA). | Float | DPF
10323 | DNOM Component | Switchable Section | SWSECT | output | SNETB | Net phase B apparent power flow (kVA). | Float | DPF
10324 | DNOM Component | Switchable Section | SWSECT | output | SNETC | Net phase C apparent power flow (kVA). | Float | DPF
10325 | DNOM Component | Switchable Section | SWSECT |  | SSISOLSW | Name of isolation (boundary) switches of line associated switchable section. The field pertains to a switchable section. | String
10326 | DNOM Component | Switch | SWT | output | CURROPEN | Specifies whether the current component's state is Open (deenergized) | Boolean
10327 | DNOM Component | Switch | SWT | output | NORMOPEN | Specifies whether the current switch specific open state classification is Normal Open (normally open). | Boolean
10328 | DNOM Component | Switch | SWT | output | TEMPOPEN | Specifies whether the current switch specific open state classification is Temporary Open (temporary deenergized). | Boolean
10329 | DNOM Component | Switch | SWT | output | BADOPEN | Specifies whether the current switch specific open state classification is Bad Open (must not be closed at normal conditions). | Boolean
10330 | DNOM Component | Switch | SWT |  | MINGRDFLTLOCISGEOGRAPHIC | Specifies whether the fault location is in the geographic view (for the Minimum Ground Pick-Up Results display) | Boolean | PRV
10331 | DNOM Component | Switch | SWT |  | MINPHSFLTLOCHASPLACEMENT | Specifies whether a switch has placement (for the Minimum Phase Pick-Up Results display) | Boolean | PRV
10332 | DNOM Component | Switch | SWT |  | MINPHSFLTLOCISGEOGRAPHIC | Specifies whether the fault location is in the geographic view (for the Minimum Phase Pick-Up Results display) | Boolean | PRV
10333 | DNOM Component | Switch | SWT |  | MINPHASEFAULTSUBNAME | Name of the substation the device with the minimum phase fault belongs to | String
10334 | DNOM Component | Composite Switch | SWT | input | IMPEDANCEEVALUATIONTYPE | The fault impedance evaluation setting for the dynamic (energizing) feeder. | String | PRV
10335 | DNOM Component | Composite Switch | SWT | input | IMPEDANCEBOLTED | The bolted fault impedance (zero-fault impedance) in R + jX ohm. | String | PRV | R + jX ohm | R + jX ohm
10336 | DNOM Component | Composite Switch | SWT | input | IMPEDANCEUSERCONFIGURED | Fault Impedance - User Configured Fault Impedance: The user-configured fault impedance in R + jX ohm. | String | PRV | R + jX ohm | R + jX ohm
10337 | DNOM Component | Switch | SWT | input | _FINALVALUE | The switch's final status that is involved in the optimization move | String
10338 | DNOM Component | Switch | SWT | input | _OPTMOVADDR | The switch's device address that is involved in the optimization move | String
10339 | DNOM Component | Switch | SWT | input | _OPTMOVDEVID | The switch's device ID that is involved in the optimization move | String
10340 | DNOM Component | Switch | SWT | input | _OPTMOVDEVNAME | Switch's name | String
10341 | DNOM Component | Switch | SWT | input | _OPTMOVSUBNAME | Switch's substation name | String
10342 | DNOM Component | Switch | SWT | input | _PLANID | The plan ID for the optimization plan contains the switch | String
10343 | DNOM Component | Switch | SWT | input | ABNDATETIME | Date and time the status was last changed. | String
10344 | DNOM Component | Switch | SWT |  | ABNDATETIME_TICKS | The time when the switch’s status changed to abnormal | String
10345 | DNOM Component | Switch | SWT |  | ACTIVEPHASETRIP | Phase trip current rating of the currently active protection settings group | Float | PRV | Amps | Amps
10346 | DNOM Component | Switch | SWT |  | ACTIVEPICKUPCURRENT | The currently active ground pick-up current setting, in Amps (deprecated, not working for now) | Float | PRV | Amps | Amps
10347 | DNOM Component | Switch | SWT |  | ACTIVESETTINGGROUP | The currently active settings group name | String
10348 | DNOM Component | Switch | SWT |  | ACTIVESETTINGGROUPMEASINDEX | The currently active settings group value (index) | Integer
10349 | DNOM Component | Switch | SWT |  | ACTIVESETTINGSGROUPTEMPLATEDESCRIPTION | The currently active settings group template description | String
10350 | DNOM Component | Switch | SWT |  | ACTIVESETTINGSGROUPTEMPLATEID | The currently active settings group template ID | String
10351 | DNOM Component | Switch | SWT |  | ACTIVESETTINGSGROUPTEMPLATEMEASINDEX | The currently active settings group template value (index) | Integer
10352 | DNOM Component | Switch | SWT |  | ACTIVESETTINGSGROUPTEMPLATENAME | The currently active settings group template name | String
10353 | DNOM Component | Switch | SWT | input | AFRSWCONTROLENABLED | Flag indicting if the switch is optimization enabled for AFR under the current problem formulation. | Boolean
10354 | DNOM Component | Switch | SWT | input | PLOSSWCONTROLENABLED | Flag indicting if the switch is reconfiguration-enabled for PLOS under the current problem formulation. | Boolean
10355 | DNOM Component | Switch | SWT | input | AFRSWSGCONTROLENABLED | Flag indicting if the switch settings group change controls are eligible for AFR | Boolean
10356 | DNOM Component | Switch | SWT | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
10357 | DNOM Component | Switch | SWT | input | ALTID | Alternate ID of the device | String
10358 | DNOM Component | Switch | SWT | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10359 | DNOM Component | Switch | SWT | input | ASSOCSGTEMPLATE | Pointer to the associated protection settings group template | String
10360 | DNOM Component | Switch | SWT | input | BRKRCLSC.CLOSELATAMP | Sufficient energy that sprints needed to close and latch the onto protector | Integer |  |  |  | BRSSWT
10361 | DNOM Component | Switch | SWT | input | BRKRCLSC.COUNT | Number of counts before operation - sectionalizer | Integer |  |  |  | BRSSWT
10362 | DNOM Component | Switch | SWT | input | BRKRCLSC.GRDCAP | Ground Trip Capable | Boolean
10363 | DNOM Component | Switch | SWT | input | BRKRCLSC.GRID | The grid is the “feeder” for the low voltage secondary network | String |  |  |  | BRSSWT
10364 | DNOM Component | Switch | SWT | input | BRKRCLSC.GRIDCOLOR | A flag indicating that the secondary network of the network protector is looped | Boolean |  |  |  | BRSSWT
10365 | DNOM Component | Switch | SWT | input | BRKRCLSC.GRTRPAMP | Ground Trip Current | Float
10366 | DNOM Component | Switch | SWT | input | BRKRCLSC.MASTERRCL | The minimum voltage by which the network transformer secondary voltage must exceed the network voltage to permit reclosing when restoration | Integer |  |  |  | BRSSWT
10367 | DNOM Component | Switch | SWT | input | BRKRCLSC.MASTERTRIP | Real power flow in the reverse direction to make reverse-power function operate | Integer |  |  |  | BRSSWT
10368 | DNOM Component | Switch | SWT | input | BRKRCLSC.MAXINTRP | Maximum interrupting current rating (breakers and reclosers) | Float |  |  |  | BRSSWT
10369 | DNOM Component | Switch | SWT | input | BRKRCLSC.NORMGDTRP | Normal Ground Trip | Boolean
10370 | DNOM Component | Switch | SWT | input | BRKRCLSC.NPNOMOPMODE | Enumeration of the network protector operation mode (0 - NotSet, 1 - Automatic, 2 - Manual) | Enumeration |  |  |  | BRSSWT
10371 | DNOM Component | Switch | SWT | input | BRKRCLSC.NUMFLFAM | Number of analog fault current measurements for the device | Integer |  |  |  | BRSSWT
10372 | DNOM Component | Switch | SWT | input | BRKRCLSC.NUMGROPS | Number of ground reclose operations - breakers and reclosers | Integer |  |  |  | BRSSWT
10373 | DNOM Component | Switch | SWT | input | BRKRCLSC.NUMPHOPS | Number of phase reclose operations - breakers and reclosers | Integer |  |  |  | BRSSWT
10374 | DNOM Component | Switch | SWT | input | BRKRCLSC.PHAANGRCL | The angle by which the distribution transformer secondary voltage must lead the network voltage to ensure that real power will flow from the transformer to the network when the network protector is closed | Integer |  |  |  | BRSSWT
10375 | DNOM Component | Switch | SWT | input | BRKRCLSC.PHAANGTRIP | The minimum angle set for reverse power operation | Integer |  |  |  | BRSSWT
10376 | DNOM Component | Switch | SWT | input | BRKRCLSC.PHTRPAMP | Phase Trip Current | Float
10377 | DNOM Component | Switch | SWT | input | BRKRCLSC.RATING | A maximum rated device continuous for network protector | Integer |  |  |  | BRSSWT
10378 | DNOM Component | Switch | SWT | input | BRKRCLSC.RCLNOMOPMODE | Enumeration of recloser nominal operating mode (0 - None, should not occur for reclosers, only for breakers and sectionalizers, 1 - Switch_Mode, 2 - Recloser_Mode, 3 - Sectionalizer_Mode | Enumeration |  |  |  | BRSSWT
10379 | DNOM Component | Switch | SWT | input | BRKRCLSC.RECENAB | Flag indicating that the reclosing feature of a recloser/breaker is enabled or disabled (true = enabled) | Boolean |  |  |  | BRSSWT
10380 | DNOM Component | Switch | SWT | output | BLAAFFECTINGDEV | BLA consistency affecting device (device ID and consistency affecting reason) | String
10381 | DNOM Component | Switch | SWT | output | BLACHECK | Flag indicating if the device is valid (used) for BLA consistency check | Boolean
10382 | DNOM Component | Switch | SWT |  | BLOCKCLOSEDERNAME | The name (or ID if the name field is blank) of the energy resource with size greater than the value specified in the Minimum DER (kW) field for the FISR problem formulation of the dynamic feeder or pre-energized feeder if there is no dynamic feeder assigned. FISR plans will include a step to prevent connection of this energy resource. This field applies to both reclosers and breakers. | String
10383 | DNOM Component | Switch | SWT |  | BLOCKCLOSEMEASSTATUS | Block Close measurement status (Applied or Not Applied). This field applies to both reclosers and breakers. | String
10384 | DNOM Component | Switch | SWT | input | BOUNDSWDYNFDR1 | Boundary Switch Dynamic Feeder 1 | String
10385 | DNOM Component | Switch | SWT | input | BOUNDSWDYNFDR2 | Boundary Switch Dynamic Feeder 2 | String
10386 | DNOM Component | Switch | SWT |  | BOUNDSWFRNODE1 | To end node 1 of the boundary switch | String
10387 | DNOM Component | Switch | SWT |  | BOUNDSWFRNODE2 | To end node 2 of the boundary switch | String
10388 | DNOM Component | Switch | SWT | input | BOUNDSWFRNODEDYNFDR1 | Boundary Switch From Node Dynamic Feeder 1 | String
10389 | DNOM Component | Switch | SWT | input | BOUNDSWFRNODEDYNFDR2 | Boundary Switch From Node Dynamic Feeder 2 | String
10390 | DNOM Component | Switch | SWT | input | BOUNDSWSUB1 | Boundary Switch Station 1 | String
10391 | DNOM Component | Switch | SWT | input | BOUNDSWSUB2 | Boundary Switch Station 2 | String
10392 | DNOM Component | Switch | SWT |  | BOUNDSWTONODE1 | From end node 1 of the boundary switch | String
10393 | DNOM Component | Switch | SWT |  | BOUNDSWTONODE2 | From end node 2 of the boundary switch | String
10394 | DNOM Component | Switch | SWT | input | BOUNDSWTONODEDYNFDR1 | Boundary Switch To Node Dynamic Feeder 1 | String
10395 | DNOM Component | Switch | SWT | input | BOUNDSWTONODEDYNFDR2 | Boundary Switch To Node Dynamic Feeder 2 | String
10396 | DNOM Component | Switch | SWT | Input | BRAKERHASMANUALENTRY | Flag indicating the switch has manual fault location input | Boolean
10397 | DNOM Component | Switch | SWT | input | BRKFAULTINDSETSTATUSPHASE | Breaker fault indicator phases that are set. | Boolean
10398 | DNOM Component | Switch | SWT | input | BRKGRTRPAMP | Breaker ground trip setting (amps). | Float |  | Amps | Amps
10399 | DNOM Component | Switch | SWT | input | BRKALTPHTRPAMP | Alternative breaker ground trip setting (amps). | Float |  | Amps | Amps
10400 | DNOM Component | Switch | SWT | input | BRKALTGRTRPAMP | Alternative breaker phase trip setting (amps). | Float |  | Amps | Amps
10401 | DNOM Component | Switch | SWT | input | BRKPHTRPAMP | Breaker phase trip setting (amps). | Float |  | Amps | Amps
10402 | DNOM Component | Switch | SWT | input | BRKRCLSC | Pointer for For breakers, reclosers, and sectionalizers | String
10403 | DNOM Component | Switch | SWT |  | BYPASSSWT | Bypass switch name of a recloser or breaker. If name is not available, switch ID is returned. | String
10404 | DNOM Component | Switch | SWT | input | CHGNOPEN | Change the normal open status flag | Boolean
10405 | DNOM Component | Switch | SWT | input | CLOSEDBREAKER | Flag indicting the switch is closed breaker. | Boolean
10406 | DNOM Component | Switch | SWT | input | COMPCONFIRMCLOSED | Confirmed Closed | Boolean
10407 | DNOM Component | Switch | SWT | input | COMPMEMBER | Whether the switch is associated with the composite switches. | Boolean
10408 | DNOM Component | Switch | SWT | input | COMPPREDICTEDOUT | The device is closed but predicted open | Boolean
10409 | DNOM Component | Switch | SWT | Input | CONNECTTOGROUND | Flag indicating the switch is energized and grounded | Integer
10410 | DNOM Component | Switch | SWT | input | CREWDISPATCHED | Indicates whether a crew is dispatched | Boolean
10411 | DNOM Component | Switch | SWT | Input | CROSSPHASE | Flag indicating the switch is cross phase | Boolean
10412 | DNOM Component | Switch | SWT |  | CURRENTSETINDEX | Current set index | String
10413 | DNOM Component | Switch | SWT | input | ENERGYCAT.NOAPPSTR | Identifier of Incident energy category | String |  |  |  | NDPFST
10414 | DNOM Component | Switch | SWT |  | CURRENTSETTING | Current setting | String
10415 | DNOM Component | Switch | SWT |  | CURRPROTSETTING | Current protection setting | String
10416 | DNOM Component | Switch | SWT |  | CURRPROTSOURCES | Current protection sources | String
10417 | DNOM Component | Switch | SWT | input | DEFAULTLOADSHEDCLASS | Default load shed circuit classification | Integer
10418 | DNOM Component | Switch | SWT | input | DEFAULTLOADSHEDCLASSDESC | Default load shed circuit classification description | String
10419 | DNOM Component | Switch | SWT | input | DEVICEDSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String
10420 | DNOM Component | Switch | SWT | input | DEVICEPHASE | Switch's available phases | String
10421 | DNOM Component | Switch | SWT | input | DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer
10422 | DNOM Component | Switch | SWT | input | SWOPERATIONMODE | The current operation mode of the recloser (such as Switch, Recloser, or Sectionalizer). | String
10423 | DNOM Component | Switch | SWT | input | BOUNDEDSELFPROTECTEDTFNAME | Shows the name of the bounding self-protected power transformer. If the device name is not provided, it will show the device Id. | String
10424 | DNOM Component | Switch | SWT | input | BOUNDEDSELFPROTECTEDTFID | The ID of the bounding self-protected power transformer. | String
10425 | DNOM Component | Switch | SWT | input | BOUNDEDSELFPROTECTEDTFSUBNAME | The substation name that the bounding self-protected power transformer belongs to. | String
10426 | DNOM Component | Switch | SWT | input | DIVISION | Division name | String
10427 | DNOM Component | Switch | SWT |  | DMSRECLOSERTYPE | Recloser type | String
10428 | DNOM Component | Switch | SWT | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
10429 | DNOM Component | Switch | SWT | input | DNOMTABNAME | The DNOM table name of the switch. | String
10430 | DNOM Component | Switch | SWT | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10431 | DNOM Component | Switch | SWT | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10432 | DNOM Component | Switch | SWT |  | DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration
10433 | DNOM Component | Switch | SWT | input | DSOSWCONTROLENABLED | Flag indicting if the switch is optimization enabled for FISR under the current problem formulation. | Boolean
10434 | DNOM Component | Switch | SWT | input | DSOSWSGCONTROLENABLED | Flag indicting if the switch settings group change controls are eligible for reconfiguration applications | Boolean
10435 | DNOM Component | Switch | SWT | input | DYNAMICFEEDER | Switch's dynamic feeder | String
10436 | DNOM Component | Switch | SWT | input | DYNFEEDERNAME2 | Second dynamic energizing feeder name (for currently open switches). | String
10437 | DNOM Component | Switch | SWT |  | DYNSTATIONNAME | Name of the energizing substation | String
10438 | DNOM Component | Switch | SWT |  | DYNSTATIONNAME2 | Name of the second energizing substation | String
10439 | DNOM Component | Switch | SWT | input | ENERGYCAT | Pointer to a string in a station vector collection to suppress storage space | String
10440 | DNOM Component | Switch | SWT | Input | EXTERNALINTERFACE | Flag indicating if the switch is membership in external interface | Boolean
10441 | DNOM Component | Switch | SWT | Input | EXTERNALLYOWNED | Flag indicating if the switch's status is provided by the external system | Boolean
10442 | DNOM Component | Switch | SWT | input | FADEVTYPE | Returns TRUE if the switching device is a breaker, a recloser, or a fuse. Fuses can be included in the study mode Protection Validation (PRV) analysis when the Check Fuses option under the PRV Study Mode Options section in the DNAF Configuration Editor (DCE) is enabled. | Boolean
10443 | DNOM Component | Switch | SWT | input | PRVRECLOSINGDEVICES | Returns TRUE if the switching device is a breaker, a recloser in recloser mode, or a fuse. Fuses can be included in the study mode Protection Validation (PRV) analysis when the Check Fuses option under the PRV Study Mode Options section in the DNAF Configuration Editor (DCE) is enabled. | Boolean
10444 | DNOM Component | Switch | SWT | Input | FDRMAIN | Flag indicating the switch is a part of the feeder main | Boolean |  | #N/A | #N/A
10445 | DNOM Component | Switch | SWT | input | FEEDERBREAKERLOCKOUTFSDELIGIBLE | Specifies whether the feeder breaker is locked out and eligible for the FSD application | Boolean
10446 | DNOM Component | Switch | SWT | input | FEEDERBREAKEROPENED | Specifies whether the feeder breaker is open | Boolean
10447 | DNOM Component | Switch | SWT |  | FEEDERLOADSHEDCLASS | Default feeder load shed classification | String
10448 | DNOM Component | Switch | SWT |  | FEEDERLOADSHEDCLASSDESC | Default feeder load shed classification description | String
10449 | DNOM Component | Switch | SWT | Input | FEEDERMAIN | Flag indicating if the switch is on feeder main. | Boolean
10450 | DNOM Component | Switch | SWT | Input | FEEDINGFEEDER | The dynamic feeder name | String
10451 | DNOM Component | Switch | SWT | Input | FEEDINGSUB | The substation name of dynamic feeder | String
10452 | DNOM Component | Switch | SWT |  | FEEDMAINBOUND | A flag indicating that the switch is a feeder main boundary device | Boolean
10453 | DNOM Component | Switch | SWT | input | FROMEMS | Flag indicting the object is described in the EMS file during model construction | Boolean |  |  |  | TOPOLOGYOBJECT
10454 | DNOM Component | Switch | SWT |  | FROMLINEVERTEXSX | X coordinates of the from line vertices | Float
10455 | DNOM Component | Switch | SWT |  | FROMLINEVERTEXSY | Y coordinates of the from line vertices | Float
10456 | DNOM Component | Switch | SWT | output | FUSEKVAD | DPF calculated total apparent power flow (kVA). | Float | DPF | kVA | kVA
10457 | DNOM Component | Switch | SWT | output | FUSELOADPERCENT | DPF calculated three-phase loading percentage. | Float | DPF | percent | percent
10458 | DNOM Component | Switch | SWT | input | FUSELOOPNUMBER | Loop Number | String
10459 | DNOM Component | Switch | SWT | output | FUSETOTALAMPS | DPF calculated total current flow (amps). | Float | DPF | Amps | Amps
10460 | DNOM Component | Switch | SWT | output | GROUNDFAULTSENSITIVITYBOLTED | The ratio of the minimum ground fault current evaluated with a zero-fault impedance to the minimum ground pick-up current (multiplied by a safety factor). | Float | PRV | percent | percent
10461 | DNOM Component | Switch | SWT | output | GROUNDFAULTSENSITIVITYUSERCONFIGURED | The ratio of the minimum ground fault current evaluated with a user configured fault impedance to the minimum ground pick-up current (multiplied by a safety factor). | Float | PRV | percent | percent
10462 | DNOM Component | Switch | SWT |  | HAS_STATUS_MEAS | A flag indicating that the switch has status measurement | Boolean
10463 | DNOM Component | Switch | SWT | Input | HASSETGROUP | Flag indicating the switch has protection settings group | Boolean
10464 | DNOM Component | Switch | SWT | input | HASSGTEMPLATEMEAS | Flag indicating whether the device has the associated settings group template measurement | Boolean
10465 | DNOM Component | Switch | SWT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
10466 | DNOM Component | Switch | SWT | output | IMPEDANCEMAXFAULTCURRENT | The maximum short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
10467 | DNOM Component | Switch | SWT | output | IMPEDANCEMINGROUNDFAULTCURRENT | The minimum ground fault current (in Amps) calculated at the furthest downstream (highest impedance) location from the protective device in the protection area evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
10468 | DNOM Component | Switch | SWT | output | IMPEDANCEMINPHASEFAULTCURRENT | The minimum phase short circuit current (in Amps) calculated at the furthest downstream (highest impedance) location from the protective device in the protection area evaluated with a user configured fault impedance. | Float | PRV | Amps | Amps
10469 | DNOM Component | Switch | SWT | input | ISAUTOMATEDSWITCH | Whether the switch is an automated switch | Boolean
10470 | DNOM Component | Switch | SWT | input | ISFEEDERHEADTIEBREAKER | Specifies whether the switch is the feeder head tie beaker (True/False). | Boolean
10471 | DNOM Component | Switch | SWT | input | ISBUSTIESWITCH | Flag indicating this is an open tie switching device between two buses on the low voltage side of two power transformers in the substation. (True/False). | Boolean
10472 | DNOM Component | Switch | SWT | input | ISBREAKERORRECLOSER | Specifies whether the device is breaker or recloser (True/False). | Boolean
10473 | DNOM Component | Switch | SWT | input | HASASSOCIATEDCOMPOSITESWITCH | Specifies whether the switch is part of a composite switch (True/False). | Boolean
10474 | DNOM Component | Switch | SWT | input | SWITCHCOMPSWID | Unique identifier of the associated composite switch | String
10475 | DNOM Component | Switch | SWT | output | SWITCHCOMPSWSTATUS | Status of the associated composite switch | String
10476 | DNOM Component | Switch | SWT | input | ISLOADSHEDDEV | Indicates whether this is a load shed device | Boolean
10477 | DNOM Component | Switch | SWT | input | ISLOADSHEDENABLEDDEV | Indicates whether the device is enabled for load shed | Boolean
10478 | DNOM Component | Switch | SWT |  | ISRECLOSERBLOCKCLOSE | Specifies whether the recloser connects an energy resource with size greater than the value specified in the Minimum DER (kW) field for the FISR problem formulation of the dynamic feeder or pre-energized feeder if there is no dynamic feeder assigned. FISR plans will include a step to prevent connection of this energy resource. This field applies to both reclosers and breakers. | Boolean
10479 | DNOM Component | Switch | SWT | input | LOADSHEDACTIVE | Indicates whether the device is currently shed | Boolean
10480 | DNOM Component | Switch | SWT | input | LOADSHEDCLASS | Load shed circuit classification | Integer
10481 | DNOM Component | Switch | SWT | input | LOADSHEDCLASSDESC | Load shed circuit classification description | String
10482 | DNOM Component | Switch | SWT | input | LOADSHEDCLASSREASON | Load shed classification reason | String
10483 | DNOM Component | Switch | SWT | input | LOADSHEDSORTVALUE | Load shed sort rule applied | Integer
10484 | DNOM Component | Switch | SWT | output | ISCOMMAND | Specifies whether the IsCommanded bit is set for the switch, which means that the status change to Open is caused by a known (commanded) operation. | Boolean
10485 | DNOM Component | Switch | SWT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
10486 | DNOM Component | Switch | SWT |  | MANLIM | Flag indicating manual limit | Boolean
10487 | DNOM Component | Switch | SWT | output | MAXCAPRATIOSBOLTED | The ratio of the maximum calculated fault current evaluated with a zero-fault impedance to the maximum interruption current of the switch, in percentage. | Float | PRV | % | %
10488 | DNOM Component | Switch | SWT | output | MAXCAPRATIOSUSERCONFIGURED | The ratio of the maximum calculated fault current evaluated with a user configured fault impedance to the maximum interruption current of the switch, in percentage. | Float | PRV | % | %
10489 | DNOM Component | Switch | SWT | output | MAXFAULTCURRENT | Maximum fault current | Float | PRV | Amps | Amps
10490 | DNOM Component | Switch | SWT | input | MAXINTERRUPT | Maximum interrupting current rating (breakers and reclosers). | Float
10491 | DNOM Component | Switch | SWT | output | MAXINTERRUPTVIOLATION | Flag indicating maximum interruption violation exists for the breaker or recloser. | Boolean | PRV | #N/A | #N/A
10492 | DNOM Component | Switch | SWT | Input | MAXPHANGLEDIFF | Maximum phase angle tolerance for feeder main switch | Float |  | degree | degree
10493 | DNOM Component | Switch | SWT | output | MINGNDPROTDEVCUR | Minimum Ground Fault Current. Calculated minimum ground fault current in amps. This value is calculated by the PRV function. For all devices, single line-to-ground fault current is calculated. | String | PRV | #N/A | #N/A
10494 | DNOM Component | Switch | SWT | output | MINGNDPROTDEVID | Minimum Ground Protective Device ID. The ID of the device that protects the zone from the minimum ground fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String | PRV | #N/A | #N/A
10495 | DNOM Component | Switch | SWT | input | MODEL.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10496 | DNOM Component | Switch | SWT | input | MODEL.ISWITTYPE | Switch Type | Integer
10497 | DNOM Component | Switch | SWT | input | MODEL.ISWTTYPE | Enumerated switch type 1 - OH Single Blade Switch 2 - UG Elbow Switch 3 - Fuse Switch 4 - Jumper 5 - Recloser 6 - Sectionalizer 7 - UG Multi Switch 8 - Automated Field Switch 9 - UG Feeder Switch 11 - Throwover - non Powell ESCO 12 - Throwover - Powell ESCO 13 - 3 Phase TX Switch | Integer |  |  |  | SWMOD
10498 | DNOM Component | Switch | SWT | input | MODEL.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | SWMOD
10499 | DNOM Component | Switch | SWT | input | MODEL.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | SWMOD
10500 | DNOM Component | Switch | SWT | input | MODEL.LIMUNIT | Enumerated limit units (1 = amps, 2 = kVA) | Integer |  |  |  | SWMOD
10501 | DNOM Component | Switch | SWT | input | MODEL.LIMVALUE | The value of the limit (in amps or kVA) | Float |  | Amps or kVA | Amps or kVA | SWMOD
10502 | DNOM Component | Switch | SWT | input | MODEL.NUMLIMIT | The number of operation limits | Integer |  |  |  | SWMOD
10503 | DNOM Component | Switch | SWT | input | MODEL.RECTYPE | Recloser type description. | String
10504 | DNOM Component | Switch | SWT | input | MODEL.SIZE | Size | Float
10505 | DNOM Component | Switch | SWT | input | MODEL.SWCOST | Default cost of performing a switching operation | Float |  | $/operation | $/operation | SWMOD
10506 | DNOM Component | Switch | SWT | output | MINGNDPROTDEVLIMIT | Minimum ground pick-up current limit in amps. | String | PRV | Amps | Amps
10507 | DNOM Component | Switch | SWT | output | MINGNDPROTDEVNAME | Minimum Ground Protective Device Name. The name of the device that protects the zone from the minimum ground fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String | PRV | #N/A | #N/A
10508 | DNOM Component | Switch | SWT | output | MINGROUNDFAULTCURRENT | Minimum ground fault current | Float | PRV | Amps | Amps
10509 | DNOM Component | Switch | SWT | Output | MINGROUNDFAULTLOCATION | The line or distribution transformer id that connected to minimum single phase to ground fault node | String
10510 | DNOM Component | Switch | SWT | output | MINGROUNDFAULTSUBNAME | The owning station name of the ground fault node. | String | DPF | #N/A | #N/A
10511 | DNOM Component | Switch | SWT | output | MINGROUNDFAULTTYPE | Type of minimum ground fault | String | PRV | #N/A | #N/A
10512 | DNOM Component | Switch | SWT | input | MINGROUNDPICKUP | Minimum ground pick up rating. | Float
10513 | DNOM Component | Switch | SWT | output | MINGROUNDPICKUPRATIOSBOLTED | The ratio of the minimum ground pick-up current (multiplied by a safety factor) to the minimum ground fault current evaluated with a zero-fault impedance in percentage. | Float | PRV | percent | percent
10514 | DNOM Component | Switch | SWT | output | MINGROUNDPICKUPRATIOSUSERCONFIGURED | The minimum ground fault current (in Amps) calculated at the furthest downstream (highest impedance) location from the protective device in the protection area evaluated with a user configured fault impedance. | Float | PRV | percent | percent
10515 | DNOM Component | Switch | SWT | output | MINGROUNDPICKUPVIOLATION | Flag indicating minimum ground pick-up violation exists for the breaker or recloser. | Boolean | PRV | #N/A | #N/A
10516 | DNOM Component | Switch | SWT | output | MINPHASEFAULTCURRENT | Minimum phase fault current | Float | PRV | Amps | Amps
10517 | DNOM Component | Switch | SWT | output | MINPHASEFAULTLOCATION | ID of min phase fault node | String | PRV | #N/A | #N/A
10518 | DNOM Component | Switch | SWT | output | MINPHASEFAULTSUBNAME | The owning station name of the phase fault node. | String | DPF | #N/A | #N/A
10519 | DNOM Component | Switch | SWT | input | MINPHASEPICKUP | Minimum phase pick up rating. | Float
10520 | DNOM Component | Switch | SWT | output | MINPHASEPICKUPRATIOSBOLTED | The ratio of the minimum phase pick-up current (multiplied by a safety factor) to the minimum phase fault current evaluated with a zero-fault impedance in percentage. | Float | PRV | percent | percent
10521 | DNOM Component | Switch | SWT | output | MINPHASEPICKUPRATIOSUSERCONFIGURED | The ratio of the minimum phase pick-up current (multiplied by a safety factor) to the minimum phase fault current evaluated with a user configured fault impedance in percentage. | Float | PRV | percent | percent
10522 | DNOM Component | Switch | SWT | output | MINPHASEPICKUPVIOLATION | Flag indicating minimum phase pick-up violation exists for the breaker or recloser. | Boolean | PRV | #N/A | #N/A
10523 | DNOM Component | Switch | SWT | input | OCPROT.CURRSETTING | Number of current setting index | Integer |  |  |  | OCPROT
10524 | DNOM Component | Switch | SWT | input | OCPROT.DEFGRNDTRIP | A flag indicating that the protective ground trip is enabled | Boolean |  |  |  | OCPROT
10525 | DNOM Component | Switch | SWT | input | OCPROT.DEFSETTING | Number of protection setting index | Integer |  |  |  | OCPROT
10526 | DNOM Component | Switch | SWT | input | OCPROT.GRNDTRIPCAP | A flag indicating that the protection is ground trip capable | Boolean |  |  |  | OCPROT
10527 | DNOM Component | Switch | SWT | input | OCPROT.LARGESTFUSE | Largest coordination fuse rating | Float |  |  |  | OCPROT
10528 | DNOM Component | Switch | SWT | input | OCPROT.NOTE | Notes | String |  |  |  | OCPROT
10529 | DNOM Component | Switch | SWT | input | OCPROT.NUMPROTSETTING | Number of protection settings populated | Integer |  |  |  | OCPROT
10530 | DNOM Component | Switch | SWT | input | OCPROT.NUMPROTSOURCES | Number of protection sources populated | Integer |  |  |  | OCPROT
10531 | DNOM Component | Switch | SWT | input | OCPROT.PROTDATA | Protection data source | Enumeration |  |  |  | OCPROT
10532 | DNOM Component | Switch | SWT | input | OCPROT.PROTTYPE | Protection device type | Enumeration |  |  |  | OCPROT
10533 | DNOM Component | Switch | SWT | output | MINPHPROTDEVCUR | Minimum Phase Fault Current. Calculated minimum phase fault current in amps. This field is not applicable for two-phase reclosers, single-phase reclosers, or fuses. | String | PRV | #N/A | #N/A
10534 | DNOM Component | Switch | SWT | output | MINPHPROTDEVID | Minimum Phase Protective Device ID. The ID of the device that protects the zone from the minimum phase fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String | PRV | #N/A | #N/A
10535 | DNOM Component | Switch | SWT | output | MINPHPROTDEVLIMIT | Minimum phase pick-up current limit in amps. This field is only applicable for three-phase devices. | String | PRV | Amps | Amps
10536 | DNOM Component | Switch | SWT | output | MINPHPROTDEVNAME | Minimum Phase Protective Device Name. The name of the device that protects the zone from the minimum phase fault current. If the device at the head of the zone is not able to protect the zone, devices progressively upstream are checked to see if they can perform the necessary protection function. | String | PRV | #N/A | #N/A
10537 | DNOM Component | Switch | SWT | input | MODEL | Pointer to associated the switch model | String
10538 | DNOM Component | Switch | SWT | input | NAME | Object name | String |  |  |  | DNMOBJ
10539 | DNOM Component | Switch | SWT |  | NETWORKLOOPED | Indicates loop conditions | String
10540 | DNOM Component | Switch | SWT | input | NEUTRALCURRENTSAFETYFACTOR | The user-configured safety factor for the neutral current trip setting | Float | PRV
10541 | DNOM Component | Switch | SWT | output | NEUTRALCURRENTVALUE | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
10542 | DNOM Component | Switch | SWT | output | NEUTRALCURRENTVIOLATION | This field is the indicator that the neutral current exceeds the neutral relay current trip setting multiplied by the user-configured safety factor | Boolean | PRV
10543 | DNOM Component | Switch | SWT | input | NEUTRALCURRENTVIOLATIONPERCENT | The neutral current violation percentage | Float | PRV | % | %
10544 | DNOM Component | Switch | SWT | output | NEUTRALCURRENTWITHSAFTEYFACTOR | The neutral current (in Amps) multiplied by a safety factor. | Float | PRV | Amps | Amps
10545 | DNOM Component | Switch | SWT | input | NEUTRALRELAYSETTING | The maximum allowed neutral trip setting (in Amps) for a switching device, which is checked by the protection validation functions | Float | PRV | Amps | Amps
10546 | DNOM Component | Switch | SWT | input | NEUTRALRELAYTRIPCURRENT | This field is the neutral trip setting (in Amps) for a breaker or a recloser which is checked by the protection validation functions | Float | PRV | Amps | Amps
10547 | DNOM Component | Switch | SWT | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10548 | DNOM Component | Switch | SWT | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10549 | DNOM Component | Switch | SWT |  | NOMINALSETTING | Nominal setting | String
10550 | DNOM Component | Switch | SWT | input | NOPEN | Normally Open | Boolean
10551 | DNOM Component | Switch | SWT |  | NORMALSETTINGGROUP | The default settings group | String
10552 | DNOM Component | Switch | SWT |  | NORMALSETTINGGROUPMEASINDEX | The nominal settings group value (index) measurement | Integer
10553 | DNOM Component | Switch | SWT |  | NORMALSETTINGGROUPMEASINDEX | The default settings group value (index) | Integer
10554 | DNOM Component | Switch | SWT | input | NORMOPENPHASES | Normally open phases | String
10555 | DNOM Component | Switch | SWT | input | NORMPOSITION | Normal position. | String
10556 | DNOM Component | Switch | SWT | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10557 | DNOM Component | Switch | SWT |  | OBJGEOMETRYNAMEFAMINGROUND | Geometry name for minimum ground device from latest PRV calculation. | String
10558 | DNOM Component | Switch | SWT |  | OBJGEOMETRYNAMEFAMINPHASE | Geometry name for minimum phase device from latest PRV calculation. | String
10559 | DNOM Component | Switch | SWT |  | OBJGEOMETRYNAMELARGESTVMM | Geometry name for the device connected to the largest voltage mismatch node from the final iteration of the latest DPF solution | String
10560 | DNOM Component | Switch | SWT |  | OBJGEOMETRYNAMEBOUNDEDSELFPROTECTEDTF | Geometry name for self-protected transformer from latest PRV calculation. | String
10561 | DNOM Component | Switch | SWT | input | OCPROT | Pointer for overcurrent protection - fuses and relays | String
10562 | DNOM Component | Switch | SWT |  | OPTMANDSOVISIBLE | Optimization eligibility manual visible | Boolean
10563 | DNOM Component | Switch | SWT | input | OSMDEVTLN | Switch ID used in OSM application | String
10564 | DNOM Component | Switch | SWT |  | PARALLELLOOPED | Indicates parallell conditions | String
10565 | DNOM Component | Switch | SWT | input | PARTOFTEAM | Specifies whether the switch is associated with an automated scheme team | Boolean
10566 | DNOM Component | Switch | SWT | input | PENDPERMNEWSTATENAME | Pending permanent switch nominal status | String
10567 | DNOM Component | Switch | SWT | input | PENDPERMSTATUS | Pending permanent status (true = awaiting permanent status change). | Boolean
10568 | DNOM Component | Switch | SWT | input | PENDPERMSWNAME | Pending permanent switch name | String
10569 | DNOM Component | Switch | SWT | output | PHASEFAULTSENSITIVITYBOLTED | The ratio of the minimum phase fault current evaluated with a user configured fault impedance to the minimum phase pick-up current (multiplied by a safety factor). | Float | PRV | percent | percent
10570 | DNOM Component | Switch | SWT | output | PHASEFAULTSENSITIVITYUSERCONFIGURED | The phase short circuit current (in Amps) calculated for a location immediately downstream of the protective device evaluated with a zero fault impedance. | Float | PRV | percent | percent
10571 | DNOM Component | Switch | SWT | output | PREDICTEDPHASES | Predicted phases | String
10572 | DNOM Component | Switch | SWT | output | PREDICTIONBLOCKED | Indicates if the prediction is blocked | Boolean
10573 | DNOM Component | Switch | SWT | output | PREDICTIONBLOCKEDPHASES | Indicates the phases for which the prediction is blocked | String
10574 | DNOM Component | Switch | SWT | output | PREDICTIONBLOCKINGPERPHASE | Indicates if the prediction is blocked for phases | Boolean
10575 | DNOM Component | Switch | SWT | input | PROHIBITRESTORATIONSTATUS | The Prohibit Restoration measurement status | String
10576 | DNOM Component | Switch | SWT | output | PROTCOORD | Short Circuit Coordination. This field returns a value of Coordinated or Uncoordinated after checking the fault analysis protection coordination calculation. This is an optional study mode only calculation performed within the fault analysis application. | String | PRV | #N/A | #N/A
10577 | DNOM Component | Switch | SWT | output | PROTCOORDUPDEV | Upstream Protection Device. The name of the coordinated upstream protection device. This device can be the further upstream protection device if the device immediately upstream is not coordinated. | String | PRV | #N/A | #N/A
10578 | DNOM Component | Switch | SWT |  | PROTCOORDUPDEVID | ID of the coordinated upstream protection device. This device can be the further upstream protection device if the device immediately upstream is not coordinated. | String
10579 | DNOM Component | Switch | SWT |  | PROTSETTING1 | Protection setting group 1 | String
10580 | DNOM Component | Switch | SWT |  | PROTSETTING10 | Protection setting group 10 | String
10581 | DNOM Component | Switch | SWT |  | PROTSETTING2 | Protection setting group 2 | String
10582 | DNOM Component | Switch | SWT |  | PROTSETTING3 | Protection setting group 3 | String
10583 | DNOM Component | Switch | SWT |  | PROTSETTING4 | Protection setting group 4 | String
10584 | DNOM Component | Switch | SWT |  | PROTSETTING5 | Protection setting group 5 | String
10585 | DNOM Component | Switch | SWT |  | PROTSETTING6 | Protection setting group 6 | String
10586 | DNOM Component | Switch | SWT |  | PROTSETTING7 | Protection setting group 7 | String
10587 | DNOM Component | Switch | SWT |  | PROTSETTING8 | Protection setting group 8 | String
10588 | DNOM Component | Switch | SWT |  | PROTSETTING9 | Protection setting group 9 | String
10589 | DNOM Component | Switch | SWT |  | PROTSOURCES1 | Protection source 1 | String
10590 | DNOM Component | Switch | SWT |  | PROTSOURCES10 | Protection source 10 | String
10591 | DNOM Component | Switch | SWT |  | PROTSOURCES2 | Protection source 2 | String
10592 | DNOM Component | Switch | SWT |  | PROTSOURCES3 | Protection source 3 | String
10593 | DNOM Component | Switch | SWT |  | PROTSOURCES4 | Protection source 4 | String
10594 | DNOM Component | Switch | SWT |  | PROTSOURCES5 | Protection source 5 | String
10595 | DNOM Component | Switch | SWT |  | PROTSOURCES6 | Protection source 6 | String
10596 | DNOM Component | Switch | SWT |  | PROTSOURCES7 | Protection source 7 | String
10597 | DNOM Component | Switch | SWT |  | PROTSOURCES8 | Protection source 8 | String
10598 | DNOM Component | Switch | SWT |  | PROTSOURCES9 | Protection source 9 | String
10599 | DNOM Component | Switch | SWT | output | PROTVALID | Protected or "Unprotected" determined by the protection validation calculation. | String | PRV | #N/A | #N/A
10600 | DNOM Component | Switch | SWT | output | PRVAPPBOUNDARY | This flag helps to know if fuse is a boundary in determining adaptive relaying Protection Validation (PRV) application zone. | Boolean
10601 | DNOM Component | Switch | SWT | input | PRVDEVICETYPE | Returns device type (breaker, recloser, or fuse) along with the relay/breaker type (mechanical, electronic, hydraulic, etc.) | String
10602 | DNOM Component | Switch | SWT | input | PRVSAFETYFACTOR | PRV Safety Factor | String
10603 | DNOM Component | Switch | SWT | input | RECAMPRATING | Recloser's rating amps | Float
10604 | DNOM Component | Switch | SWT | input | RECGRTRIPAMPS | Recloser ground trip setting (amps) multiplied by a safety factor. | Float
10605 | DNOM Component | Switch | SWT | input | RECGRTRIPAMPSNOSF | Ground trip current setting (amps) with no safety factor multiplied. | Float
10606 | DNOM Component | Switch | SWT | input | RECGRTRIPCAPABLE | Flag indicating recloser has ground trip capability. | Boolean
10607 | DNOM Component | Switch | SWT | input | RECGRTRIPSTATUS | Recloser ground trip status. | String
10608 | DNOM Component | Switch | SWT | input | RECINTERRUPTAMPS | Maximum interruption rating (amps). | Float
10609 | DNOM Component | Switch | SWT | input | RECNOMOPMODE | Recloser's nominal operating mode | String
10610 | DNOM Component | Switch | SWT | input | RECPHTRIPAMPS | Recloser phase trip setting (amps) multiplied by a safety factor. | Float
10611 | DNOM Component | Switch | SWT | input | RECPHTRIPAMPSNOSF | Phase trip current setting (amps) with no safety factor multiplied. | Float
10612 | DNOM Component | Switch | SWT | input | RECRECLOSESTATUS | Reclosing Status | String
10613 | DNOM Component | Switch | SWT | input | RECRECLOSEUISTATUS | Reclosing enabled status. | String
10614 | DNOM Component | Switch | SWT | input | RELAYTYPE | The relay type of the switch. | String
10615 | DNOM Component | Switch | SWT | input | REMOTE | Remote | Boolean
10616 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJAVAILCAPAMP1 | Level 1 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
10617 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJAVAILCAPAMP2 | Level 2 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
10618 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJAVAILCAPAMP3 | Level 3 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
10619 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJAVAILCAPAMP4 | Level 4 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
10620 | DNOM Component | Switch | SWT | input | SECONDID.NOAPPSTR | Second ID | String |  |  |  | NDPFST
10621 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJAVAILCAPAMP5 | Level 5 Amp limit minus maximum calculated phase amps adjusted for reserved capacity. | String |  | Amps | Amps
10622 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJFLOWA | Phase A calculated Amps plus reserved capacity on phase A. | String |  | Amps | Amps
10623 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJFLOWB | Phase B calculated Amps plus reserved capacity on phase B. | String |  | Amps | Amps
10624 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJFLOWC | Phase C calculated Amps plus reserved capacity on phase C. | String |  | Amps | Amps
10625 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJLOADING1 | Percentage loading using level 1 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
10626 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJLOADING2 | Percentage loading using level 2 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
10627 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJLOADING3 | Percentage loading using level 3 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
10628 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJLOADING4 | Percentage loading using level 4 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
10629 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYADJLOADING5 | Percentage loading using level 5 Amp limit and maximum calculated phase amps adjusted for reserved capacity. | String |  | % | %
10630 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYAMPA | Reserved capacity on phase A due to reserved capacity objects. | String |  | Amps | Amps
10631 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYAMPB | Reserved capacity on phase B due to reserved capacity objects. | String |  | Amps | Amps
10632 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYAMPC | Reserved capacity on phase C due to reserved capacity objects. | String |  | Amps | Amps
10633 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYDERATEDLIMITLOADING1 | Percentage loading using de-rated level 1 Amp limit and maximum calculated phase amps. | String |  | % | %
10634 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYDERATEDLIMITLOADING2 | Percentage loading using de-rated level 2 Amp limit and maximum calculated phase amps. | String |  | % | %
10635 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYDERATEDLIMITLOADING3 | Percentage loading using de-rated level 3 Amp limit and maximum calculated phase amps. | String |  | % | %
10636 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYDERATEDLIMITLOADING4 | Percentage loading using de-rated level 4 Amp limit and maximum calculated phase amps. | String |  | % | %
10637 | DNOM Component | Switch | SWT |  | RESERVEDCAPACITYDERATEDLIMITLOADING5 | Percentage loading using de-rated level 5 Amp limit and maximum calculated phase amps. | String |  | % | %
10638 | DNOM Component | Switch | SWT | input | RESTORATIONPOINTS | Restoration points | String
10639 | DNOM Component | Switch | SWT | input | REVERSIBLEREC | Flag indicating if recloser is reversible for current flow direction | Boolean
10640 | DNOM Component | Switch | SWT | input | SCHEMEID | ID of the automated scheme the switch is associated with | String
10641 | DNOM Component | Switch | SWT | input | SCHEMENAME | Name of the automated scheme the switch is associated with | String
10642 | DNOM Component | Switch | SWT | input | SECONDID | Pointer to a string in a station vector collection | String
10643 | DNOM Component | Switch | SWT | input | SECTIONALIZATIONPOINTS | Sectionalization points | String
10644 | DNOM Component | Switch | SWT |  | SETTINGSGROUPTEMPLATEMEASINDEX | The active settings group template measurement | String
10645 | DNOM Component | Switch | SWT | input | SGALLTEMPLATENAMES | The list of available settings group templates. Applies to reclosers only. | String
10646 | DNOM Component | Switch | SWT | input | SGDEFAULTTEMPLATENAME | The name of the default settings group template. Applies to reclosers only. | String
10647 | DNOM Component | Switch | SWT | Input | SGNOTES | The notes of protection settings group | String
10648 | DNOM Component | Switch | SWT | Input | SGNUM | The number of limits in protection settings group | Integer
10649 | DNOM Component | Switch | SWT | Input | SGSETTINGS | The station, feeder, setting of protection setting in protection settings group | String
10650 | DNOM Component | Switch | SWT | input | SGTEMPLATENAME | The name of the nominal settings group template. Applies to reclosers only. | String
10651 | DNOM Component | Switch | SWT | input | SOLIDBLADEFUSE | Flag indicating if device is a solid blade fuse | Boolean
10652 | DNOM Component | Switch | SWT |  | STATIONBOUNDARY | A flag indicating that the switch is a station boundary device | Boolean
10653 | DNOM Component | Switch | SWT | input | SWCLOSEDPHASES | Switch's phases in "Closed" state | String
10654 | DNOM Component | Switch | SWT | input | SWCURRENTPOSITION | Current position. | String
10655 | DNOM Component | Switch | SWT | input | SWDERATEDLIM1 | Switch derated limit 1 | String |  | Amps | Amps
10656 | DNOM Component | Switch | SWT | input | SWDERATEDLIM2 | Switch derated limit 2 | String |  | Amps | Amps
10657 | DNOM Component | Switch | SWT | input | SWDERATEDLIM3 | Switch derated limit 3 | String |  | Amps | Amps
10658 | DNOM Component | Switch | SWT | input | SWDERATEDLIM4 | Switch derated limit 4 | String |  | Amps | Amps
10659 | DNOM Component | Switch | SWT | input | SWDERATEDLIM5 | Switch derated limit 5 | String |  | Amps | Amps
10660 | DNOM Component | Switch | SWT | input | SWHASMANFLOWLIM | Flag indicating having manual entry flow limit | Boolean
10661 | DNOM Component | Switch | SWT | input | SWHASMANLDBRKCAP | Flag indicating having manual entry load break capability | Boolean
10662 | DNOM Component | Switch | SWT | input | SWHASMANLDBRKRAT | Flag indicating having manual entry load break rating | Boolean
10663 | DNOM Component | Switch | SWT | Input | SWHASMANUALENTRY | Flag indicating the switch has manual entry | Boolean
10664 | DNOM Component | Switch | SWT | input | SWITCHCUSTCNT | Customer count, number of energized downstream customers. | Integer
10665 | DNOM Component | Switch | SWT | input | SWITCHMODPHA | Get the phase A's switch model name | String
10666 | DNOM Component | Switch | SWT | input | SWITCHMODPHB | Get the phase B's switch model name | String
10667 | DNOM Component | Switch | SWT | input | SWITCHMODPHC | Get the phase C's switch model name | String
10668 | DNOM Component | Switch | SWT | input | SWITCHNOMINAL | Switch nominal status | String
10669 | DNOM Component | Switch | SWT | input | SWITCHPHASEIND | Switch phase indication (True/False) | Boolean
10670 | DNOM Component | Switch | SWT | input | SWITCHSINGLEPHASE | Switch is a single-phase device (True/False) | Boolean
10671 | DNOM Component | Switch | SWT | input | SWITCHSIZE | Switch size (from associated model). | Float
10672 | DNOM Component | Switch | SWT | Input | SWITCHTYPE | switch type enumeration description of associated switch model for the switch | String
10673 | DNOM Component | Switch | SWT | input | SWLIM1 | Level 1 limit nominal value (used by limit monitor function). | Float
10674 | DNOM Component | Switch | SWT | input | SWLIM1NAME | Level 1 limit name. | String
10675 | DNOM Component | Switch | SWT | Input | SWLIM1SEASON | Level 1 limit information under current season of associated switch model of the switch. | String
10676 | DNOM Component | Switch | SWT | input | SWLIM2 | Level 2 limit nominal value (used by limit monitor function). | Float
10677 | DNOM Component | Switch | SWT | input | SWLIM2NAME | Level 2 limit name. | String
10678 | DNOM Component | Switch | SWT | Input | SWLIM2SEASON | Level 2 limit information under current season of associated switch model of the switch. | String
10679 | DNOM Component | Switch | SWT | input | SWLIM3 | Level 3 limit nominal value (used by limit monitor function). | Float
10680 | DNOM Component | Switch | SWT | input | SWLIM3NAME | Level 3 limit name. | String
10681 | DNOM Component | Switch | SWT | Input | SWLIM3SEASON | Level 3 limit information under current season of associated switch model of the switch. | String
10682 | DNOM Component | Switch | SWT | input | SWLIM4 | Level 4 limit nominal value (used by limit monitor function). | Float
10683 | DNOM Component | Switch | SWT | input | SWLIM4NAME | Level 4 limit name. | String
10684 | DNOM Component | Switch | SWT | Input | SWLIM4SEASON | Level 4 limit information under current season of associated switch model of the switch. | String
10685 | DNOM Component | Switch | SWT | input | SWLIM5 | Level 5 limit nominal value (used by limit monitor function). | Float
10686 | DNOM Component | Switch | SWT | input | SWPLACE.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer | N/A | N/A |  | PLACE
10687 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
10688 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
10689 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
10690 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
10691 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
10692 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
10693 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
10694 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
10695 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
10696 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
10697 | DNOM Component | Switch | SWT | input | SWPLACE.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
10698 | DNOM Component | Switch | SWT | input | SWPLACE.GSCOMPALTNAME | Alternate name of the component | String | N/A | N/A | Client | PLACE
10699 | DNOM Component | Switch | SWT | input | SWPLACE.GSCOMPGEOMNAME | Name of the geometry | String | N/A | N/A | Client | PLACE
10700 | DNOM Component | Switch | SWT | input | SWPLACE.GSCOMPID | ID of the component | String | N/A | N/A | Client | PLACE
10701 | DNOM Component | Switch | SWT | input | SWPLACE.GSCOMPNAME | Name of the component | String | N/A | N/A | Client | PLACE
10702 | DNOM Component | Switch | SWT | input | SWPLACE.GSSTATIONNAME | Name of the substation | String | N/A | N/A | Client | PLACE
10703 | DNOM Component | Switch | SWT | input | SWPLACE.ROTATION | Rotation anagle of the placement | String |  | degrees | degrees | PTPLCE
10704 | DNOM Component | Switch | SWT | input | SWPLACE.SIZE | Size of the object | String |  |  |  | PTPLCE
10705 | DNOM Component | Switch | SWT | input | SWPLACE.X | X coordinate of the placement | String |  |  |  | PTPLCE
10706 | DNOM Component | Switch | SWT | input | SWPLACE.Y | Y coordinate of the placement | String |  |  |  | PTPLCE
10707 | DNOM Component | Switch | SWT | input | SWLIM5NAME | Level 5 limit name. | String
10708 | DNOM Component | Switch | SWT | Input | SWLIM5SEASON | Level 5 limit information under current season of associated switch model of the switch. | String
10709 | DNOM Component | Switch | SWT | Input | SWLOADBRKCAPNOM | Flag indicating the switch has nominal load break capability | Boolean
10710 | DNOM Component | Switch | SWT | input | SWLOADBRKRATING | Load Break Rating | Float
10711 | DNOM Component | Switch | SWT | Input | SWLOADBRKRATINGNOM | nominal load break rating (amps per phase) | Float
10712 | DNOM Component | Switch | SWT | input | SWMANDSO | Flag indicting if the switch is optimization enabled | Boolean
10713 | DNOM Component | Switch | SWT | input | SWMANFLOWLIM | Manual entry flow limit | Float
10714 | DNOM Component | Switch | SWT | Input | SWMANLDBRKCAPABLE | Flag indicating if the switch has manual entry load break capability. | Boolean
10715 | DNOM Component | Switch | SWT | input | SWMANLDBRKRAT | Manual entry load break rating (amps per phase) | Float
10716 | DNOM Component | Switch | SWT | input | SWMASK | Switch attribute mask | Integer
10717 | DNOM Component | Switch | SWT | input | SWMASK2 | Switch attribute mask | Integer
10718 | DNOM Component | Switch | SWT |  | SWMASKD | Switch attribute mask | Integer
10719 | DNOM Component | Switch | SWT | Input | SWNOMLIM1 | Level 1 nominal limit information under current season of associated switch model of the switch. | String
10720 | DNOM Component | Switch | SWT | input | SWOPENPHASEA | Indicates if phase A is open | Boolean
10721 | DNOM Component | Switch | SWT | input | SWOPENPHASEB | Indicates if phase B is open | Boolean
10722 | DNOM Component | Switch | SWT | input | SWOPENPHASEC | Indicates if phase C is open | Boolean
10723 | DNOM Component | Switch | SWT | input | SWOPENPHASES | Switch's phases in "Open" state | String
10724 | DNOM Component | Switch | SWT | Input | SWOSWTINFOMASK | Additional bits for related phase independent statuses | Integer
10725 | DNOM Component | Switch | SWT | input | SWPLACE | Pointer to the associated switch placement | String
10726 | DNOM Component | Switch | SWT |  | SWAFRSTATUSDADISABLEDDEVICE | ID of upstream switch with DA status disabled (if any) causing this switch to be ineligible for AFR | String
10727 | DNOM Component | Switch | SWT | input | SWSGMANDSO | Flag indicting if the switch settings group change is optimization enabled | Boolean
10728 | DNOM Component | Switch | SWT |  | SWFISRSTATUSDADISABLEDDEVICE | ID of upstream switch with DA status disabled (if any) causing this switch to be ineligible for FISR | String
10729 | DNOM Component | Switch | SWT | input | SWSTATUS | The switch status. Deenergized, Open, Looped, Paralleled, Closed. | String
10730 | DNOM Component | Switch | SWT | input | SWOPERATIONMODE | The current operation mode of the recloser (Switch, Recloser, or Sectionalizer). | String
10731 | DNOM Component | Switch | SWT | input | SWSTRINGTYPE | The switch device type | String
10732 | DNOM Component | Switch | SWT | input | SWTABNORMAL | Phases Abnormally Energized | Integer
10733 | DNOM Component | Switch | SWT |  | SWTALARMSTATUS | Alarm status measurement | String
10734 | DNOM Component | Switch | SWT |  | SWTAUTOMANUAL | Auto/Manual status measurement. Deprecated. Use SWTAUTOMANUALSTATUS instead. | String
10735 | DNOM Component | Switch | SWT |  | SWTAUTOMANUALSTATUS | Auto/Manual status measurement. Queries directly from the SCADA measurement information. | String
10736 | DNOM Component | Switch | SWT |  | SWTAUTORECLSTATUS | Automatic reclosing status measurement | String
10737 | DNOM Component | Switch | SWT | input | SWTAUTOSCH | Flag indicting if the auto scheme is enabled. | Boolean
10738 | DNOM Component | Switch | SWT | input | SWTCLPUGRADE | Switch cold load pickup grade | String
10739 | DNOM Component | Switch | SWT |  | SWTCURPOSSTATUS | Current switch state measurement | String
10740 | DNOM Component | Switch | SWT |  | SWTCURPOSSTATUSMEASID | ID of the switch status measurement point | String
10741 | DNOM Component | Switch | SWT | input | SWTDEVICEFAIL | Flag indicting if the switch is set as failure for all phases in SCADA. | Boolean
10742 | DNOM Component | Switch | SWT | input | SWTDSOSCADA | Flag indicting switch is currently DSO SCADA decides | Boolean
10743 | DNOM Component | Switch | SWT | input | SWTDSOUSEROFF | Flag indicting switch is currently DSO user disabled | Boolean
10744 | DNOM Component | Switch | SWT | input | SWTDSOUSERON | Flag indicting switch is currently DSO user enabled | Boolean
10745 | DNOM Component | Switch | SWT | output | SWTFLOWIMBLIMITPERCENT | Get flow imbalance limit percent value by method 1 (with safety factor) | Float | DPF | percent | percent
10746 | DNOM Component | Switch | SWT | output | SWTFLOWIMBLIMITPERCENT2 | Flow imbalance limit percent value by method 2 | Float | DPF | percent | percent
10747 | DNOM Component | Switch | SWT | output | SWTFLOWIMBLIMITVALUE | Flow imbalance limit value | Float | DPF | Amps | Amps
10748 | DNOM Component | Switch | SWT | output | SWTFLOWIMBVALUE | Get flow imbalance value by method 1 (with safety factor) | Float | DPF | Amps | Amps
10749 | DNOM Component | Switch | SWT | output | SWTFLOWIMBVALUE2 | Get flow imbalance value by method 2 | Float | DPF | Amps | Amps
10750 | DNOM Component | Switch | SWT | Output | SWTFRPHANGLEA | Phase A voltage angle of from node | Float |  | degree | degree
10751 | DNOM Component | Switch | SWT | Output | SWTFRPHANGLEB | Phase B voltage angle of from node | Float |  | degree | degree
10752 | DNOM Component | Switch | SWT | Output | SWTFRPHANGLEC | Phase C voltage angle of from node | Float |  | degree | degree
10753 | DNOM Component | Switch | SWT | input | SWTFUTURE | Future (not constructed) phases. | String
10754 | DNOM Component | Switch | SWT | output | SWTHASFLOWIMBLVIOLATION | Flag indicting the switch has flow imbalance violation by method 1 (with safety factor) | Boolean | DPF | #N/A | #N/A
10755 | DNOM Component | Switch | SWT | output | SWTHASFLOWIMBLVIOLATION2 | Flag indicting the switch has flow imbalance violation by method 2 | Boolean | DPF | #N/A | #N/A
10756 | DNOM Component | Switch | SWT |  | SWTHOTLINETAGSTATUS | Hot line tag status measurement | String
10757 | DNOM Component | Switch | SWT | output | SWTIDSOFSCHEME | The list of switch IDs that are associated with automated scheme teams that the switch is associated with | String
10758 | DNOM Component | Switch | SWT | Input | SWTLOCKOUT | Flag indicating the switch is lockout | Boolean
10759 | DNOM Component | Switch | SWT |  | SWTLOCKOUTSTATUS | Lockout status measurement | String
10760 | DNOM Component | Switch | SWT | input | SWTLOOPED | Phases currently in a loop. | String
10761 | DNOM Component | Switch | SWT | input | SWTMANSCADADSO | Flag indicting if the switch is currently DSO SCADA decides | Boolean
10762 | DNOM Component | Switch | SWT | Input | SWTMANUSERDSODISABLED | Flag indicating if the switch is currently DSO user disabled | Boolean
10763 | DNOM Component | Switch | SWT | input | SWTMANUSERDSOENABLED | Flag indicating if the switch is currently DSO user enabled | Boolean
10764 | DNOM Component | Switch | SWT | input | SWTNEUTRALCURRENTVIOLATIONSORT | The highest neutral current violation percentage | Float | PRV | % | %
10765 | DNOM Component | Switch | SWT | Output | SWTPHANGLEADIFF | Phase A voltage angle difference between from node and to node | Float |  | degree | degree
10766 | DNOM Component | Switch | SWT | Output | SWTPHANGLEBDIFF | Phase B voltage angle difference between from node and to node | Float |  | degree | degree
10767 | DNOM Component | Switch | SWT | Output | SWTPHANGLECDIFF | Phase C voltage angle difference between from node and to node | Float |  | degree | degree
10768 | DNOM Component | Switch | SWT | input | SWTPREVENTCLOSE | Flag indicting if the switch is in Block Close mode. In this mode, switch can not be closed. | Boolean
10769 | DNOM Component | Switch | SWT | input | SWTRECLOSERACTIVEOPMODESTATUS | Specifies whether the switch is working in the recloser operation mode | Boolean
10770 | DNOM Component | Switch | SWT |  | SWTRECLOSEROPMODESTATUS | Recloser mode status measurement | String
10771 | DNOM Component | Switch | SWT |  | SWTREMOTECONTROLSTATUS | Remote control status measurement | String
10772 | DNOM Component | Switch | SWT | input | SWTREMOTECTRL | Flag indicates whether the switch is remotely controlled. | Boolean
10773 | DNOM Component | Switch | SWT | input | SWTSCADADSO | Flag indicting if the switch is currently DSO SCADA decides | Boolean
10774 | DNOM Component | Switch | SWT | input | SWTSCUTOUT | Flag indicting if the switch is in Supervisory Cutout mode. In this mode, switch is not controllable by the operator but it can be manually operated in the field. | Boolean
10775 | DNOM Component | Switch | SWT |  | SWTSUPERVISORYCUTOUTSTATUS | Supervisory cutout status measurement | String
10776 | DNOM Component | Switch | SWT | Output | SWTTOPHANGLEA | Phase A voltage angle of to node | Float |  | degree | degree
10777 | DNOM Component | Switch | SWT | Output | SWTTOPHANGLEB | Phase B voltage angle of to node | Float |  | degree | degree
10778 | DNOM Component | Switch | SWT | Output | SWTTOPHANGLEC | Phase C voltage angle of to node | Float |  | degree | degree
10779 | DNOM Component | Switch | SWT | Input | SWTTYPECODE | Switch device type enumeration | Integer
10780 | DNOM Component | Switch | SWT | Input | SWTUSERDSODISABLED | Flag indicating if the switch is currently DSO user disabled | Boolean
10781 | DNOM Component | Switch | SWT | input | SWTUSERDSOENABLED | Flag indicating if the switch is currently DSO user enabled | Boolean
10782 | DNOM Component | Switch | SWT | input | TERMFR.PHASING.PHASES | Phases flag of “from” terminal Phase A = 1, Phase B = 2, Phase C = 4, Phase N = 8 | Integer
10783 | DNOM Component | Switch | SWT | input | TERMTO.PHASING.PHASES | Phases flag of "to" terminal | Integer
10784 | DNOM Component | Switch | SWT | Output | TCAMPS1A | Phase A amps of Feeder 1 of TC solution for the switch | Float
10785 | DNOM Component | Switch | SWT | Output | TCAMPS1B | Phase B amps of Feeder 1 of TC solution for the switch | Float
10786 | DNOM Component | Switch | SWT | Output | TCAMPS1C | Phase C amps of Feeder 1 of TC solution for the switch | Float
10787 | DNOM Component | Switch | SWT | Output | TCAMPS2A | Phase A amps of Feeder 2 of TC solution for the switch | Float
10788 | DNOM Component | Switch | SWT | Output | TCAMPS2B | Phase B amps of Feeder 2 of TC solution for the switch | Float
10789 | DNOM Component | Switch | SWT | Output | TCAMPS2C | Phase C amps of Feeder 2 of TC solution for the switch | Float
10790 | DNOM Component | Switch | SWT | Input | TCDEVTYPE | Flag indicating the switch has transfer capacity | Boolean
10791 | DNOM Component | Switch | SWT | Output | TCFEEDFROM1 | Feeder name of from node side in TC result | String
10792 | DNOM Component | Switch | SWT | Output | TCFEEDFROM2 | Feeder name of from node side in TC result | String
10793 | DNOM Component | Switch Terminal | SWTERM | input | LINE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10794 | DNOM Component | Switch Terminal | SWTERM | input | LINE.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10795 | DNOM Component | Switch Terminal | SWTERM | input | LINE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10796 | DNOM Component | Switch Terminal | SWTERM | input | LINE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10797 | DNOM Component | Switch Terminal | SWTERM | input | LINE.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10798 | DNOM Component | Switch Terminal | SWTERM | input | LINE.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10799 | DNOM Component | Switch Terminal | SWTERM | input | LINE.LENGTH | Line length | Float |  | Meters | Feet | LN
10800 | DNOM Component | Switch Terminal | SWTERM | input | LINE.NAME | Name of the object | String |  |  |  | DNMOBJ
10801 | DNOM Component | Switch Terminal | SWTERM | input | LINE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10802 | DNOM Component | Switch Terminal | SWTERM | input | LINE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10803 | DNOM Component | Switch Terminal | SWTERM | input | LINE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10804 | DNOM Component | Switch Terminal | SWTERM | input | LINE.NUMFLFAM | Number of fault location analog measurements | String |  |  |  | LN
10805 | DNOM Component | Switch Terminal | SWTERM | input | LINE.PRMFRATE | Permanent failure rate (failures/length-year) | Float |  |  |  | LN
10806 | DNOM Component | Switch Terminal | SWTERM | input | LINE.REPAIRTM | Sustained outage mean time to repair | Float |  | Hours | Hours | LN
10807 | DNOM Component | Switch Terminal | SWTERM | input | LINE.TMPFRATE | Temporary failure rate (failures/length-year) | Float |  |  |  | LN
10808 | DNOM Component | Switch Terminal | SWTERM | input | LINE.ZLENGTH | Impedance for PRV function (in pu) | Float |  |  |  | LN
10809 | DNOM Component | Switch | SWT | Output | TCFEEDTO1 | Feeder name of to node side in TC result | String
10810 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10811 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10812 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
10813 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.CURROPEN | Current open status | Boolean |  |  |  | SWT
10814 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
10815 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10816 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10817 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
10818 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10819 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10820 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.NAME | Name of the object | String |  |  |  | DNMOBJ
10821 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10822 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10823 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.NOPEN | Normally Open | Boolean |  |  |  | SWT
10824 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10825 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.REMOTE | Remote | Boolean |  |  |  | SWT
10826 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
10827 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
10828 | DNOM Component | Switch | SWT | Output | TCFEEDTO2 | Feeder name of to node side in TC result | String
10829 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10830 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.BRCHLIMA | ID of branch with the lowest phase A limit | String |  |  |  | SWSECT
10831 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.BRCHLIMB | ID of branch with the lowest phase B limit | String |  |  |  | SWSECT
10832 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.BRCHLIMC | ID of branch with the lowest phase C limit | String |  |  |  | SWSECT
10833 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10834 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10835 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.ID | Object unique ID | String |  |  |  | DNMOBJ
10836 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.LOWLIMA | Lowest phase A branch flow limit value | Float |  | Amps | Amps | SWSECT
10837 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.LOWLIMB | Lowest phase B branch flow limit value | Float |  | Amps | Amps | SWSECT
10838 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.LOWLIMC | Lowest phase C branch flow limit value | Float |  | Amps | Amps | SWSECT
10839 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NAME | Object name | String |  |  |  | DNMOBJ
10840 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NTPFLAG | NTP flags(e.g. 1 = section is fully energized, 2 = partially energized, 4 = one or more temp grounds) | Integer |  |  |  | SWSECT
10841 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMCRCST | Number of critical customers. | Integer |  |  |  | SWSECT
10842 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMCUST3 | Number of three-phase customers | Integer |  |  |  | SWSECT
10843 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMCUSTA | Number of phase A customers | Integer |  |  |  | SWSECT
10844 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMCUSTB | Number of phase B customers | Integer |  |  |  | SWSECT
10845 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMCUSTC | Number of phase C customers | Integer |  |  |  | SWSECT
10846 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMTF3 | Number of three-phase distribution transformers | Integer |  |  |  | SWSECT
10847 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMTFA | Number of phase A distribution transformers | Integer |  |  |  | SWSECT
10848 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMTFB | Number of phase B distribution transformers | Integer |  |  |  | SWSECT
10849 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT.NUMTFC | Number of phase C distribution transformers | Integer |  |  |  | SWSECT
10850 | DNOM Component | Switch | SWT | Output | TCMARKDEVICES | Two limiting switch Id and owning station name if TC for the switch is solved | String
10851 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10852 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.BRCHLIMA | ID of branch with the lowest phase A limit | String |  |  |  | SWSECT
10853 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.BRCHLIMB | ID of branch with the lowest phase B limit | String |  |  |  | SWSECT
10854 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.BRCHLIMC | ID of branch with the lowest phase C limit | String |  |  |  | SWSECT
10855 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10856 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10857 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.ID | Object unique ID | String |  |  |  | DNMOBJ
10858 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.LOWLIMA | Lowest phase A branch flow limit value | Float |  | Amps | Amps | SWSECT
10859 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.LOWLIMB | Lowest phase B branch flow limit value | Float |  | Amps | Amps | SWSECT
10860 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.LOWLIMC | Lowest phase C branch flow limit value | Float |  | Amps | Amps | SWSECT
10861 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NAME | Object name | String |  |  |  | DNMOBJ
10862 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NTPFLAG | NTP flags(e.g. 1 = section is fully energized, 2 = partially energized, 4 = one or more temp grounds) | Integer |  |  |  | SWSECT
10863 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMCRCST | Number of critical customers. | Integer |  |  |  | SWSECT
10864 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMCUST3 | Number of three-phase customers | Integer |  |  |  | SWSECT
10865 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMCUSTA | Number of phase A customers | Integer |  |  |  | SWSECT
10866 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMCUSTB | Number of phase B customers | Integer |  |  |  | SWSECT
10867 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMCUSTC | Number of phase C customers | Integer |  |  |  | SWSECT
10868 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMTF3 | Number of three-phase distribution transformers | Integer |  |  |  | SWSECT
10869 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMTFA | Number of phase A distribution transformers | Integer |  |  |  | SWSECT
10870 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMTFB | Number of phase B distribution transformers | Integer |  |  |  | SWSECT
10871 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.NUMTFC | Number of phase C distribution transformers | Integer |  |  |  | SWSECT
10872 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT.THATSECT | Pointer to the section on the other side of switch | String
10873 | DNOM Component | Switch | SWT | Output | TCSW1SUBNAME | limiting switch 1 owning station name if TC for the switch is solved | String
10874 | DNOM Component | Switch | SWT | Output | TCSW2SUBNAME | limiting switch 2 owning station name if TC for the switch is solved | String
10875 | DNOM Component | Switch | SWT | Output | TCSWFILTER | Flag indicating a non-zero TC solution exists for the switching device | Boolean
10876 | DNOM Component | Switch | SWT | Output | TCSWITCH1 | limiting switch 1 name if TC for the switch is solved | String
10877 | DNOM Component | Switch | SWT | Output | TCSWITCH2 | limiting switch 2 name if TC for the switch is solved | String
10878 | DNOM Component | Switch | SWT | input | TEAMIDS | IDs of automated scheme teams that the switch is associated with | String
10879 | DNOM Component | Switch | SWT | input | TEAMNAMES | Names of automated scheme teams that the switch is associated with | String
10880 | DNOM Component | Switch | SWT | Input | TESTSWITCHATTRIBUTE | Test attribute value for a switch | String
10881 | DNOM Component | Switch | SWT |  | TOLINEVERTEXSX | X coordinates of the to line vertices | Float
10882 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10883 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
10884 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.CHGNOPEN | Change the normal open status flag | Boolean |  |  |  | SWT
10885 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.CURROPEN | Current open status | Boolean |  |  |  | SWT
10886 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.DEVTYPE | Device type. 1 = Switch 2 = Fuse 3 = Recloser 4 = Breaker 5 = Sectionalizer 6 = Jumper | Integer |  |  |  | SWT
10887 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10888 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10889 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | SWT
10890 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10891 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10892 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.NAME | Name of the object | String |  |  |  | DNMOBJ
10893 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10894 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10895 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.NOPEN | Normally Open | Boolean |  |  |  | SWT
10896 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10897 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.REMOTE | Remote | Boolean |  |  |  | SWT
10898 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.SWMASK | Switch attribute mask | Integer |  |  |  | SWT
10899 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH.SWMASK2 | Switch attribute mask | Integer |  |  |  | SWT
10900 | DNOM Component | Switch | SWT |  | TOLINEVERTEXSY | Y coordinates of the to line vertices | Float
10901 | DNOM Component | Switch | SWT |  | TOPOABNORMAL | Phases abnormally energized | String
10902 | DNOM Component | Switch | SWT |  | TOPOLOOPED | Phases currently in a loop | String
10903 | DNOM Component | Switch | SWT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
10904 | DNOM Component | Switch | SWT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
10905 | DNOM Component | Switch | SWT | output | SWITCHCOMPSWSTATUSNAME | Status name of the associated composite switch | String
10906 | DNOM Component | Switch | SWT | output | SWSPECIFICOPENSTATUS | The switch classification (--. Temporary Open, Bad Open, or Normal Open) | String
10907 | DNOM Component | Switch | SWT | input | FUSEBANK | Specifies whether this is a multi-fuse device | Boolean
10908 | Virtual Object | Switches and Composite Switches | SWTCOMPSW | output | SWTCOMPSWFEEDERNAME1 | The name of the feeder to which the switching device is connected. | String
10909 | Virtual Object | Switches and Composite Switches | SWTCOMPSW | output | SWTCOMPSWSTATIONNAME1 | The name of the station to which the switching device is connected. | String
10910 | DNOM Component | Tag | TAG | input | PTAGTYPE.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10911 | DNOM Component | Tag | TAG | input | PTAGTYPE.BEHAVIOR | Tag type characteristics | Integer |  |  |  | TAGTYPE
10912 | DNOM Component | Tag | TAG | input | PTAGTYPE.COLOR | Tag's color | Integer |  |  |  | TAGTYPE
10913 | DNOM Component | Tag | TAG | input | PTAGTYPE.DESC | Description | Integer |  |  |  | TAGTYPE
10914 | DNOM Component | Tag | TAG | input | PTAGTYPE.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10915 | DNOM Component | Tag | TAG | input | PTAGTYPE.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10916 | DNOM Component | Tag | TAG | input | PTAGTYPE.ID | Object unique ID | String |  |  |  | DNMOBJ
10917 | DNOM Component | Tag | TAG | input | PTAGTYPE.NAME | Object name | String |  |  |  | DNMOBJ
10918 | DNOM Component | Tag | TAG | input | PTAGTYPE.TARGBIT | Target bit | Integer |  |  |  | TAGTYPE
10919 | Virtual Object | Switches and Composite Switches | SWTCOMPSW | output | SWTCOMPSWFEEDERNAME2 | The name of the second feeder to which the switching device is connected. | String
10920 | Virtual Object | Switches and Composite Switches | SWTCOMPSW | output | SWTCOMPSWSTATIONNAME2 | The name of the second station to which the switching device is connected. | String
10921 | DNOM Component | Switch Terminal | SWTERM |  | BTERM | A flag indicating the first terminal of the switch (true = first terminal, false - second terminal) | Boolean
10922 | DNOM Component | Switch Terminal | SWTERM | input | LINE | Pointer to the associated line | String
10923 | DNOM Component | Switch Terminal | SWTERM | input | SWITCH | Pointer to the associated switch | String
10924 | DNOM Component | Switch Terminal | SWTERM | input | THATSECT | Refers to the switchable section for the other side of switch | String
10925 | DNOM Component | Switch Terminal | SWTERM | input | THISSECT | Refers to the switchable section that this terminal belongs to - it is a pointer back to the parent | String
10926 | DNOM Component | Tag | TAG | input | TAGCOMP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10927 | DNOM Component | Tag | TAG | input | TAGCOMP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10928 | DNOM Component | Tag | TAG | input | TAGCOMP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10929 | DNOM Component | Tag | TAG | input | TAGCOMP.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
10930 | DNOM Component | Tag | TAG | input | TAGCOMP.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
10931 | DNOM Component | Tag | TAG | input | TAGCOMP.NAME | Name of the object | String |  |  |  | DNMOBJ
10932 | DNOM Component | Tag | TAG | input | TAGCOMP.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10933 | DNOM Component | Tag | TAG | input | TAGCOMP.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
10934 | DNOM Component | Tag | TAG | input | TAGCOMP.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
10935 | DNOM Component | Switch Output | SWTOUT |  | IFROMA | Phase A current injected at from end of line into the line | Float |  | Amps | Amps
10936 | DNOM Component | Switch Output | SWTOUT |  | IFROMB | Phase B current injected at from end of line into the line | Float |  | Amps | Amps
10937 | DNOM Component | Switch Output | SWTOUT |  | IFROMC | Phase C current injected at from end of line into the line | Float |  | Amps | Amps
10938 | DNOM Component | Switch Output | SWTOUT |  | IFROMN | Phase N current injected at from end of line into the line | Float |  | Amps | Amps
10939 | DNOM Component | Switch Output | SWTOUT | output | NEUCURPERCENT | The neutral current percentage, which is calculated as the neutral current divided by the product of the neutral relay current trip setting and the user-configured safety factor. | Float | PRV | % | %
10940 | DNOM Component | Switch Output | SWTOUT | output | NEUCURVIOL | Specifies whether the neutral current violation exists | Boolean | PRV
10941 | DNOM Component | Switch Output | SWTOUT |  | PQFROMA | Phase A power injected at from end of line into the line | Float |  | kVA | KVA
10942 | DNOM Component | Switch Output | SWTOUT |  | PQFROMB | Phase B power injected at from end of line into the line | Float |  | kVA | KVA
10943 | DNOM Component | Switch Output | SWTOUT |  | PQFROMC | Phase C power injected at from end of line into the line | Float |  | kVA | KVA
10944 | DNOM Component | Switch Output | SWTOUT |  | PQFROMN | Phase N power injected at from end of line into the line | Float |  | kVA | KVA
10945 | DNOM Component Placement | Switch Placement | SWTPLE | input | SWITCH | Pointer to the associated switch | String
10946 | DNOM Component | Tag | TAG | input | AREAIND | Integer (index) into station permission area list. | Integer
10947 | DNOM Component | Tag | TAG | input | COLOR | Tag's color | Integer
10948 | DNOM Component | Tag | TAG | input | COMMENT | The user's comment | String
10949 | DNOM Component | Tag | TAG | input | DEVICEID | Device ID | String
10950 | DNOM Component | Tag | TAG | input | DNOMX | X coordinate | Float
10951 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag. | Pointer to the associated tag | String
10952 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
10953 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.COMMENT | The user's comment | String |  |  |  | TAG
10954 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.DEVICEID | Device ID | String |  |  |  | TAG
10955 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
10956 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
10957 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.ID | ID of the object | String |  |  |  | DNMOBJ
10958 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.NAME | Object name | String |  |  |  | DNMOBJ
10959 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.STAGTYPE | Tag type Id | String |  |  |  | TAG
10960 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.TAGCOLOR | Tag color mask | Integer |  |  |  | TAG
10961 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.TAGGEOM | Placement geometry name | String |  |  |  | TAG
10962 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.TAGTYPEID | Global tagType ID | String |  |  |  | TAG
10963 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.USER | Who placed the tag | String |  |  |  | TAG
10964 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.XCOORD | X coordinate | Float |  |  |  | TAG
10965 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag.YCOORD | Y coordinate | Float |  |  |  | TAG
10966 | DNOM Component | Tag | TAG | input | DNOMY | Y coordinate | Float
10967 | DNOM Component | Tag | TAG | input | ID | Object unique ID | String |  |  |  | DNMOBJ
10968 | DNOM Component | Tag | TAG | input | NAME | Object name | String |  |  |  | DNMOBJ
10969 | DNOM Component | Tag | TAG | input | PLACEDBYUSER | The user who placed the tag | String
10970 | DNOM Component | Tag | TAG | input | PTAGTYPE | Pointer to the associated tag type | String
10971 | DNOM Component | Tag | TAG | input | STAGTYPE | Tag type Id | String
10972 | DNOM Component | Tag | TAG | output | TAGBLKCLOSE | The tag block close status | String
10973 | DNOM Component | Tag | TAG |  | TAGBLKDSOOP | Tag optimization prevented status | Boolean
10974 | DNOM Component | Tag | TAG |  | TAGBLKLDSHED | Tag load shed tripped status | Boolean
10975 | DNOM Component | Tag | TAG | output | TAGBLKOPEN | The tag block open status | String
10976 | DNOM Component | Tag | TAG |  | TAGBLKSETP | Tag setpoint prevented status | Boolean
10977 | DNOM Component | Tag | TAG | input | TAGCOLOR | Tag color mask | Integer
10978 | DNOM Component | Tag | TAG | input | TAGCOMP | Associated component pointer | String
10979 | DNOM Component | Tag | TAG | input | TAGCOMPID | The tag id | String
10980 | DNOM Component | Tag | TAG | input | TAGGEOM | Placement geometry name | String
10981 | DNOM Component | Tag | TAG |  | TAGID | Tag ID | String
10982 | DNOM Component | Tag | TAG |  | TAGLIMITCLOSE | Tag close restricted status | Boolean
10983 | DNOM Component | Tag | TAG |  | TAGLIMITOPEN | Tag open restricted status | Boolean
10984 | DNOM Component | Tag | TAG |  | TAGLIMITSETP | Tag setpoint restricted status | Boolean
10985 | DNOM Component | Tag | TAG | input | TAGSTATIONNAME | The tag station name | String
10986 | DNOM Component | Tag | TAG |  | TAGSUBNAME | Name of the substation the tag belongs to | String
10987 | DNOM Component | Tag | TAG | input | TAGTYPEID | Global tagType ID | String
10988 | DNOM Component | Tag | TAG | input | TAGTYPENAME | The tag type name | String
10989 | DNOM Component | Tag | TAG | input | USER | Who placed the tag | String
10990 | DNOM Component | Tag | TAG | input | X | Geographical coordinate | Float
10991 | DNOM Component | Tag | TAG | input | XCOORD | X coordinate | Float
10992 | DNOM Component | Tag | TAG | input | Y | Geographical coordinate | Float
10993 | DNOM Component | Tag | TAG | input | YCOORD | Y coordinate | Float
10994 | DNOM Component Placement | Tag Placement | TAGPLE | input | pTag | Pointer to the associated splice box | String
10995 | DNOM Component | Tag Type | TAGTYPE |  | BEHAVIOR | Tag type characteristics | Integer
10996 | DNOM Component | Tag Type | TAGTYPE |  | COLOR | Tag color | Integer
10997 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE | Pointer to regulation mode | String |  |  |  | REGMODE
10998 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.DEFREGMODE | Default regulation mode | String |  |  |  | REGMODE
10999 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWAEDREGMETHOD | Forward regulation method | String |  |  |  | REGMODE
11000 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDFLOWTHRESHOLD | Forward regulation flow threshold | String |  |  |  | REGMODE
11001 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDLDCR | The LDC resistance for forward regulation defined in volts | String |  | Volts | Volts | REGMODE
11002 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDLDCX | The LDC reactance for forward regulation defined in volts | String |  | Volts | Volts | REGMODE
11003 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDREGNODESIDE | Forward regulation node side | String |  |  |  | REGMODE
11004 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDVBANDWIDTH | The voltage bandwidth for forward regulation | String |  | Volts | Volts | REGMODE
11005 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDVOLTREDUCCAPABLE | The status of forward voltage reduction capability | Boolean |  |  |  | REGMODE
11006 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDVOLTREDUCVALUE1 | The level 1 voltage reduction value for forward regulation | String |  | Volts | Volts | REGMODE
11007 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDVOLTREDUCVALUE2 | The level 2 voltage reduction value for forward regulation | String |  | Volts | Volts | REGMODE
11008 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FORWARDVOLTREDUCVALUE3 | The level 3 voltage reduction value for forward regulation | String |  | Volts | Volts | REGMODE
11009 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.FOWRARDVOLTAGETARGET | The voltage target for forward regulation | String |  | Volts | Volts | REGMODE
11010 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.ISREACTIVEFLOWSENSE | Can be true or false | Boolean |  |  |  | REGMODE
11011 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.NUMREGMODE | Number of the regulation mode | String |  |  |  | REGMODE
11012 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REGID | Regulation mode ID | String |  |  |  | REGMODE
11013 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFLDCR | The LDC resistance for forward regulation. | String |  |  |  | REGMODE
11014 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFLDCX | The LDC reactance for forward regulation. | String |  |  |  | REGMODE
11015 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFNAME | The name of the forward regulation mode. | String |  |  |  | REGMODE
11016 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFSIDE | The side of the transformer used for forward regulation. | String |  |  |  | REGMODE
11017 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFV1 | The level 1 voltage target for forward regulation. | String |  |  |  | REGMODE
11018 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFV2 | The level 2 voltage target for forward regulation. | String |  |  |  | REGMODE
11019 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFV3 | The level 3 voltage target for forward regulation. | String |  |  |  | REGMODE
11020 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFVBANDWIDTH | The voltage regulation bandwidth for forward regulation. | String |  |  |  | REGMODE
11021 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFVREDCAP | The voltage reduction capability status for forward regulation. | String |  |  |  | REGMODE
11022 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODEFVTARGET | The voltage target for forward regulation. | String |  |  |  | REGMODE
11023 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODENAME | The name of the regulation mode. | String |  |  |  | REGMODE
11024 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERLDCR | The LDC resistance for reverse regulation. | String |  |  |  | REGMODE
11025 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERLDCX | The LDC reactance for reverse regulation. | String |  |  |  | REGMODE
11026 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERNAME | The name of the reverse regulation mode. | String |  |  |  | REGMODE
11027 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERSIDE | The side of the transformer used for reverse regulation. | String |  |  |  | REGMODE
11028 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERV1 | The level 1 voltage target for reverse regulation. | String |  |  |  | REGMODE
11029 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERV2 | The level 2 voltage target for reverse regulation. | String |  |  |  | REGMODE
11030 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERV3 | The level 3 voltage target for reverse regulation. | String |  |  |  | REGMODE
11031 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERVBANDWIDTH | The voltage regulation bandwidth for reverse regulation. | String |  |  |  | REGMODE
11032 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERVREDCAP | The voltage reduction capability status for reverse regulation. | String |  |  |  | REGMODE
11033 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF.REGMODE.REGMODERVTARGET | The voltage target for reverse regulation. | String |  |  |  | REGMODE
11034 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REGNAME | Regulation mode name | String |  |  |  | REGMODE
11035 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REGULATIONMODENAME | Regulation mode name | String |  |  |  | REGMODE
11036 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEFLOWTHRESHOLD | Reverse regulation flow threshold | String |  |  |  | REGMODE
11037 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSELDCR | The LDC resistance for reverse regulation defined in volts | String |  | Volts | Volts | REGMODE
11038 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSELDCX | The LDC reactance for reverse regulation defined in volts | String |  | Volts | Volts | REGMODE
11039 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEREGMETHOD | Reverse regulation method | String |  |  |  | REGMODE
11040 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEREGNODESIDE | Reverse regulation node side | String |  |  |  | REGMODE
11041 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVBANDWIDTH | The voltage bandwidth for reverse regulation | String |  | Volts | Volts | REGMODE
11042 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVOLTAGETARGET | The voltage target for reverse regulation | String |  | Volts | Volts | REGMODE
11043 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVOLTREDUCCAPABLE | The status of reverse voltage reduction capability | Boolean |  |  |  | REGMODE
11044 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVOLTREDUCVALUE1 | The level 1 voltage reduction value for reverse regulation | String |  | Volts | Volts | REGMODE
11045 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVOLTREDUCVALUE2 | The level 2 voltage reduction value for reverse regulation | String |  | Volts | Volts | REGMODE
11046 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.REVERSEVOLTREDUCVALUE3 | The level 3 voltage reduction value for reverse regulation | String |  | Volts | Volts | REGMODE
11047 | DNOM Component | Tap Changer | TAPCHR |  | REGCONTROLDEF.REGMODE.SCADAMEASVALUE | SCADA measurement value | String |  |  |  | REGMODE
11048 | DNOM Component | Tag Type | TAGTYPE |  | DESC | Description | Integer
11049 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
11050 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
11051 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
11052 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
11053 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.ID | ID of the regulation node | String |  |  |  | DNMOBJ
11054 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11055 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11056 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
11057 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE.VOLTCALC | Node mask | Integer |  |  |  | NODE
11058 | DNOM Component | Tag Type | TAGTYPE |  | TARGBIT | Target bit | Integer
11059 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
11060 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
11061 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
11062 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
11063 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
11064 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
11065 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
11066 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
11067 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
11068 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
11069 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
11070 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
11071 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
11072 | DNOM Component | Tap Changer | TAPCHR |  | _KEY | The unique identifier to represent the device. | String
11073 | DNOM Component | Tap Changer | TAPCHR |  | BANDWITH | One sided bandwidth | Integer
11074 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
11075 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
11076 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
11077 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
11078 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.ID | ID of the node | String |  |  |  | DNMOBJ
11079 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11080 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11081 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
11082 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND.VOLTCALC | Node mask | Integer |  |  |  | NODE
11083 | DNOM Component | Tap Changer | TAPCHR |  | CTRATIO | Regulator CT ratio - used to determine the per unit LDC R and X required by the power flow | Float
11084 | DNOM Component | Tap Changer | TAPCHR |  | CTSECAMP | Regulator CT full load secondary amps (used to determine the per unit LDC R and X required by the power flow) | Float
11085 | DNOM Component | Tap Changer | TAPCHR |  | DEVICETYPENAME | Device type name | String
11086 | DNOM Component | Tap Changer | TAPCHR | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
11087 | DNOM Component | Tap Changer | TAPCHR |  | DSOTAPCONTROLENABLED | A flag indicating that the tap changer status is "Enabled" | Boolean
11088 | DNOM Component | Tap Changer | TAPCHR |  | HASMANUALENTRY | Indicates if one or some fields of the tap changer have value override | Boolean
11089 | DNOM Component | Tap Changer | TAPCHR | input | ID | Object unique ID | String |  |  |  | DNMOBJ
11090 | DNOM Component | Tap Changer | TAPCHR |  | LDCCMPRV | Line drop compensation resistance (read in rom file and for display purposes) | Integer |  | Volts | Volts
11091 | DNOM Component | Tap Changer | TAPCHR |  | LDCCMPXV | Line drop compensation reactance (read in rom file and for display purposes) | Integer |  | Volts | Volts
11092 | DNOM Component | Tap Changer | TAPCHR |  | LDCCOMPR | Value for the line drop compensation resistance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms
11093 | DNOM Component | Tap Changer | TAPCHR |  | LDCCOMPX | Value for the line drop compensation reactance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms
11094 | DNOM Component | Tap Changer | TAPCHR |  | MANBANDWITH | Override value of voltage bandwidth | Integer
11095 | DNOM Component | Tap Changer | TAPCHR |  | MANLDCCMPRV | Override value of line drop compensation resistance | Integer
11096 | DNOM Component | Tap Changer | TAPCHR |  | MANLDCCMPXV | Override value of line drop compensation reactance | Integer
11097 | DNOM Component | Tap Changer | TAPCHR |  | MANVTARGET | Override value of target voltage to regulate | Integer
11098 | DNOM Component | Tap Changer | TAPCHR | input | NAME | Object name | String |  |  |  | DNMOBJ
11099 | DNOM Component | Tap Changer | TAPCHR |  | NORMTAP | Normal tap ratio (mainly set for fixed taps) | Integer
11100 | DNOM Component | Tap Changer | TAPCHR |  | NRMTPRAT | Fixed tap ratio value | Float
11101 | DNOM Component | Tap Changer | TAPCHR |  | OPTMANDSOELIGIBLE | DSO eligible state | Integer
11102 | DNOM Component | Tap Changer | TAPCHR | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
11103 | DNOM Component | Tap Changer | TAPCHR |  | PHSENSED | Regulation node phases that are sensed | Integer
11104 | DNOM Component | Tap Changer | TAPCHR |  | PRTAPPOSITION | Primary side tap position | String
11105 | DNOM Component | Tap Changer | TAPCHR |  | PTRATIO | Regulator PT ratio, used to determine the voltage target range (VMax and VMin) | Float
11106 | DNOM Component | Tap Changer | TAPCHR | input | REGCONTROLDEF | Pointer to regulation control definition | String |  |  |  | REGCONTROLDEF
11107 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.ID | Object unique ID | String |  |  |  | DNMOBJ
11108 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.MAXTAP | Maximum tap step (maybe +16) | Integer |  |  |  | TAPMOD
11109 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.MINTAP | Minimum tap step (maybe -16) | Integer |  |  |  | TAPMOD
11110 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.NOMTAP | Nominal tap setting (maybe 0) | Integer |  |  |  | TAPMOD
11111 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.TAPCOST | Relative cost of the tap changing operation | Float |  | $/operation | $/operation | TAPMOD
11112 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.TAPSTEP | Tap increment (percent V) | Float |  |  |  | TAPMOD
11113 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.TMDELAY | Time delay for Initial tap movement (seconds) | Float |  |  |  | TAPMOD
11114 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL.TMDELAYT | Time delay for subsequent tap movements | Float |  | Seconds | Seconds | TAPMOD
11115 | DNOM Component | Tap Changer | TAPCHR | input | REGNODE | Pointer to the associated regulation node | String
11116 | DNOM Component | Tap Changer | TAPCHR | input | REGSCHED | Pointer to the regulation schedule | String
11117 | DNOM Component | Tap Changer | TAPCHR |  | REVREG | Flag indicating that the regulator has reverse regulation capability | Boolean
11118 | DNOM Component | Tap Changer | TAPCHR | input | REVREGND | Pointer to the reverse regulation node (if the regulator has the reverse regulation capability) | String
11119 | DNOM Component | Tap Changer | TAPCHR |  | SCTAPPOSITION | Secondary side tap position | String
11120 | DNOM Component | Tap Changer | TAPCHR |  | STATIONNAME | Name of the substation the tap changer belongs to | String
11121 | DNOM Component | Tap Changer | TAPCHR |  | TAPBLOCKED | Tap changer blocked/unblocked status | Boolean
11122 | DNOM Component | Tap Changer | TAPCHR |  | TAPCNTRL | Tap control mode (0 - No tap control - for fixed tap, 1 - Remote only, 2 - Local only, 3 - Remote and local) | Enumeration
11123 | DNOM Component | Tap Changer | TAPCHR |  | TAPCONTROLMODE | Regulating tap changer control mode | String
11124 | DNOM Component | Tap Changer | TAPCHR |  | TAPCTRLCAPBLMODE | Tap control capability mode No_Control = 0, // tap can not be changed. RaiseLower_Only, // tap can only receive raise/lower control VoltSetpoint_Only, // tap can only receive voltage setting control RaiseLower_VoltSetpoint, // tap can receive both raise/lower control and voltage setting control VoltSettingsGroup // tap can support different (>2) control modes, to be implemented later | Enumeration
11125 | DNOM Component | Tap Changer | TAPCHR |  | TAPCTRLCURRMODE | Tap current control mode None = 0, RaiseLowerTap, VoltSetpoint, VoltSettingGroup1, VoltSettingGroup2 | Enumeration
11126 | DNOM Component | Tap Changer | TAPCHR |  | TAPDSOSCADA | DSO status is "SCADA Decide" (used on the device toolbar) | Boolean
11127 | DNOM Component | Tap Changer | TAPCHR |  | TAPDSOUSEROFF | DSO status is "User Disabled" (used on the device toolbar) | Boolean
11128 | DNOM Component | Tap Changer | TAPCHR |  | TAPDSOUSERON | DSO status is "User Enabled" (used on the device toolbar) | Boolean
11129 | DNOM Component | Tap Changer | TAPCHR |  | TAPEND | Transformer winding with movable tap (0 - Primary, 1 - Secondary, 2 - Tertiary) | Enumeration
11130 | DNOM Component | Tap Changer | TAPCHR | input | TF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11131 | DNOM Component | Tap Changer | TAPCHR | input | TF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
11132 | DNOM Component | Tap Changer | TAPCHR | input | TF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | TF
11133 | DNOM Component | Tap Changer | TAPCHR | input | TF.DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean |  |  |  | TF
11134 | DNOM Component | Tap Changer | TAPCHR | input | TF.DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer |  |  |  | TF
11135 | DNOM Component | Tap Changer | TAPCHR | input | TF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11136 | DNOM Component | Tap Changer | TAPCHR | input | TF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11137 | DNOM Component | Tap Changer | TAPCHR | input | TF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | TF
11138 | DNOM Component | Tap Changer | TAPCHR | input | TF.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | TF
11139 | DNOM Component | Tap Changer | TAPCHR | input | TF.FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float |  |  |  | TF
11140 | DNOM Component | Tap Changer | TAPCHR | input | TF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
11141 | DNOM Component | Tap Changer | TAPCHR | input | TF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | TF
11142 | DNOM Component | Tap Changer | TAPCHR | input | TF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | TF
11143 | DNOM Component | Tap Changer | TAPCHR | input | TF.GROUNDTE | Tertiary grounded flag | Boolean |  |  |  | TF
11144 | DNOM Component | Tap Changer | TAPCHR | input | TF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
11145 | DNOM Component | Tap Changer | TAPCHR | input | TF.LVMPROFORMINDEX | LVM problem formulation index | Integer |  |  |  | TF
11146 | DNOM Component | Tap Changer | TAPCHR | input | TF.MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer |  |  |  | TF
11147 | DNOM Component | Tap Changer | TAPCHR | input | TF.MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  |  |  | TF
11148 | DNOM Component | Tap Changer | TAPCHR | input | TF.NAME | Name of the object | String |  |  |  | DNMOBJ
11149 | DNOM Component | Tap Changer | TAPCHR | input | TF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11150 | DNOM Component | Tap Changer | TAPCHR | input | TF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11151 | DNOM Component | Tap Changer | TAPCHR | input | TF.NOMCCUST | The number of nominally connected customers | Integer |  |  |  | TF
11152 | DNOM Component | Tap Changer | TAPCHR | input | TF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
11153 | DNOM Component | Tap Changer | TAPCHR | input | TF.PRIMGNDR | Primary grounding branch resistance | Float |  | Ohms | Ohms | TF
11154 | DNOM Component | Tap Changer | TAPCHR | input | TF.PRIMGNDX | Primary grounding branch reactance | Float |  | Ohms | Ohms | TF
11155 | DNOM Component | Tap Changer | TAPCHR | input | TF.PRIMWIND | Primary winding connection type | Integer |  |  |  | TF
11156 | DNOM Component | Tap Changer | TAPCHR | input | TF.REGULATIONMARGIN | Regulation margin | Float |  |  |  | TF
11157 | DNOM Component | Tap Changer | TAPCHR | input | TF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | TF
11158 | DNOM Component | Tap Changer | TAPCHR | input | TF.SEC1GNDR | Secondary grounding branch resistance | Float |  | Ohms | Ohms | TF
11159 | DNOM Component | Tap Changer | TAPCHR | input | TF.SEC1GNDX | Secondary grounding branch reactance | Float |  | Ohms | Ohms | TF
11160 | DNOM Component | Tap Changer | TAPCHR | input | TF.SEC2GNDR | Tertiary grounding branch resistance | Float |  | Ohms | Ohms | TF
11161 | DNOM Component | Tap Changer | TAPCHR | input | TF.SEC2GNDX | Tertiary grounding branch reactance | Float |  | Ohms | Ohms | TF
11162 | DNOM Component | Tap Changer | TAPCHR | input | TF.SECWIND | Secondary winding connection type | Integer |  |  |  | TF
11163 | DNOM Component | Tap Changer | TAPCHR | input | TF.TERTWIND | Tertiary winding connection type | Integer |  |  |  | TF
11164 | DNOM Component | Tap Changer | TAPCHR | input | TF.TFLOADED | Connected load flag | Boolean |  |  |  | TF
11165 | DNOM Component | Tap Changer | TAPCHR | input | TF.TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean |  |  |  | TF
11166 | DNOM Component | Tap Changer | TAPCHR | input | TF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | TF
11167 | DNOM Component | Tap Changer | TAPCHR | input | TF.VOLTPR | Primary voltage (kV line to ground) | Float |  | kV | kV | TF
11168 | DNOM Component | Tap Changer | TAPCHR | input | TF.VOLTSC | Secondary voltage (kV line to ground) | Float |  | kV | kV | TF
11169 | DNOM Component | Tap Changer | TAPCHR | input | TF.VOLTTE | Tertiary voltage (kV line to ground) | Float |  | kV | kV | TF
11170 | DNOM Component | Tap Changer | TAPCHR |  | TAPHASLOCAL | Flag indicating tap changer has local control capability | Boolean
11171 | DNOM Component | Tap Changer | TAPCHR |  | TAPHASREMOTE | Flag indicating rap changer has remote control capability | Boolean
11172 | DNOM Component | Tap Changer | TAPCHR |  | TAPINIT | Initial tap position | Integer
11173 | DNOM Component | Tap Changer | TAPCHR |  | TAPLDCRMANOVER | Flag indicating the nominal line drop compensation resistance override | Boolean
11174 | DNOM Component | Tap Changer | TAPCHR |  | TAPLDCXMANOVER | Flag indicating the nominal line drop compensation reactance override | Boolean
11175 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANBLOCKED | Manually entered blocked/unblocked status | Boolean
11176 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANSCADADSO | Flag indicating that the tap changer DSO status is manually set to "SCADA Decide" | Boolean
11177 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANTAPCOSTOPT | Override value of scale cost for tap move | Integer
11178 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANUSERDSODISABLED | Manually set "User Disabled" status | Boolean
11179 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANUSERDSOENABLED | Manually set "User Enabled" status | Boolean
11180 | DNOM Component | Tap Changer | TAPCHR |  | TAPMANVREDCTON | Manually entered voltage reduction enabled status | Boolean
11181 | DNOM Component | Tap Changer | TAPCHR |  | TAPMODE | Tap changer regulation mode (0 - No_Tap, 1 - Fixed, 2 - VoltageRegulation, 3 - VarRegulation) | Enumeration
11182 | DNOM Component | Tap Changer | TAPCHR | input | TAPMODEL | Pointer to associated tap changer model | String
11183 | DNOM Component | Tap Changer | TAPCHR |  | TAPNOM | Nominal tap ratio (deterned as terminal voltage divided by the internal transformer voltage) | Float
11184 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.ID | ID of the schedule | String |  |  |  | DNMOBJ
11185 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
11186 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
11187 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
11188 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
11189 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
11190 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
11191 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
11192 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
11193 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
11194 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
11195 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.YUNITONE | Y1 axis units | String |  |  |  | SCHED
11196 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
11197 | DNOM Component | Tap Changer | TAPCHR |  | TAPREDVALMANENABLE | A flag indicating a voltage reduction override is enabled | Boolean
11198 | DNOM Component | Tap Changer | TAPCHR |  | TAPREGULATIONON | Indicates if the tap changer regulation is enabled | Boolean
11199 | DNOM Component | Tap Changer | TAPCHR |  | TAPSCADADSO | Flag indicating that the tap changer DSO status is "SCADA Decide" | Boolean
11200 | DNOM Component | Tap Changer | TAPCHR |  | TAPSTEP | Final (resulting) tap position | Integer
11201 | DNOM Component | Tap Changer | TAPCHR |  | TAPSUBNAME | Substation name | String
11202 | DNOM Component | Tap Changer | TAPCHR |  | TAPTAPCOSTOPTMANENABLE | A flag indicating the scale cost for tap move override | Boolean
11203 | DNOM Component | Tap Changer | TAPCHR |  | TAPTFNAME | Name of the transformer the tap changer belongs to | String
11204 | DNOM Component | Tap Changer | TAPCHR |  | TAPUSERDSODISABLED | DSO status is "User Disabled" | Boolean
11205 | DNOM Component | Tap Changer | TAPCHR |  | TAPUSERDSOENABLED | DSO status is "User Enabled" | Boolean
11206 | DNOM Component | Tap Changer | TAPCHR |  | TAPVBWMANENABLE | Flag indicating the voltage bandwidth override | Boolean
11207 | DNOM Component | Tap Changer | TAPCHR |  | TAPVREDUCTCAPABLE | Determines if the regulating tap changer supports voltage reduction | Boolean
11208 | DNOM Component | Tap Changer | TAPCHR |  | TAPVTGMANENABLE | Flag indicating the voltage target override | Boolean
11209 | DNOM Component | Tap Changer | TAPCHR |  | TETAPPOSITION | Tertiary side tap position | String
11210 | DNOM Component | Tap Changer | TAPCHR | input | TF | Pointer to the transformer that owns the tap changer | String
11211 | DNOM Component | Tap Changer | TAPCHR | input | TFTIMELASTOPERATE | Date and time of the last operation | String
11212 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11213 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11214 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11215 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
11216 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.NAME | Name of the object | String |  |  |  | DNMOBJ
11217 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK.NUMTF | The number of single-phase transformers in the bank. | Integer |  |  |  | TFBNK
11218 | DNOM Component | Tap Changer | TAPCHR | input | TFTIMELASTOPERATE_TICKS | Date and time of the last operation in ticks | String
11219 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket. | Pointer to associated trouble ticket | String
11220 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11221 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.DEVICEID | Associated suspect device ID. | String |  |  |  | TTK
11222 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11223 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11224 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.FSTSTAGE | First stage device | String |  |  |  | TTK
11225 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.ID | ID of the object | String |  |  |  | DNMOBJ
11226 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.NAME | Object name | String |  |  |  | DNMOBJ
11227 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.STATUS | Ticket status. | String |  |  |  | TTK
11228 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.TICKTYPE | Ticket Type | String |  |  |  | TTK
11229 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.X | X Coordinate | Float |  |  |  | TTK
11230 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket.Y | Y Coordinate | Float |  |  |  | TTK
11231 | DNOM Component | Tap Changer | TAPCHR |  | VOLTREDSTEP | Current voltage reduction step (1-3) | Integer
11232 | DNOM Component | Tap Changer | TAPCHR |  | VREDBLK | A flag indicating that the tap has one step voltage reduction and blocking capability | Boolean
11233 | DNOM Component | Tap Changer | TAPCHR |  | VREDPU | Voltage reduction value. The voltage target range is shifted down by this value when the voltage reduction is enabled. | Float |  | p.u. | p.u.
11234 | DNOM Component | Tap Changer | TAPCHR |  | VREDVAL | - | -
11235 | DNOM Component | Tap Changer | TAPCHR |  | VREDVALNOM | The amount of voltage reduction - when enabled | Integer
11236 | DNOM Component | Tap Changer | TAPCHR |  | VSETPNTDEADBAND | The minimum voltage setpoint change needed in a LVM plan | Integer
11237 | DNOM Component | Tap Changer | TAPCHR |  | VSETPNTRANGEMAX | Maximum allowed voltage setpoint value | Integer
11238 | DNOM Component | Tap Changer | TAPCHR |  | VSETPNTRANGEMIN | Minimum allowed voltage setpoint value | Integer
11239 | DNOM Component | Tap Changer | TAPCHR |  | VREGLINELINE | Specifies whether the regulators are connected in delta configuration (line-to-line) | Boolean
11240 | DNOM Component | Tap Changer | TAPCHR |  | VTARGET | Target voltage to regulate | Float
11241 | DNOM Component | Tap Changer | TAPCHR |  | VTARGMAX | Maximum voltage target to regulate | Float |  | p.u. | p.u.
11242 | DNOM Component | Tap Changer | TAPCHR |  | VTARGMIN | Minimum voltage target to regulate | Float |  | p.u. | p.u.
11243 | DNOM Component Placement | Tap Changer | TAPCHR |  | MANUALEXCLUSIONFLAG | Flag indicating that the device is manually excluded for LVM | Boolean
11244 | Global Object | Tap Changer Model | TAPMOD | input | CSTSCHED | The name of a tap changer cost schedule. This schedule can be used to bias the operating range of a regulator or TCUL. This field is optional. | String
11245 | Global Object | Tap Changer Model | TAPMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
11246 | Global Object | Tap Changer Model | TAPMOD |  | MAXTAP | Maximum tap step (maybe +16). | Integer
11247 | Global Object | Tap Changer Model | TAPMOD | input | MAXVOLTRED | Maximum voltage reduction percent for voltage reduction steps 1-3, and for advanced regulation, manual and SCADA overrides. | String |  | % | %
11248 | Global Object | Tap Changer Model | TAPMOD |  | MINTAP | Minimum tap step (maybe -16). | Integer
11249 | Global Object | Tap Changer Model | TAPMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
11250 | Global Object | Tap Changer Model | TAPMOD |  | NOMTAP | Nominal tap setting (maybe 0). | Integer
11251 | Global Object | Tap Changer Model | TAPMOD |  | TAPCOST | Relative cost of the tap changing operation ($/operation). | Float
11252 | Global Object | Tap Changer Model | TAPMOD |  | TAPSTEP | Tap increment (percent V). | Float
11253 | Global Object | Tap Changer Model | TAPMOD |  | TMDELAY | Time delay for Initial tap movement (seconds). | Float
11254 | Global Object | Tap Changer Model | TAPMOD |  | TMDELAYT | Time delay for subsequent tap movements (seconds). | Float
11255 | DNOM Component | Terminal | TERM |  | PHASING. | Enumeration of external phasing at this terminal. These are the phases that could be connected. 0 – none, 1 - PhaseA, 2 - PhaseB, 4 - PhaseC, 8 - PhaseN, 16 - PhaseAxB, 32 - PhaseAxC, 64 - PhaseAxN, 128 - PhaseBxA, 256 - PhaseBxC, 512 - PhaseBxN, 1024 - PhaseCxA, 2048 - PhaseCxB, 4096 - PhaseCxN, 8192 - PhaseNxA, 16384 - PhaseNxB, 32768 - PhaseNxC/ | Enumeration
11256 | Global Object | Tap Changer Model | TAPMOD | input | VOLTRED1 | Voltage reduction percent for step 1 (if 1 or more steps supported) | String |  | % | %
11257 | Global Object | Tap Changer Model | TAPMOD | input | VOLTRED2 | Voltage reduction percent for step 2 (if 2 or more steps supported) | String |  | % | %
11258 | DNOM Component | Transformer | TF | input | ADDRESS.NOAPPSTR | Transformer address. | String
11259 | Global Object | Tap Changer Model | TAPMOD | input | VOLTRED3 | Voltage reduction percent for step 3 (if 3 or more steps supported) | String |  | % | %
11260 | Global Object | Tap Changer Model | TAPMOD | input | VOLTREDSTEPS | The number of voltage reduction steps supported. 0 = no voltage reduction capability. 1-3 = number of steps used by controller | String
11261 | DNOM Component Placement | Transformer Bank Label Placement | TBLBPL | input | TFBANK | Pointer to the associated transformer bank | String
11262 | DNOM Component Placement | Trouble Ticket Placement | TCKPLE | input | pTicket | Pointer to the associated trouble ticket | String
11263 | DNOM Component | Temporary Ground | TEMPGROUND |  | ABNDATETIME | Date and time when the temporary ground was placed | String
11264 | DNOM Component | Temporary Ground | TEMPGROUND |  | ABNDATETIME_TICKS | The time when the status of the temporary ground was last modified | String
11265 | DNOM Component | Temporary Ground | TEMPGROUND | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11266 | DNOM Component | Temporary Ground | TEMPGROUND |  | COMPID | Component ID | String
11267 | DNOM Component | Temporary Ground | TEMPGROUND | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
11268 | DNOM Component | Temporary Ground | TEMPGROUND |  | FRLENGTH | Position of the connection point of the temporary ground on the associated line segment, expressed as a fraction (for example, 0.32). Allowable values are 0-1, where 0 and 1 show that the connection point is placed on the node terminal. | Float
11269 | DNOM Component | Temporary Ground | TEMPGROUND | input | ID | Object unique ID | String |  |  |  | DNMOBJ
11270 | DNOM Component | Temporary Ground | TEMPGROUND |  | LBLPOSITION | Label position | String
11271 | DNOM Component | Temporary Ground | TEMPGROUND | input | NAME | Object name | String |  |  |  | DNMOBJ
11272 | DNOM Component | Temporary Ground | TEMPGROUND |  | NPHASE | A flag indicating the neutral phase | Boolean
11273 | DNOM Component | Temporary Ground | TEMPGROUND |  | OPCOMMNT | Operator inserted comment. | String
11274 | DNOM Component | Temporary Ground | TEMPGROUND |  | ORGCMPID | Original component ID | String
11275 | DNOM Component | Temporary Ground | TEMPGROUND |  | PHASE | Phase | String
11276 | DNOM Component | Temporary Ground | TEMPGROUND |  | POSITIONTXT | Position specific comments | Integer
11277 | DNOM Component | Temporary Ground | TEMPGROUND |  | PRTDEVID | ID of the protection device | String
11278 | DNOM Component | Temporary Ground | TEMPGROUND |  | RGROUND | Grounding resistance (ohms) | Float |  | ohms | ohms
11279 | DNOM Component | Temporary Ground | TEMPGROUND |  | TEMPGRNDTYPE | Type of the temporary ground | String
11280 | DNOM Component | Temporary Ground | TEMPGROUND |  | TGROTATION | Temporary ground rotation angle (NW = 225, N = 180, NE = 135, E = 90, SE = 45, S = 0, SW = 315, W = 2700 | String
11281 | DNOM Component | Temporary Ground | TEMPGROUND |  | TEMPMODDESCRIPT | Operator inserted comment | String
11282 | DNOM Component | Temporary Ground | TEMPGROUND |  | TEMPMODPERMITAREA | Associated permission area name | String
11283 | DNOM Component | Temporary Ground | TEMPGROUND |  | WASSNAPPED | A flag indicating that the ground position was updated | Boolean
11284 | DNOM Component | Temporary Ground | TEMPGROUND | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
11285 | DNOM Component | Temporary Ground | TEMPGROUND |  | XGROUND | Grounding reactance (ohms) | Float |  | ohms | ohms
11286 | DNOM Component | Temporary Ground | TEMPGROUND | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
11287 | DNOM Component | Transformer | TF | input | _KEY | The unique identifier to represent a device. | String
11288 | DNOM Component | Transformer | TF | output | ACTIVEDEMANDDIFF | Total real power demand difference between calculated and measured values | String |  | MW | MW
11289 | DNOM Component | Transformer | TF | input | AFRPROFORMINDEX | The AFR problem formulation index | Integer
11290 | DNOM Component | Transformer | TF | input | AFRPROFORMNAME | The AFR problem formulation name | Integer
11291 | DNOM Component | Transformer | TF | output | AGGREGATIONACTIVEDEMAND | Total DPF calculated real power demand at the load side (secondary) | String | DPF | MW | MW
11292 | DNOM Component | Transformer | TF | input | BANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11293 | DNOM Component | Transformer | TF | input | BANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11294 | DNOM Component | Transformer | TF | input | BANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11295 | DNOM Component | Transformer | TF | input | BANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
11296 | DNOM Component | Transformer | TF | input | BANK.NAME | Name of the object | String |  |  |  | DNMOBJ
11297 | DNOM Component | Transformer | TF | input | BANK.NUMTF | The number of single-phase transformers in the bank. | Integer |  |  |  | TFBNK
11298 | DNOM Component | Transformer | TF | output | AGGREGATIONACTIVEDEMANDHIGHLOW | Total DPF calculated real power demand at the source side (primary) and at the load side (secondary) | String | DPF | MW | MW
11299 | DNOM Component | Transformer | TF | output | AGGREGATIONACTIVELOSS | Total DPF calculated real power loss | String | DPF | MVAR | MVAR
11300 | DNOM Component | Transformer | TF | output | AGGREGATIONCAPACITORMVAROFFLINE | The calculated offline capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. As opposed to the calculation for online capacitor reactive power, the offline calculation only includes disconnected remote capacitors. | String | MVAR | MVAR | MVAR
11301 | DNOM Component | Transformer | TF | output | AGGREGATIONCAPACITORMVARONLINE | The calculated online capacitor reactive power, which is an aggregation of all capacitors downstream of the given aggregation object. This includes connected fixed and remote capacitors as well as all local capacitors. | String | MVAR | MVAR | MVAR
11302 | DNOM Component | Transformer | TF | output | AGGREGATIONCAPACITORMVARTOTAL | The total capacitor reactive power, which is the sum of the online and offline capacitor reactive power for each aggregation object. | String | MVAR | MVAR | MVAR
11303 | DNOM Component | Transformer | TF | output | AGGREGATIONDERACTIVEDEMAND | Calculated DER/DG real power injection in MW | Float | DPF | MW | MW
11304 | DNOM Component | Transformer | TF | output | AGGREGATIONDERREACTIVEDEMAND | Calculated DER/DG reactive power injection in MVAR | Float | DPF | MVAR | MVAR
11305 | DNOM Component | Transformer | TF | output | AGGREGATIONNATIVEACTIVEDEMAND | Calculated native real power demand in MW | Float | DPF | MW | MW
11306 | DNOM Component | Transformer | TF | output | AGGREGATIONNATIVEREACTIVEDEMAND | Calculated native reactive power demand in MVAR | Float | DPF | MVAR | MVAR
11307 | DNOM Component | Transformer | TF | output | AGGREGATIONPOWERFACTOR | Calculated power factor at the load side | String | DPF
11308 | DNOM Component | Transformer | TF | output | AGGREGATIONPOWERFACTORHIGHLOW | Calculated power factor at the source side (primary) and at the load side (secondary) | String | DPF
11309 | DNOM Component | Transformer | TF | output | AGGREGATIONREACTIVEDEMAND | Total DPF calculated reactive power demand at the load side (secondary) | String | DPF | MVAR | MVAR
11310 | DNOM Component | Transformer | TF | output | AGGREGATIONREACTIVEDEMANDHIGHLOW | Total DPF calculated reactive power demand at the source side (primary) and at the load side (secondary) | String | DPF | MVAR | MVAR
11311 | DNOM Component | Transformer | TF | output | AGGREGATIONREACTIVELOSS | Total DPF calculated reactive power loss | String | DPF | MVAR | MVAR
11312 | DNOM Component | Transformer | TF | input | ALTID | Returns the ADDRESS | String
11313 | DNOM Component | Transformer | TF | output | AMP3PH | Three-phase current (amps). | Float | DPF | Amps | Amps
11314 | DNOM Component | Transformer | TF | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11315 | DNOM Component | Transformer | TF | input | ASCCOILSIZE | Arc Suppression Coil size (kVA). | Float |  | kVA | kVA
11316 | DNOM Component | Transformer | TF | output | AVAILABLEVOLTMARGIN | Minimum available voltage margin (in percent voltage) | Float
11317 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGECALCAMPWEIGHTALLBUS | Weighted calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
11318 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGECALCAMPWEIGHTMVBUS | Weighted calculated average voltage in per unit. Only station MV buses are accounted. The weighting factor is the calculated current value on the same bus. | Float | DPF | p.u. | p.u.
11319 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGECALCNOWEIGHTALLBUS | Calculated average voltage in per unit, including both station MV buses and regulator buses on feeders. | Float | DPF | p.u. | p.u.
11320 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGECALCNOWEIGHTMVBUS | Calculated average voltage in per unit. Only station MV buses are accounted. | Float | DPF | p.u. | p.u.
11321 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
11322 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGEMEASAMPWEIGHTMVBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
11323 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGEMEASNOWEIGHTALLBUS | Weighted measured average voltage in per unit, including both station MV buses and regulator buses on feeders. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
11324 | DNOM Component | Transformer | TF | output | AVRAGEVOLTAGEMEASNOWEIGHTMVBUS | Measured average voltage, station bus only, in per unit | Float | DPF | p.u. | p.u.
11325 | DNOM Component | Transformer | TF | input | BANDWITH | Regulating transformer two side bandwidth (per unit or configurable voltage base) from the external data. | Float
11326 | DNOM Component | Transformer | TF | input | BANK | Pointer to the associated tansformer bank | String
11327 | DNOM Component | Transformer | TF | input | BOUNDARY | The boundary flag | Integer
11328 | DNOM Component | Transformer | TF | output | BUSVOLTMISMATCH | Specifies whether bus voltage mismatch exists | Boolean
11329 | DNOM Component | Transformer | TF |  | CONSOPER | The number of consequent operations | String
11330 | DNOM Component | Transformer | TF | input | CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean
11331 | DNOM Component | Transformer | TF | input | DERKVAR3PHASE | Reactive power output by the DERs | String |  | kVAR | kVAR
11332 | DNOM Component | Transformer | TF | input | DERKW3PHASE | Real power output by the DERs | String |  | kW | kW
11333 | DNOM Component | Transformer | TF | input | DERPF | DER power factor | String
11334 | DNOM Component | Transformer | TF | input | DERPGENMAX | Maximum real power generation by the DERs | String |  | kW | kW
11335 | DNOM Component | Transformer | TF | input | DERQGENMAX | Maximum reactive power generation by DERs | String |  | KVAR | KVAR
11336 | DNOM Component | Transformer | TF | input | DERQGENMIN | Minimum reactive power generation by DERs | String |  | KVAR | KVAR
11337 | DNOM Component | Transformer | TF | input | DEVICEDSOOVER | The override status for DSO Eligible. The value is True and False (not eligible). If it is not set, the value is "--" | String
11338 | DNOM Component | Transformer | TF | input | DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean
11339 | DNOM Component | Transformer | TF |  | DNAFAUTOENABLEDAPPS | Auto enabling bitmask (all apps) | Integer
11340 | DNOM Component | Transformer | TF | Input | DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer
11341 | DNOM Component | Transformer | TF | output | DNAFENABLEDVVALARMS | Bitmaks that indicates if the LVM alarm is enabled | Integer
11342 | DNOM Component | Transformer | TF |  | DNAFLVMENABLED | Indicates If DNAF LVM application is enabled in this feeder | Boolean
11343 | DNOM Component | Transformer | TF | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
11344 | DNOM Component | Transformer | TF | input | DNOMTABNAME | DNOM table name | String
11345 | DNOM Component | Transformer | TF | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11346 | DNOM Component | Transformer | TF | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11347 | DNOM Component | Transformer | TF | input | DSECGRND | Grounded phase winding for a transformer | Integer
11348 | DNOM Component | Transformer | TF |  | DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration
11349 | DNOM Component | Transformer | TF |  | DSOTAPCONTROLENABLED | A flag indicating that the tap changer status is "Enabled" | Boolean
11350 | DNOM Component | Transformer | TF | Output | ESTVOLTAFTERTAPMOVE | Estimated voltage after tap change | Float
11351 | DNOM Component | Transformer | TF | input | EXTERNALID | Pointer to the external ID (from external system) string in the station vector collection. | String
11352 | DNOM Component | Transformer | TF | input | FAULTIND | Pointer to the associated fault indicator | String
11353 | DNOM Component | Transformer | TF | Input | FEEDERMAIN | Flag indicating if the transformer is on feeder main. | Boolean
11354 | DNOM Component | Transformer | TF | input | FISRLOSSVOLTPLANEXEC | Loss of voltage plan execution mode for FISR | Integer
11355 | DNOM Component | Transformer | TF | input | FISRPERMFAULTPLANEXEC | Permanent Fault Plan Execution Mode for FISR | Integer
11356 | DNOM Component | Transformer | TF | input | FISRPROFORMINDEX | The FISR problem formulation index | Integer
11357 | DNOM Component | Transformer | TF | input | FISRPROFORMNAME | The FISR problem formulation name | Integer
11358 | DNOM Component | Transformer | TF | input | FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float
11359 | DNOM Component | Transformer | TF | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
11360 | DNOM Component | Transformer | TF | input | FSDTFNSFAULTSTATUS | Specifies whether the arc suppression coil fault status (Set or Unset). If Set, the transformer is eligible for FSD. | String
11361 | DNOM Component | Transformer | TF | input | GROUNDPR | Primary grounded flag | Boolean
11362 | DNOM Component | Transformer | TF | input | GROUNDSC | Secondary grounded flag | Boolean
11363 | DNOM Component | Transformer | TF | input | GROUNDTE | Tertiary grounded flag | Boolean
11364 | DNOM Component | Transformer | TF |  | HAS_PRTAPPOS_MEAS | A flag indicating that the primary side has tap position measurement | Boolean
11365 | DNOM Component | Transformer | TF |  | HAS_REGBLOCKED_MEAS | A flag indicating that the transformer has Regulation Blocked status measurement | Boolean
11366 | DNOM Component | Transformer | TF |  | HAS_REGULATION_MEAS | A flag indicating that the transformer has Regulation status measurement | Boolean
11367 | DNOM Component | Transformer | TF |  | HAS_REMOTEENABLED_MEAS | A flag indicating that the transformer has Remote Enabled status measurement | Boolean
11368 | DNOM Component | Transformer | TF |  | HAS_SCTAPPOS_MEAS | A flag indicating that the secondary side has tap position measurement | Boolean
11369 | DNOM Component | Transformer | TF |  | HAS_TAPPOS_MEAS | A flag indicating that the transformer has tap position measurement | Boolean
11370 | DNOM Component | Transformer | TF |  | HAS_TETAPPOS_MEAS | A flag indicating that the tertiary side has tap position measurement | Boolean
11371 | DNOM Component | Transformer | TF |  | HAS_VOLTREDUCTION_MEAS | A flag indicating that the transformer has Voltage Reduction status measurement | Boolean
11372 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_BUS_HV | Flag indicating feeder bus HV violation limit value is auto, inherited or manual | String
11373 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_BUS_LV | Flag indicating feeder bus LV violation limit value is auto, inherited or manual | String
11374 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_BUSOPT_HV | Flag indicating feeder bus HV optimization limit value is auto, inherited or manual | String
11375 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_BUSOPT_LV | Flag indicating feeder bus LV optimization limit value is auto, inherited or manual | String
11376 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_FLOW | Flag indicating all the feeder flow limit value is auto, inherited or manual | String
11377 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_LOAD_HV | Flag indicating feeder load HV violation limit value is auto, inherited or manual | String
11378 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_LOAD_LV | Flag indicating feeder load LV violation limit value is auto, inherited or manual | String
11379 | DNOM Component | Transformer | TF | input | HASMAN_FDR_LOADOPT_HV | Flag indicating feeder load HV optimization limit value is auto, inherited or manual | String
11380 | DNOM Component | Transformer | TF | input | HASMAN_FDR_LOADOPT_LV | Flag indicating feeder load LV optimization limit value is auto, inherited or manual | String
11381 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_LOADSCALING | Flag indicating the feeder load scaling factor value is auto, inherited or manual | String
11382 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_LVM_MAX_PF | Flag indicating feeder LVM maximum PF target value is auto,inherited, or manual | String
11383 | DNOM Component | Transformer | TF | Input | HASMAN_FDR_LVM_MIN_PF | Flag indicating feeder LVM minimum PF target value is auto,inherited, or manual | String
11384 | DNOM Component | Transformer | TF | Input | HASMAN_TRANS_FLOW | Flag indicating the transformer flow limit value is auto, inherited or manual | String
11385 | DNOM Component | Transformer | TF | Input | HASMANUALENTRY | Flag indicating the transformer has manual entry | Boolean
11386 | DNOM Component | Transformer | TF | output | HASPRTAP | Has tap changer at primary side | Boolean |  | #N/A | #N/A
11387 | DNOM Component | Transformer | TF | input | HASREGTAP | Flag indicating if the transformer has regulation tap | Boolean
11388 | DNOM Component | Transformer | TF | output | HASSCTAP | Has tap changer at secondary side | Boolean |  | #N/A | #N/A
11389 | DNOM Component | Transformer | TF | output | HASTETAP | Has tap changer at tertiary side | Boolean
11390 | DNOM Component | Transformer | TF | output | HISTTFCOPPERLOSSKVAR | Reactive power of Copper loss | Float | DPF | kVAR | kVAR
11391 | DNOM Component | Transformer | TF | output | HISTTFCOPPERLOSSKW | Real power of Copper loss | Float | DPF | kW | kW
11392 | DNOM Component | Transformer | TF | output | HISTTFCORELOSSKVAR | Reactive power of Core loss | Float | DPF | kVAR | kVAR
11393 | DNOM Component | Transformer | TF | output | HISTTFCORELOSSKW | Real power of Core loss | Float | DPF | kW | kW
11394 | DNOM Component | Transformer | TF | output | HISTTFSECVAR3PH | Sum of three phase reactive power injected at Secondary side into the transformer | Float | DPF | VAR | VAR
11395 | DNOM Component | Transformer | TF | input | LOWSDBUS.AREAIND | Index in the station permission area list | Integer |  |  |  | DNMOBJ
11396 | DNOM Component | Transformer | TF | input | LOWSDBUS.DNOMX | X coordinate of the node | Float |  |  |  | DNMOBJ
11397 | DNOM Component | Transformer | TF | input | LOWSDBUS.DNOMY | Y coordinate of the node | Float |  |  |  | DNMOBJ
11398 | DNOM Component | Transformer | TF | input | LOWSDBUS.FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
11399 | DNOM Component | Transformer | TF | input | LOWSDBUS.ID | ID of the node | String |  |  |  | DNMOBJ
11400 | DNOM Component | Transformer | TF | input | LOWSDBUS.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11401 | DNOM Component | Transformer | TF | input | LOWSDBUS.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11402 | DNOM Component | Transformer | TF | input | LOWSDBUS.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
11403 | DNOM Component | Transformer | TF | input | LOWSDBUS.VOLTCALC | Node mask | Integer |  |  |  | NODE
11404 | DNOM Component | Transformer | TF | output | HISTTFSECWATT3PH | Sum of three phase real power injected at Secondary side into the transformer | Float | DPF | Walt | Walt
11405 | DNOM Component | Transformer | TF | input | ID | Object unique ID | String |  |  |  | DNMOBJ
11406 | DNOM Component | Transformer | TF | output | ISDERGATEWAYCONTROLLED | Specifies whether the transformer has DERs that are controlled by the 2030.5 Gateway | Boolean
11407 | DNOM Component | Transformer | TF |  | ISMANVREDUCTAPPLICABLE | A flag indicating that manual voltage reduction is enabled | Boolean
11408 | DNOM Component | Transformer | TF | input | ISPOWERTF | Flag indicating if the transformer is power transformer | Boolean
11409 | DNOM Component | Transformer | TF | input | ISPOWERTFORSTATIONREG | Flag indicating if the transformer is power transformer or station regulator | String
11410 | DNOM Component | Transformer | TF | input | ISRTAFRVALID | Specifies whether AFR is enabled for RT | Boolean
11411 | DNOM Component | Transformer | TF | input | ISRTDPFVALID | Specifies whether DPF is enabled for RT | Boolean
11412 | DNOM Component | Transformer | TF | input | ISRTFISRVALID | Specifies whether FISR is enabled for RT | Boolean
11413 | DNOM Component | Transformer | TF | input | ISRTFLVALID | Specifies whether FL is enabled for RT | Boolean
11414 | DNOM Component | Transformer | TF | input | ISRTLVMVALID | Specifies whether LVM is enabled for RT | Boolean
11415 | DNOM Component | Transformer | TF | input | ISRTPRVVALID | Specifies whether PRV is enabled for RT | Boolean
11416 | DNOM Component | Transformer | TF | input | ISRTSCCVALID | Specifies whether SCC is enabled for RT | Boolean
11417 | DNOM Component | Transformer | TF | input | ISSIMDPFVALID | Specifies whether DPF is enabled for SIM | Boolean
11418 | DNOM Component | Transformer | TF | input | ISSIMFLVALID | Specifies whether FL is enabled for SIM | Boolean
11419 | DNOM Component | Transformer | TF | input | ISSTAFRVALID | Specifies whether AFR is enabled for ST | Boolean
11420 | DNOM Component | Transformer | TF | input | ISSTDPFVALID | Specifies whether DPF is enabled for ST | Boolean
11421 | DNOM Component | Transformer | TF | input | ISSTFISRCAVALID | Specifies whether FISRCA is enabled for RT | Boolean
11422 | DNOM Component | Transformer | TF | input | ISSTFISRVALID | Specifies whether FISR is enabled for ST | Boolean
11423 | DNOM Component | Transformer | TF | input | ISSTFLVALID | Specifies whether FL is enabled for ST | Boolean
11424 | DNOM Component | Transformer | TF | input | ISSTLVMVALID | Specifies whether LVM is enabled for ST | Boolean
11425 | DNOM Component | Transformer | TF | input | ISSTPLOSVALID | Specifies whether PLOS is enabled for ST | Boolean
11426 | DNOM Component | Transformer | TF | input | ISSTPRVVALID | Specifies whether PRV is enabled for ST | Boolean
11427 | DNOM Component | Transformer | TF | input | ISSTSCCVALID | Specifies whether SCC is enabled for ST | Boolean
11428 | DNOM Component | Transformer | TF | input | LDCCMPRV | Regulating transformer line drop compensation resistance (V). | Float
11429 | DNOM Component | Transformer | TF | input | LDCCMPXV | Nominal regulating transformer line drop compensation reactance (V). | Float
11430 | DNOM Component | Transformer | TF |  | LIMFLAGS | Number of limit violations | Integer
11431 | DNOM Component | Transformer | TF | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
11432 | DNOM Component | Transformer | TF | input | LOWSDBUS | Pointer to associated low side bus (node is statically determined) | String
11433 | DNOM Component | Transformer | TF | input | SRCPROTDEV | Pointer to the source side protective device | String
11434 | DNOM Component | Transformer | TF | input | LOADPROTDEV | Pointer to the load side protective device | String
11435 | DNOM Component | Transformer | TF | Output | LTCREGDAILYOPERATIONS | The num of daily switching operations of tap changer | Integer |  | #N/A | #N/A
11436 | DNOM Component | Transformer | TF | Input | LTCREGMONIDURATION | Regulation device tap position change monitored duration (in hours) | Integer |  | #N/A | #N/A
11437 | DNOM Component | Transformer | TF | Output | LTCREGMONIENDTIM | Monitoring ending time of tap changer | String
11438 | DNOM Component | Transformer | TF | Output | LTCREGMONIENDTIM_TICKS | Monitoring ending time of tap changer in ticks count | Integer
11439 | DNOM Component | Transformer | TF | Output | LTCREGMONIOPERATIONS | The num of operations within monitoring time intervals of tap changer | Integer |  | Hour | Hour
11440 | DNOM Component | Transformer | TF | Output | LTCREGMONISTARTTIM | Monitoring starting time of tap changer | String |  | #N/A | #N/A
11441 | DNOM Component | Transformer | TF | Output | LTCREGMONISTARTTIM_TICKS | Monitoring starting time of tap changer in ticks count | Integer
11442 | DNOM Component | Transformer | TF |  | LVMAUTOENABLEDTEXT | LVM auto enabled text | String
11443 | DNOM Component | Transformer | TF | output | LVMBACKCALCPRIORITY | LVM Back Calculation Priority | Integer |  | #N/A | #N/A
11444 | DNOM Component | Transformer | TF | Output | LVMELIGIBILITY | Flag indicating Heuristic LVM is eligible | Boolean
11445 | DNOM Component | Transformer | TF | Output | LVMEVALORDER | Heuristic LVM evaluation order | Integer
11446 | DNOM Component | Transformer | TF | output | LVMFAILSAFEACTIVE | Specifies whether a failsafe LVM problem formulation is applied. | Boolean
11447 | DNOM Component | Transformer | TF | output | LVMFAILSAFEREASON | This flag determines the LVM failsafe condition reason 1=Bus Voltage Mismatch, 2=DPF Solution State, 3=Bus Voltage Mismatch and DPF Solution State. | Integer
11448 | DNOM Component | Transformer | TF | input | MODEL.BANKCODE | Transformer bank code | String |  |  |  | TFMOD
11449 | DNOM Component | Transformer | TF | input | MODEL.CNSTTYPE | Configuration type (overhead, underground, padmount, others) | Integer |  |  |  | TFMOD
11450 | DNOM Component | Transformer | TF | input | MODEL.CYCREACT | CYC matrix elements - reactive portion | Integer |  |  |  | TFMOD
11451 | DNOM Component | Transformer | TF | input | MODEL.CYCREAL | CYC matrix elements - real portion | Integer |  |  |  | TFMOD
11452 | DNOM Component | Transformer | TF | input | MODEL.DMSTYPE | Enumerated transformer type. The following values are used: 1 = Secondary transformer, 2 = Voltage regulator, 3 = Power transformer, 4 = Auto-transformer, 5 = Step Up/Down transformer, 6 = Zigzag transformer. | Integer |  |  |  | TFMOD
11453 | DNOM Component | Transformer | TF | input | MODEL.EXCITEPF | Magnetization power factor (optional if percent excitation current is provided) | Float |  |  |  | TFMOD
11454 | DNOM Component | Transformer | TF | input | MODEL.EXCTEAMP | Average percent excitation current (optional if the magnetizing power factor is provided) | Float |  |  |  | TFMOD
11455 | DNOM Component | Transformer | TF | input | MODEL.ID | Object unique ID | String |  |  |  | DNMOBJ
11456 | DNOM Component | Transformer | TF | input | MODEL.LIMITEVENT | A flag indicating operational limit event | Boolean |  |  |  | TFMOD
11457 | DNOM Component | Transformer | TF | input | MODEL.LIMITEVENTSEC | A flag indicating secondary operational limit event | Boolean |  |  |  | TFMOD
11458 | DNOM Component | Transformer | TF | input | MODEL.LIMITEVENTTER | A flag indicating tertiary operational limit event | Boolean |  |  |  | TFMOD
11459 | DNOM Component | Transformer | TF | input | MODEL.LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term) | String |  |  |  | TFMOD
11460 | DNOM Component | Transformer | TF | input | MODEL.LIMNAMES | The limits name in secondary winding | String |  |  |  | TFMOD
11461 | DNOM Component | Transformer | TF | input | MODEL.LIMNAMET | The limits name in tertiary winding | String |  |  |  | TFMOD
11462 | DNOM Component | Transformer | TF | input | MODEL.LIMSEASSEC | Season of the operational limit in secondary winding | String |  |  |  | TFMOD
11463 | DNOM Component | Transformer | TF | input | MODEL.LIMUNIT | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | Integer |  |  |  | TFMOD
11464 | DNOM Component | Transformer | TF | input | MODEL.LIMUNITS | The limits unit in secondary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer |  |  |  | TFMOD
11465 | DNOM Component | Transformer | TF | input | MODEL.LIMUNITT | The limits unit in tertiary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer |  |  |  | TFMOD
11466 | DNOM Component | Transformer | TF | input | MODEL.LIMVALS | The limits value in secondary winding | Float |  |  |  | TFMOD
11467 | DNOM Component | Transformer | TF | input | MODEL.LIMVALT | The limits value in tertiary winding | Float |  |  |  | TFMOD
11468 | DNOM Component | Transformer | TF | input | MODEL.LIMVALUE | Value of the operational limit | Float |  | Amps, kVA, or MVA | Amps, kVA, or MVA | TFMOD
11469 | DNOM Component | Transformer | TF | input | MODEL.MAGLOSS | Transformer nominal core loss | Float |  |  |  | TFMOD
11470 | DNOM Component | Transformer | TF | input | MODEL.MAGYZERO | Zero sequence magnetization susceptance (optional) | Complex |  |  |  | TFMOD
11471 | DNOM Component | Transformer | TF | input | MODEL.NAME | Associated transformer model name. | String
11472 | DNOM Component | Transformer | TF | input | MODEL.NUMCYCEL | Number of elements | Integer |  |  |  | TFMOD
11473 | DNOM Component | Transformer | TF | input | MODEL.NUMCYCRW | Number of rows | Integer |  |  |  | TFMOD
11474 | DNOM Component | Transformer | TF | input | MODEL.NUMLIMIT | The number of operation limits | Integer |  |  |  | TFMOD
11475 | DNOM Component | Transformer | TF | input | MODEL.NUMLIMSS | The number of the operation limits in secondary winding | Integer |  |  |  | TFMOD
11476 | DNOM Component | Transformer | TF | input | MODEL.NUMLIMST | The number of the limits in tertiary winding | Integer |  |  |  | TFMOD
11477 | DNOM Component | Transformer | TF | input | MODEL.NUMRGLIM | The number of regulator step limits | Integer |  |  |  | TFMOD
11478 | DNOM Component | Transformer | TF | input | MODEL.PRIMGRDZ | Primary grounding impedance | Float |  |  |  | TFMOD
11479 | DNOM Component | Transformer | TF | input | MODEL.PRIMZ | Primary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
11480 | DNOM Component | Transformer | TF | input | MODEL.REGLIMIT | Regulator step limit | Float |  | Amps | Amps | TFMOD
11481 | DNOM Component | Transformer | TF | input | MODEL.REGLIMITEVENT | A flag indicating regulation limit event | Boolean |  |  |  | TFMOD
11482 | DNOM Component | Transformer | TF | input | MODEL.REGRTGIV | Flag indicating whether the provided rating is the regulating VA | Boolean |  |  |  | TFMOD
11483 | DNOM Component | Transformer | TF | input | MODEL.REGUNITS | Enumerated flag indicating the voltage units that should be used for transformers with voltage regulation capability. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer |  |  |  | TFMOD
11484 | DNOM Component | Transformer | TF | input | MODEL.RGLIMSTP | The regulation step in percent voltage such as 5.0% or 10.0% | Float |  |  |  | TFMOD
11485 | DNOM Component | Transformer | TF | input | MODEL.SECGRDZ | Secondary grounding impedance | Float |  |  |  | TFMOD
11486 | DNOM Component | Transformer | TF | input | MODEL.SECZ | Secondary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
11487 | DNOM Component | Transformer | TF | input | MODEL.SRATING | Transformer rating | Float |  | kVA or MVA | kVA or MVA | TFMOD
11488 | DNOM Component | Transformer | TF | input | MODEL.SRATINGTER | Tertiary winding Rated capacity in kVA or MVA depending on the units flag | Float |  | kVA or MVA | kVA or MVA | TFMOD
11489 | DNOM Component | Transformer | TF | input | MODEL.SUNITS | A flag indicating units used for displaying transformer rating (true - kVA, false - MVA) | Boolean |  |  |  | TFMOD
11490 | DNOM Component | Transformer | TF | input | MODEL.TERTGRDZ | Tertiary grounding impedance | Float |  |  |  | TFMOD
11491 | DNOM Component | Transformer | TF | input | MODEL.TERTZ | Tertiary positive sequence resistance (per unit on transformer power base) | Float |  |  |  | TFMOD
11492 | DNOM Component | Transformer | TF | input | MODEL.TFTYPE | Enumerated transformer type for linking the transformer model to a transformer type that is needed by the power flow function | Integer |  |  |  | TFMOD
11493 | DNOM Component | Transformer | TF | input | MODEL.TFTYPEINDEX | Transformer type index, used for validation purposes | Integer |  |  |  | TFMOD
11494 | DNOM Component | Transformer | TF | output | LVMFAILSAFEREVERSALMETHOD | This flag determines whether LVM automatically reverts the problem formulation to the one used before the heuristic failsafe problem formulation. 0=Manual Reversion, 1=Automatic Reversion. | Integer
11495 | DNOM Component | Transformer | TF | Input | LVMMAXPHASEVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float
11496 | DNOM Component | Transformer | TF |  | LVMNOTELIGIBLECOUNT | LVM not eligible counter | Integer
11497 | DNOM Component | Transformer | TF | output | LVMPROFILEDATA | LVM profile data | Integer
11498 | DNOM Component | Transformer | TF | Input | LVMPROFORMINDEX | LVM problem formulation index | Integer
11499 | DNOM Component | Transformer | TF |  | LVMPROFORMNAME | LVM problem formulation name | String
11500 | DNOM Component | Transformer | TF | Input | MAN_FDR_BUS_HV | feeder bus HV violation limit (p.u.) manual override value | Float
11501 | DNOM Component | Transformer | TF | Input | MAN_FDR_BUS_LV | feeder bus LV violation limit (p.u.) manual override value | Float
11502 | DNOM Component | Transformer | TF | Input | MAN_FDR_BUSOPT_HV | feeder bus HV optimization limit (p.u.) manual override value | Float
11503 | DNOM Component | Transformer | TF | Input | MAN_FDR_BUSOPT_LV | feeder bus LV optimization limit (p.u.) manual override value | Float
11504 | DNOM Component | Transformer | TF | Input | MAN_FDR_FLOW | all feeder devices flow limit (% of nominal) manual override value | Float
11505 | DNOM Component | Transformer | TF | Input | MAN_FDR_LOAD_HV | feeder load HV violation limit (p.u.) manual override value | Float
11506 | DNOM Component | Transformer | TF | Input | MAN_FDR_LOAD_LV | feeder load LV violation limit (p.u.) manual override value | Float
11507 | DNOM Component | Transformer | TF | input | MAN_FDR_LOADOPT_HV | Feeder load HV optimization limit (p.u.) manual override value | Float
11508 | DNOM Component | Transformer | TF | input | MAN_FDR_LOADOPT_LV | Feeder load LV optimization limit (p.u.) manual override value | Float
11509 | DNOM Component | Transformer | TF | Input | MAN_FDR_LOADSCALING | The feeder load scaling factor manual override value | Float
11510 | DNOM Component | Transformer | TF | Input | MAN_FDR_LVM_MAX_PF | feeder LVM maximum PF target manual override value | Float
11511 | DNOM Component | Transformer | TF | Input | MAN_FDR_LVM_MIN_PF | feeder LVM minimum PF target manual override value | Float
11512 | DNOM Component | Transformer | TF | Input | MAN_TRANS_FLOW | transformer flow limit (% of nominal) manual override value | Float
11513 | DNOM Component | Transformer | TF | input | MANBANDWITH | Manually entered voltage bandwidth value (per unit or configurable voltage base). | Float
11514 | DNOM Component | Transformer | TF | input | MANLDCCMPRV | Manually entered line drop compensation resistance (V). | Float
11515 | DNOM Component | Transformer | TF | input | MANLDCCMPXV | Manually entered line drop compensation resistance (V). | Float
11516 | DNOM Component | Transformer | TF | input | MANVREDVAL | Manually entered voltage reduction value (per unit or configurable voltage base). | Float
11517 | DNOM Component | Transformer | TF | input | MANVTARGET | Manually entered voltage regulation target (per unit or configurable voltage base). | Float
11518 | DNOM Component | Transformer | TF | input | MAXASCGROUNDX | Default value of the Arc Suppression Coil maximum grounding reactance (ohms). | Float |  | Ohms | Ohms
11519 | DNOM Component | Transformer | TF | Input | MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer
11520 | DNOM Component | Transformer | TF | Input | MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  | % | %
11521 | DNOM Component | Transformer | TF | input | MINASCGROUNDX | Default value of the Arc Suppression Coil minimum grounding reactance (ohms). | Float |  | Ohms | Ohms
11522 | DNOM Component | Transformer | TF | input | MODEL | Pointer to the associated transformer model | String
11523 | DNOM Component | Transformer | TF | input | NAME | Object name | String |  |  |  | DNMOBJ
11524 | DNOM Component | Transformer | TF | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11525 | DNOM Component | Transformer | TF | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
11526 | DNOM Component | Transformer | TF | input | NOMBANDWITH | Regulating transformer two side nominal bandwidth (per unit or configurable voltage base) from the external data. | Float
11527 | DNOM Component | Transformer | TF | input | NOMCCUST | The number of nominally connected customers | Integer
11528 | DNOM Component | Transformer | TF | input | NOMLDCCMPRV | Nominal Regulating transformer line drop compensation resistance (V). | Float
11529 | DNOM Component | Transformer | TF | Input | NOMLDCCMPXV | Nominal Regulating transformer line drop compensation reactance. | Float
11530 | DNOM Component | Transformer | TF | input | NOMVREDVAL | Nominal Voltage reduction value (per unit or configurable voltage base). | Float
11531 | DNOM Component | Transformer | TF | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
11532 | DNOM Component | Transformer | TF |  | OLDLVMPROFORMINDEX | Index of the LVM problem formulation that was specified in the DNAF System Configuration display for the transformer before applying a failsafe problem formulation. Used for Failsafe reversion. | Integer |  | #NA | #NA
11533 | DNOM Component | Transformer | TF | input | POWERTFENGZSTATUS | Power transformer energization status on primary side | String
11534 | DNOM Component | Transformer | TF | input | POWERTFLWBUSENGZSTATUS | Power transformer energization status on secondary side | String
11535 | DNOM Component | Transformer | TF | input | PRIMBANDWTH | Primary tap bandwidth (per unit or configurable voltage base) | Float
11536 | DNOM Component | Transformer | TF | input | PRIMCTRATIO | Primary winding tap CT ratio. | Float
11537 | DNOM Component | Transformer | TF | Input | PRIMCTSECAMPRATING | Primary tap CT amps | Float
11538 | DNOM Component | Transformer | TF | input | PRIMGNDR | Primary grounding branch resistance | Float
11539 | DNOM Component | Transformer | TF | input | PRIMGNDX | Primary grounding branch reactance | Float
11540 | DNOM Component | Transformer | TF | input | PRIMLDCR | Primary winding line drop compensation resistance (V). | Float
11541 | DNOM Component | Transformer | TF | input | PRIMLDCX | Primary winding transformer line drop compensation reactance (V). | Float
11542 | DNOM Component | Transformer | TF | input | PRIMMAXTAPKV | Primary tap - maximum tap position in kV | Float |  | kV | kV
11543 | DNOM Component | Transformer | TF | input | PRTAP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11544 | DNOM Component | Transformer | TF | input | PRTAP.BANDWITH | One sided bandwidth | Integer |  |  |  | TAPCHR
11545 | DNOM Component | Transformer | TF | input | PRTAP.CTRATIO | Regulator CT ratio - used to determine the per unit LDC R and X required by the power flow | Float |  |  |  | TAPCHR
11546 | DNOM Component | Transformer | TF | input | PRTAP.CTSECAMP | Regulator CT full load secondary amps (used to determine the per unit LDC R and X required by the power flow) | Float |  |  |  | TAPCHR
11547 | DNOM Component | Transformer | TF | input | PRTAP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11548 | DNOM Component | Transformer | TF | input | PRTAP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11549 | DNOM Component | Transformer | TF | input | PRTAP.ID | Object unique ID | String |  |  |  | DNMOBJ
11550 | DNOM Component | Transformer | TF | input | PRTAP.LDCCMPRV | Line drop compensation resistance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11551 | DNOM Component | Transformer | TF | input | PRTAP.LDCCMPXV | Line drop compensation reactance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11552 | DNOM Component | Transformer | TF | input | PRTAP.LDCCOMPR | Value for the line drop compensation resistance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11553 | DNOM Component | Transformer | TF | input | PRTAP.LDCCOMPX | Value for the line drop compensation reactance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11554 | DNOM Component | Transformer | TF | input | PRTAP.MANBANDWITH | Override value of voltage bandwidth | Integer |  |  |  | TAPCHR
11555 | DNOM Component | Transformer | TF | input | PRTAP.MANLDCCMPRV | Override value of line drop compensation resistance | Integer |  |  |  | TAPCHR
11556 | DNOM Component | Transformer | TF | input | PRTAP.MANLDCCMPXV | Override value of line drop compensation reactance | Integer |  |  |  | TAPCHR
11557 | DNOM Component | Transformer | TF | input | PRTAP.MANVREDVAL | Override value of voltage reduction | Integer |  |  |  | TAPCHR
11558 | DNOM Component | Transformer | TF | input | PRTAP.MANVTARGET | Override value of target voltage to regulate | Integer |  |  |  | TAPCHR
11559 | DNOM Component | Transformer | TF | input | PRTAP.NAME | Primary tap name. | String |  |  |  | DNMOBJ
11560 | DNOM Component | Transformer | TF | input | PRTAP.NORMTAP | Normal tap ratio (mainly set for fixed taps) | Integer |  |  |  | TAPCHR
11561 | DNOM Component | Transformer | TF | input | PRTAP.NRMTPRAT | Fixed tap ratio value | Float |  |  |  | TAPCHR
11562 | DNOM Component | Transformer | TF | input | PRTAP.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | TAPCHR
11563 | DNOM Component | Transformer | TF | input | PRTAP.PTRATIO | Regulator PT ratio, used to determine the voltage target range (VMax and VMin) | Float |  |  |  | TAPCHR
11564 | DNOM Component | Transformer | TF | input | PRTAP.REVREG | Flag indicating that the regulator has reverse regulation capability | Boolean |  |  |  | TAPCHR
11565 | DNOM Component | Transformer | TF | input | PRTAP.TAPCNTRL | Tap control mode (0 - No tap control - for fixed tap, 1 - Remote only, 2 - Local only, 3 - Remote and local) | Enumeration |  |  |  | TAPCHR
11566 | DNOM Component | Transformer | TF | input | PRTAP.TAPEND | Transformer winding with movable tap (0 - Primary, 1 - Secondary, 2 - Tertiary) | Enumeration |  |  |  | TAPCHR
11567 | DNOM Component | Transformer | TF | input | PRTAP.TAPINIT | Initial tap position | Integer |  |  |  | TAPCHR
11568 | DNOM Component | Transformer | TF | input | PRTAP.TAPLDCRMANOVER | Flag indicating the nominal line drop compensation resistance override | Boolean |  |  |  | TAPCHR
11569 | DNOM Component | Transformer | TF | input | PRTAP.TAPLDCXMANOVER | Flag indicating the nominal line drop compensation reactance override | Boolean |  |  |  | TAPCHR
11570 | DNOM Component | Transformer | TF | input | PRTAP.TAPMANTAPCOSTOPT | Override value of scale cost for tap move | Integer |  |  |  | TAPCHR
11571 | DNOM Component | Transformer | TF | input | PRTAP.TAPMODE | Tap changer regulation mode (0 - No_Tap, 1 - Fixed, 2 - VoltageRegulation, 3 - VarRegulation) | Enumeration |  |  |  | TAPCHR
11572 | DNOM Component | Transformer | TF | input | PRTAP.TAPNOM | Nominal tap ratio (deterned as terminal voltage divided by the internal transformer voltage) | Float |  |  |  | TAPCHR
11573 | DNOM Component | Transformer | TF | input | PRTAP.TAPREDVALMANENABLE | A flag indicating the voltage reduction override | Boolean |  |  |  | TAPCHR
11574 | DNOM Component | Transformer | TF | input | PRTAP.TAPSTEP | Final (resulting) tap position | Integer |  |  |  | TAPCHR
11575 | DNOM Component | Transformer | TF | input | PRTAP.TAPTAPCOSTOPTMANENABLE | A flag indicating the scale cost for tap move override | Boolean |  |  |  | TAPCHR
11576 | DNOM Component | Transformer | TF | input | PRTAP.TAPVBWMANENABLE | Flag indicating the voltage bandwidth override | Boolean |  |  |  | TAPCHR
11577 | DNOM Component | Transformer | TF | input | PRTAP.TAPVTGMANENABLE | Flag indicating the voltage target override | Boolean |  |  |  | TAPCHR
11578 | DNOM Component | Transformer | TF | input | PRTAP.VREDBLK | A flag indicating that the tap has one step voltage reduction and blocking capability | Boolean |  |  |  | TAPCHR
11579 | DNOM Component | Transformer | TF | input | PRTAP.VREDPU | Voltage reduction value. The voltage target range is shifted down by this value when the voltage reduction is enabled. | Float |  | p.u. | p.u. | TAPCHR
11580 | DNOM Component | Transformer | TF | input | PRTAP.VTARGET | Target voltage to regulate | Float |  |  |  | TAPCHR
11581 | DNOM Component | Transformer | TF | input | PRTAP.VTARGMAX | Maximum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11582 | DNOM Component | Transformer | TF | input | PRTAP.VTARGMIN | Minimum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11583 | DNOM Component | Transformer | TF | input | PRIMMAXTAPPOS | Maximum tap position of the tap changer installed on the primary winding | Integer
11584 | DNOM Component | Transformer | TF | input | PRIMMINTAPKV | Primary tap - minimum tap position in kV | Float |  | kV | kV
11585 | DNOM Component | Transformer | TF | input | PRIMMINTAPPOS | Minimum tap position of the tap changer installed on the primary winding | Integer
11586 | DNOM Component | Transformer | TF | input | PRIMNOMINALTAPKV | Primary tap - nominal tap position in kV | Float |  | kV | kV
11587 | DNOM Component | Transformer | TF | input | PRIMNOMTAPPOS | Nominal tap position of the tap changer installed on the primary winding | Integer
11588 | DNOM Component | Transformer | TF | input | PRIMNORMTAPPOS | Transformer primary side tap normal position. The value is “--“ (null) for "Regulating" or "None" (no tap exists for the winding) tap changer types, or an integer between (or equal to) the minimum and maximum tap position for the "Fixed" tap changer type. | Integer
11589 | DNOM Component | Transformer | TF | input | PRIMPHASESENSED | Primary winding phases Measured | String
11590 | DNOM Component | Transformer | TF | Input | PRIMPTRATIO | Primary winding PT ratio | Float
11591 | DNOM Component | Transformer | TF | Input | PRIMPTVMEASLL | Flag indicating regulation voltage is measured line to line for primary winding (True = line to line) | Boolean
11592 | DNOM Component | Transformer | TF |  | PRIMTAPBLOCK | Primary tap blocked status | String
11593 | DNOM Component | Transformer | TF | input | PRIMTAPBLOCKSTATUS | Primary tap blocked status with measurement quality | String
11594 | DNOM Component | Transformer | TF | input | PRIMTAPCONTROLMODE | Primary tap control mode | String
11595 | DNOM Component | Transformer | TF | input | PRIMTAPCOST | Primary tap switching cost | String
11596 | DNOM Component | Transformer | TF |  | PRIMTAPLOCALREMOTE | Primary tap remote control status | String
11597 | DNOM Component | Transformer | TF |  | PRIMTAPMANREGULATIONON | Primary tap regulation status | String
11598 | DNOM Component | Transformer | TF | input | PRIMTAPOPERMODE | Primary tap operation mode | String
11599 | DNOM Component | Transformer | TF |  | PRIMTAPREGULATION | Primary tap regulation status | String
11600 | DNOM Component | Transformer | TF | input | PRIMTAPREMOTEOPERMODE | Primary tap tap changer current remote control mode (None, Raise/Lower, Voltage Setpoint, or Voltage Reduction). | String
11601 | DNOM Component | Transformer | TF | input | SECTAPREMOTEOPERMODE | Secondary tap tap changer current remote control mode (None, Raise/Lower, Voltage Setpoint, or Voltage Reduction). | String
11602 | DNOM Component | Transformer | TF | input | PRIMTAPREMOTECONTROLMODE | Primary tap tap changer remote control capability (None, Raise/Lower, Voltage Setpoint, Raise/Lower and Voltage Setpoint, or Voltage Reduction). | String
11603 | DNOM Component | Transformer | TF | input | SECTAPREMOTECONTROLMODE | Secondary tap tap changer remote control capability (None, Raise/Lower, Voltage Setpoint, Raise/Lower and Voltage Setpoint, or Voltage Reduction). | String
11604 | DNOM Component | Transformer | TF | input | PRIMTAPSTEP | Tap step of the tap changer installed on the primary winding (%) | Float
11605 | DNOM Component | Transformer | TF | input | PRIMTAPSTEPKV | Primary tap - tap step size in kV | Float |  | kV | kV
11606 | DNOM Component | Transformer | TF | input | PRIMTARGETVOLT | Primary tap voltage target (per unit or configurable voltage base). | Float
11607 | DNOM Component | Transformer | TF |  | PRIMTFREGTAPPOSSTATUS | Primary TF regulating tap position status | Integer
11608 | DNOM Component | Transformer | TF |  | PRIMTFREGULATIONSTATUS | Primary TF regulation status | String
11609 | DNOM Component | Transformer | TF |  | PRIMTFREMOTECONTROLSTATUS | Primary TF remote control status | String
11610 | DNOM Component | Transformer | TF | input | PRIMTFVOLTREDUCTSTATUS | Voltage reduction status for the primary winding. Measured value (Enable/Disable) | String
11611 | DNOM Component | Transformer | TF | input | PRIMVSETPNTDEADBAND | Primary voltage setpoint deadband | String
11612 | DNOM Component | Transformer | TF | input | PRIMWIND | Primary winding connection type | Integer
11613 | DNOM Component | Transformer | TF | input | PRTAP | Pointer to the primary winding tap changer | String
11614 | DNOM Component | Transformer | TF | Output | PRTAPMANENABLE | Flag indicating the tap changer on the primary side has manual overridden value | Boolean
11615 | DNOM Component | Transformer | TF | Output | PRTAPPOS | Primary Side Tap Position | Integer
11616 | DNOM Component | Transformer | TF | output | PRTAPPOSITION | Primary Side Tap Position | Integer | DPF | #N/A | #N/A
11617 | DNOM Component | Transformer | TF |  | PTTAPINIT | Manually entered primary side tap position value | String
11618 | DNOM Component | Transformer | TF | input | PWRTFBANKID | Power transformer bank ID | String
11619 | DNOM Component | Transformer | TF | input | PWRTFBANKNAME | Power transformer bank name | String
11620 | DNOM Component | Transformer | TF | output | REACTIVEDEMANDDIFF | Total reactive power demand difference between calculated and measured values | String |  | MVAR | MVAR
11621 | DNOM Component | Transformer | TF | input | REALVTARGET | Real/effective voltage regulation target (per unit or configurable voltage base). | Float
11622 | DNOM Component | Transformer | TF | input | REGAMPS | Regulating transformer base ampacity limit. | Float
11623 | DNOM Component | Transformer | TF | input | REGBANDWTH | Regulating transformer two side bandwidth (per unit or configurable voltage base) | Float
11624 | DNOM Component | Transformer | TF | input | REGBYPASSSW | Bypass switch name | String
11625 | DNOM Component | Transformer | TF | input | REGCTRATIO | Regulating tap CT ratio. | Float
11626 | DNOM Component | Transformer | TF | Input | REGCTSECAMPRATING | CT secondary amps | Float
11627 | DNOM Component | Transformer | TF | input | REGULATORGROUP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11628 | DNOM Component | Transformer | TF | input | REGULATORGROUP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11629 | DNOM Component | Transformer | TF | input | REGULATORGROUP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11630 | DNOM Component | Transformer | TF | input | REGULATORGROUP.ID | Object unique ID | String |  |  |  | DNMOBJ
11631 | DNOM Component | Transformer | TF | input | REGULATORGROUP.NAME | Object name | String |  |  |  | DNMOBJ
11632 | DNOM Component | Transformer | TF | input | REGULATORGROUP.NUMTF | The number of transformers in the regulator group | Integer |  |  |  | REGULATORGROUP
11633 | DNOM Component | Transformer | TF |  | REGDIRFLAG | Bitmask for regulation direction | Integer
11634 | DNOM Component | Transformer | TF | input | REGEFFECTSIZE | Effective power rating of the transformer | Float
11635 | DNOM Component | Transformer | TF | Input | REGKVA | Rated capacity in kVA of associated transformer model for the transformer | Float
11636 | DNOM Component | Transformer | TF | input | REGLDCR | Regulating transformer line drop compensation resistance (V). | Float
11637 | DNOM Component | Transformer | TF | input | REGLDCX | Regulating transformer line drop compensation reactance (V). | Float
11638 | DNOM Component | Transformer | TF | Input | REGMARGIN | Regulation margin | Float
11639 | DNOM Component | Transformer | TF | Output | REGMARGINLIMIT | Tap increment with margin | Float
11640 | DNOM Component | Transformer | TF | input | REGMAXPOS | Regulating Tap Maximum Position | String
11641 | DNOM Component | Transformer | TF | input | REGMAXTAPKV | Regulating tap - maximum tap position in kV | Float |  | kV | kV
11642 | DNOM Component | Transformer | TF | input | REGMINPOS | Regulating Tap Minimum Position | String
11643 | DNOM Component | Transformer | TF | input | REGMINTAPKV | Regulating tap - minimum tap position in kV | Float |  | kV | kV
11644 | DNOM Component | Transformer | TF | input | REGNOMINALTAPKV | Regulating tap - nominal tap position in kV | Float |  | kV | kV
11645 | DNOM Component | Transformer | TF | input | REGNOMPOS | Regulating Tap Nominal Position | String
11646 | DNOM Component | Transformer | TF | input | REGPHASESENSED | Regulating transformer Phases Measured | String
11647 | DNOM Component | Transformer | TF | Input | REGPTRATIO | Regulator PT ratio | Float
11648 | DNOM Component | Transformer | TF | Input | REGPTVMEASLL | Flag indicating regulation voltage is measured line to line | Boolean
11649 | DNOM Component | Transformer | TF | input | REGSOURCEVOLT | Regulating transformer source voltage (line to line kV). | Float
11650 | DNOM Component | Transformer | TF | input | REGTAPID | Regulating tap changer ID | String
11651 | DNOM Component | Transformer | TF | input | REGTAPINCREMENT | Regulating Tap Step Increment | String
11652 | DNOM Component | Transformer | TF | input | REGTAPSIDE | Regulation tap position (Primary or secondary) | String
11653 | DNOM Component | Transformer | TF | input | REGTAPSTEPKV | Regulating tap - tap step size in kV | Float |  | kV | kV
11654 | DNOM Component | Transformer | TF | Input | REGTAPSTEPSIZE | Tap increment (in percent voltage) | Float
11655 | DNOM Component | Transformer | TF |  | REGTAPTYPE | Regulation tap type | String
11656 | DNOM Component | Transformer | TF | input | REGTARGETVOLT | Regulating transformer voltage target (per unit or configurable voltage base). | Float
11657 | DNOM Component | Transformer | TF | input | REGTIMEDELAY | Regulating transformer time delay (seconds). | Float
11658 | DNOM Component | Transformer | TF | input | REGULATIONMARGIN | Regulation margin. Default value: 0.5%, Range: [0 - 10] | Float
11659 | DNOM Component | Transformer | TF | input | REGULATORGROUP | Pointer to the associated regulator group | String
11660 | DNOM Component | Transformer | TF | input | REGVSETPNTDEADBAND | Regulation voltage setpoint deadband | String
11661 | DNOM Component | Transformer | TF | input | REGVTARGETKV | Regulating tap - voltage target in kV | Float |  | kV | kV
11662 | DNOM Component | Transformer | TF | input | REGVTARGETLDCCOMPKV | Regulating tap - voltatage target in kV considering Line Drop Compensation adjustment | Float |  | kV | kV
11663 | DNOM Component | Transformer | TF |  | ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer
11664 | DNOM Component | Transformer | TF | output | SCADAACTIVEDEMAND | Total measured real power load | String |  | MW | MW
11665 | DNOM Component | Transformer | TF |  | SCADALVMENABLED | SCADA LVM enabled | Boolean
11666 | DNOM Component | Transformer | TF | input | SECTAP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11667 | DNOM Component | Transformer | TF | input | SECTAP.BANDWITH | One sided bandwidth | Integer |  |  |  | TAPCHR
11668 | DNOM Component | Transformer | TF | input | SECTAP.CTRATIO | Regulator CT ratio - used to determine the per unit LDC R and X required by the power flow | Float |  |  |  | TAPCHR
11669 | DNOM Component | Transformer | TF | input | SECTAP.CTSECAMP | Regulator CT full load secondary amps (used to determine the per unit LDC R and X required by the power flow) | Float |  |  |  | TAPCHR
11670 | DNOM Component | Transformer | TF | input | SECTAP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11671 | DNOM Component | Transformer | TF | input | SECTAP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11672 | DNOM Component | Transformer | TF | input | SECTAP.ID | Object unique ID | String |  |  |  | DNMOBJ
11673 | DNOM Component | Transformer | TF | input | SECTAP.LDCCMPRV | Line drop compensation resistance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11674 | DNOM Component | Transformer | TF | input | SECTAP.LDCCMPXV | Line drop compensation reactance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11675 | DNOM Component | Transformer | TF | input | SECTAP.LDCCOMPR | Value for the line drop compensation resistance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11676 | DNOM Component | Transformer | TF | input | SECTAP.LDCCOMPX | Value for the line drop compensation reactance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11677 | DNOM Component | Transformer | TF | input | SECTAP.MANBANDWITH | Override value of voltage bandwidth | Integer |  |  |  | TAPCHR
11678 | DNOM Component | Transformer | TF | input | SECTAP.MANLDCCMPRV | Override value of line drop compensation resistance | Integer |  |  |  | TAPCHR
11679 | DNOM Component | Transformer | TF | input | SECTAP.MANLDCCMPXV | Override value of line drop compensation reactance | Integer |  |  |  | TAPCHR
11680 | DNOM Component | Transformer | TF | input | SECTAP.MANVTARGET | Override value of target voltage to regulate | Integer |  |  |  | TAPCHR
11681 | DNOM Component | Transformer | TF | input | SECTAP.NAME | Secondary tap name. | String |  |  |  | DNMOBJ
11682 | DNOM Component | Transformer | TF | input | SECTAP.NORMTAP | Normal tap ratio (mainly set for fixed taps) | Integer |  |  |  | TAPCHR
11683 | DNOM Component | Transformer | TF | input | SECTAP.NRMTPRAT | Fixed tap ratio value | Float |  |  |  | TAPCHR
11684 | DNOM Component | Transformer | TF | input | SECTAP.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | TAPCHR
11685 | DNOM Component | Transformer | TF | input | SECTAP.PTRATIO | Secondary tap (regulating) PT ratio. | Float |  |  |  | TAPCHR
11686 | DNOM Component | Transformer | TF | input | SECTAP.REVREG | Flag indicating that the regulator has reverse regulation capability | Boolean |  |  |  | TAPCHR
11687 | DNOM Component | Transformer | TF | input | SECTAP.TAPCNTRL | Tap control mode (0 - No tap control - for fixed tap, 1 - Remote only, 2 - Local only, 3 - Remote and local) | Enumeration |  |  |  | TAPCHR
11688 | DNOM Component | Transformer | TF | input | SECTAP.TAPEND | Transformer winding with movable tap (0 - Primary, 1 - Secondary, 2 - Tertiary) | Enumeration |  |  |  | TAPCHR
11689 | DNOM Component | Transformer | TF | input | SECTAP.TAPINIT | Initial tap position | Integer |  |  |  | TAPCHR
11690 | DNOM Component | Transformer | TF | input | SECTAP.TAPLDCRMANOVER | Flag indicating the nominal line drop compensation resistance override | Boolean |  |  |  | TAPCHR
11691 | DNOM Component | Transformer | TF | input | SECTAP.TAPLDCXMANOVER | Flag indicating the nominal line drop compensation reactance override | Boolean |  |  |  | TAPCHR
11692 | DNOM Component | Transformer | TF | input | SECTAP.TAPMANTAPCOSTOPT | Override value of scale cost for tap move | Integer |  |  |  | TAPCHR
11693 | DNOM Component | Transformer | TF | input | SECTAP.TAPMODE | Tap changer regulation mode (0 - No_Tap, 1 - Fixed, 2 - VoltageRegulation, 3 - VarRegulation) | Enumeration |  |  |  | TAPCHR
11694 | DNOM Component | Transformer | TF | input | SECTAP.TAPNOM | Nominal tap ratio (deterned as terminal voltage divided by the internal transformer voltage) | Float |  |  |  | TAPCHR
11695 | DNOM Component | Transformer | TF | input | SECTAP.TAPREDVALMANENABLE | A flag indicating the voltage reduction override | Boolean |  |  |  | TAPCHR
11696 | DNOM Component | Transformer | TF | input | SECTAP.TAPSTEP | Final (resulting) tap position | Integer |  |  |  | TAPCHR
11697 | DNOM Component | Transformer | TF | input | SECTAP.TAPTAPCOSTOPTMANENABLE | A flag indicating the scale cost for tap move override | Boolean |  |  |  | TAPCHR
11698 | DNOM Component | Transformer | TF | input | SECTAP.TAPVBWMANENABLE | Flag indicating the voltage bandwidth override | Boolean |  |  |  | TAPCHR
11699 | DNOM Component | Transformer | TF | input | SECTAP.TAPVTGMANENABLE | Flag indicating the voltage target override | Boolean |  |  |  | TAPCHR
11700 | DNOM Component | Transformer | TF | input | SECTAP.VTARGET | Target voltage to regulate | Float |  |  |  | TAPCHR
11701 | DNOM Component | Transformer | TF | input | SECTAP.VTARGMAX | Maximum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11702 | DNOM Component | Transformer | TF | input | SECTAP.VTARGMIN | Minimum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11703 | DNOM Component | Transformer | TF | output | SCADAPOWERFACTOR | Measured power factor | String
11704 | DNOM Component | Transformer | TF | output | SCADAREACTIVEDEMAND | Total measured reactive power load | String |  | MVAR | MVAR
11705 | DNOM Component | Transformer | TF | Output | SCTAPMANENABLE | Flag indicating the tap changer on the secondary side has manual overridden value | Boolean
11706 | DNOM Component | Transformer | TF | Output | SCTAPPOS | Secondary Side Tap Position | Integer
11707 | DNOM Component | Transformer | TF | output | SCTAPPOSITION | Secondary Side Tap Position | Integer | DPF | #N/A | #N/A
11708 | DNOM Component | Transformer | TF | input | SEC1GNDR | Secondary grounding branch resistance | Float
11709 | DNOM Component | Transformer | TF | input | SEC1GNDX | Secondary grounding branch reactance | Float
11710 | DNOM Component | Transformer | TF | input | SEC2GNDR | Tertiary grounding branch resistance | Float
11711 | DNOM Component | Transformer | TF | input | SEC2GNDX | Tertiary grounding branch reactance | Float
11712 | DNOM Component | Transformer | TF | input | SECBANDWTH | Secondary tap bandwidth (per unit or configurable voltage base) | Float
11713 | DNOM Component | Transformer | TF | input | SECCTRATIO | Secondary winding tap CT ratio. | Float
11714 | DNOM Component | Transformer | TF | Input | SECCTSECAMPRATING | Secondary tap CT amps | Float
11715 | DNOM Component | Transformer | TF | input | SECDEFASCREGULATIONON | Default value of Arc Suppression Coil regulation on status | Boolean
11716 | DNOM Component | Transformer | TF | input | SECHASARCSUPPRESSIONCOIL | Power transformer has an Arc Suppression Coil connected to it | Boolean
11717 | DNOM Component | Transformer | TF | input | SECLDCR | Secondary winding line drop compensation resistance (V). | Float
11718 | DNOM Component | Transformer | TF | input | SECLDCX | Secondary winding transformer line drop compensation reactance (V). | Float
11719 | DNOM Component | Transformer | TF | input | SECMAXTAPKV | Secondary tap - maximum tap position in kV | Float |  | kV | kV
11720 | DNOM Component | Transformer | TF | input | SERVCNTR.NAME | Service center name. | String
11721 | DNOM Component | Transformer | TF | input | SECMAXTAPPOS | Maximum tap position of the tap changer installed on the secondary winding | Integer
11722 | DNOM Component | Transformer | TF | input | SECMINTAPKV | Secondary tap - minimum tap position in kV | Float |  | kV | kV
11723 | DNOM Component | Transformer | TF | input | SECMINTAPPOS | Minimum tap position of the tap changer installed on the secondary winding | Integer
11724 | DNOM Component | Transformer | TF | input | SECNOMINALTAPKV | Secondary tap - nominal tap position in kV | Float |  | kV | kV
11725 | DNOM Component | Transformer | TF | input | SECNOMTAPPOS | Nominal tap position of the tap changer installed on the secondary winding | Integer
11726 | DNOM Component | Transformer | TF | input | SECNORMTAPPOS | Transformer secondary side tap normal position. The value is “--“ (null) for "Regulating" or "None" (no tap exists for the winding) tap changer types, or an integer between (or equal to) the minimum and maximum tap position for the "Fixed" tap changer type. | Integer
11727 | DNOM Component | Transformer | TF | input | SECPHASESENSED | Secondary winding Phases Measured | String
11728 | DNOM Component | Transformer | TF | Input | SECPTRATIO | Secondary winding PT ratio | Float
11729 | DNOM Component | Transformer | TF | Input | SECPTVMEASLL | Flag indicating regulation voltage is measured line to line for secondary winding (True = line to line) | Boolean
11730 | DNOM Component | Transformer | TF | input | SECTAP | Pointer to the secondary winding tap changer | String
11731 | DNOM Component | Transformer | TF |  | SECTAPBLOCK | Secondary tap blocked status | String
11732 | DNOM Component | Transformer | TF | input | SECTAPBLOCKSTATUS | Secondary tap blocked status with measurement quality | String
11733 | DNOM Component | Transformer | TF | input | SECTAPCONTROLMODE | Secondary tap control mode | String
11734 | DNOM Component | Transformer | TF | input | SECTAPCOST | Secondary tap switching cost | String
11735 | DNOM Component | Transformer | TF |  | SECTAPLOCALREMOTE | Secondary tap remote control status | String
11736 | DNOM Component | Transformer | TF |  | SECTAPMANREGULATIONON | Secondary tap regulation status | String
11737 | DNOM Component | Transformer | TF | input | SECTAPOPERMODE | Secondary tap operation mode | String
11738 | DNOM Component | Transformer | TF |  | SECTAPREGULATION | Secondary tap regulation status | String
11739 | DNOM Component | Transformer | TF | input | SECTAPSTEP | Tap step of the tap changer installed on the secondary winding (%) | Float
11740 | DNOM Component | Transformer | TF | input | SECTAPSTEPKV | Secondary tap - tap step size in kV | Float |  | kV | kV
11741 | DNOM Component | Transformer | TF | input | SECTARGETVOLT | Secondary tap voltage target (per unit or configurable voltage base). | Float
11742 | DNOM Component | Transformer | TF |  | SECTFREGTAPPOSSTATUS | Secondary TF regulating tap position status | String
11743 | DNOM Component | Transformer | TF |  | SECTFREGULATIONSTATUS | Secondary TF regulation status | String
11744 | DNOM Component | Transformer | TF |  | SECTFREMOTECONTROLSTATUS | Secondary TF remote control status | String
11745 | DNOM Component | Transformer | TF | input | SECTFVOLTREDUCTSTATUS | Voltage reduction status for the secondary winding. Measured value (Enable/Disable) | String
11746 | DNOM Component | Transformer | TF | input | SECVSETPNTDEADBAND | Secondary voltage setpoint deadband | String
11747 | DNOM Component | Transformer | TF | input | SECWIND | Secondary winding connection type | Integer
11748 | DNOM Component | Transformer | TF |  | STTAPINIT | Manually entered secondary side tap position value | String
11749 | DNOM Component | Transformer | TF | input | SUBTF | Flag indicating if the transformer is substation internal transformer | Boolean
11750 | DNOM Component | Transformer | TF | output | TAPBLOCK | Tap changer block status, blocked or Unblocked | String |  | #N/A | #N/A
11751 | DNOM Component | Transformer | TF | input | TAPBLOCKED | Regulating transformer blocked/unblocked status. | Boolean
11752 | DNOM Component | Transformer | TF |  | TAPBLOCKMEAS | Blocked/unblocked measurement status (Yes/No) | String
11753 | DNOM Component | Transformer | TF | Output | TAPBLOCKNETVIEWSTAT | Translate the flag that tap is blocked into TAPBLOCK and TAPUNBLOCK, as is used by netview | String
11754 | DNOM Component | Transformer | TF | input | TAPBLOCKSTATSTR | Blocked/unblocked status. (Yes/No) | String
11755 | DNOM Component | Transformer | TF | input | TAPBYPASSSTATSTR | regulator bypass switch status | String
11756 | DNOM Component | Transformer | TF | input | TAPCONTROLMODE | Regulating transformer tap control mode | String
11757 | DNOM Component | Transformer | TF | input | TAPDECSTEP | Tap Changer decrease Step Button Enabled (used on device toolbar) | String
11758 | DNOM Component | Transformer | TF | input | TAPDSOSCADA | DSO status is "SCADA decides" (used on device toolbar) | String
11759 | DNOM Component | Transformer | TF | input | TAPDSOUSEROFF | DSO status is "User Disabled" (used on device toolbar) | String
11760 | DNOM Component | Transformer | TF | input | TAPDSOUSERON | DSO status is "User enabled" (used on device toolbar) | String
11761 | DNOM Component | Transformer | TF | input | TAPENABLELOCALREMOTE | Tap changer is in remote or local mode (used on device toolbar) | Boolean
11762 | DNOM Component | Transformer | TF | Output | TAPEVALUATED | Flag indicating Heuristic LVM regulator is evaluated | Boolean
11763 | DNOM Component | Transformer | TF | input | TAPHASLOCAL | Flag indicating regulating transformer has local control capability. | Boolean
11764 | DNOM Component | Transformer | TF | input | TAPHASREMOTE | Indicates if the tap changer can be controlled remotely | String
11765 | DNOM Component | Transformer | TF | input | TAPINCSTEP | Tap Changer increase Step Button Enabled (used on device toolbar) | String
11766 | DNOM Component | Transformer | TF | input | TAPINIT | Initial tap position. | Integer
11767 | DNOM Component | Transformer | TF | input | TAPLDCRMANOVER | Flag indicating a manually entered line drop compensation resistance has been entered. | Boolean
11768 | DNOM Component | Transformer | TF | input | TAPLDCXMANOVER | Flag indicating a manually entered line drop compensation reactance has been entered. | Boolean
11769 | DNOM Component | Transformer | TF | output | TAPLOCALREMOTE | Tap changer control type (Remote or Local) | String
11770 | DNOM Component | Transformer | TF | input | TAPLOCALREMOTESTATSTR | Local/Remote Status (Local/Remote/Fixed) | String
11771 | DNOM Component | Transformer | TF | input | TAPMANBLOCKED | Manually entered blocked/unblocked status. | Boolean
11772 | DNOM Component | Transformer | TF | Output | TAPMANREGULATIONON | Flag indicating the tap changer on the transformer is on tertiary side | Boolean
11773 | DNOM Component | Transformer | TF | input | TAPMANSCADADSO | Flag indicating if the transformer regulating tap changer DSO status is "Scada decides" or not | Boolean
11774 | DNOM Component | Transformer | TF | input | TAPMANUSERDSODISABLED | DSO status is "User Disable" (used for manual entry) | String
11775 | DNOM Component | Transformer | TF | input | TAPMANUSERDSOENABLED | DSO status is "User Enable" (used for manual entry) | String
11776 | DNOM Component | Transformer | TF | input | TAPMANVREDCTON | Manually entered voltage reduction enabled status. | Boolean
11777 | DNOM Component | Transformer | TF | input | TAPOPERMODE | Current regulating transformer operation mode. | String
11778 | DNOM Component | Transformer | TF | input | TAPPOSITION | Regulation tap position | Integer
11779 | DNOM Component | Transformer | TF |  | TAPPOSSOURCE | Source of the tap position | String
11780 | DNOM Component | Transformer | TF | input | TAPREDVALMANENABLE | Flag indicating a manually entered voltage reduction value has been entered. | Boolean
11781 | DNOM Component | Transformer | TF | output | TAPREGULATION | Regulation Status, On" or "Off"" | String |  | #N/A | #N/A
11782 | DNOM Component | Transformer | TF |  | TAPREGULATIONMEAS | Regulation measurement status (Off/On) | String
11783 | DNOM Component | Transformer | TF |  | TERMSC2. | Phasing is stored with rotated phases
11784 | DNOM Component | Transformer | TF | input | TAPREGULATIONON | Tap changer regulation on/off status (used on device toolbar) | String
11785 | DNOM Component | Transformer | TF | input | TAPREGULATIONSTATSTR | Regulation status.(Off/On) | String
11786 | DNOM Component | Transformer | TF | input | TAPSCADADSO | Flag indicating if the transformer regulating tap changer DSO status is "Scada decides" or not | Boolean
11787 | DNOM Component | Transformer | TF | Output | TAPSELFORPLAN | Flag indicating Heuristic LVM plan is generated | Boolean
11788 | DNOM Component | Transformer | TF |  | TAPSUPERVISORYCUTOUTSTR | Tap supervisory cutout | String
11789 | DNOM Component | Transformer | TF | Output | TAPTOTVOLCHA | Total voltage change for Heuristic LVM Voltage Monitoring | Float
11790 | DNOM Component | Transformer | TF | Output | TAPTOTVOLVIO | Total voltage violation for Heuristic LVM Voltage Monitoring | Float
11791 | DNOM Component | Transformer | TF | input | TAPUSERDSODISABLED | DSO status is "User Disable" | String
11792 | DNOM Component | Transformer | TF | input | TAPUSERDSOENABLED | DSO status is "User Enable" | String
11793 | DNOM Component | Transformer | TF | input | TAPVBWMANENABLE | Flag indicating a manually entered voltage bandwidth value has been entered. | Boolean
11794 | DNOM Component | Transformer | TF | output | TAPVOLTRECDCT | Tap Changer Voltage reduction control flag, Enable or Disable | String |  | #N/A | #N/A
11795 | DNOM Component | Transformer | TF |  | TAPVOLTRECDCTMEAS | Regulating transformer voltage reduction measurement status (Off/On) | String
11796 | DNOM Component | Transformer | TF | input | TAPVOLTRECDCTSTATSTR | Regulating transformer voltage reduction enabled status. (Off/On) | String
11797 | DNOM Component | Transformer | TF | input | TAPVREDCTON | Regulating transformer voltage reduction enabled status. | Boolean
11798 | DNOM Component | Transformer | TF | input | TAPVREDUCTCAPABLE | Determine if the regulating transformer supports voltage reduction | Boolean
11799 | DNOM Component | Transformer | TF | input | TAPVTGMANENABLE | Flag indicating a manually entered voltage target has been entered. | Boolean
11800 | DNOM Component | Transformer | TF | input | TAPVVCELIGIBLE | Flag indicating regulating device is a candidate optimization device in LVM. | String
11801 | DNOM Component | Transformer | TF |  | TERABCWINDKVA | Phase ABC apparent power flow in kVA without angle on teritiary side | Float |  | kVA | kVA
11802 | DNOM Component | Transformer | TF | Output | TERAWINDKVA | phase A apparent power flow in kilo without angle on teritiary side | Float
11803 | DNOM Component | Transformer | TF | Output | TERAWINDKVAR | phase A reactive power flow in kilo without angle on teritiary side | Float
11804 | DNOM Component | Transformer | TF | Output | TERAWINDKW | phase A real power flow in kilo without angle on teritiary side | Float
11805 | DNOM Component | Transformer | TF | Output | TERBWINDKVA | phase B apparent power flow in kilo without angle on teritiary side | Float
11806 | DNOM Component | Transformer | TF | Output | TERBWINDKVAR | phase B reactive power flow in kilo without angle on teritiary side | Float
11807 | DNOM Component | Transformer | TF | Output | TERBWINDKW | phase B real power flow in kilo without angle on teritiary side | Float
11808 | DNOM Component | Transformer | TF | Output | TERCWINDKVA | phase C apparent power flow in kilo without angle on teritiary side | Float
11809 | DNOM Component | Transformer | TF | Output | TERCWINDKVAR | phase C reactive power flow in kilo without angle on teritiary side | Float
11810 | DNOM Component | Transformer | TF | Output | TERCWINDKW | phase C real power flow in kilo without angle on teritiary side | Float
11811 | DNOM Component | Transformer | TF | Input | TERNODE | Tertiary node name | String
11812 | DNOM Component | Transformer | TF | Output | TERNODEAMPA | phase A current with angle on teritiary side | String
11813 | DNOM Component | Transformer | TF | Output | TERNODEAMPB | phase B current with angle on teritiary side | String
11814 | DNOM Component | Transformer | TF | Output | TERNODEAMPC | phase C current with angle on teritiary side | String
11815 | DNOM Component | Transformer | TF | Output | TERNODEAMPN | phase N current with angle on teritiary side | String
11816 | DNOM Component | Transformer | TF | Output | TERNODEKVAR3PH | Sum of reactive power flow in kilo without angle of phase A,B,C on tertiary side | Float
11817 | DNOM Component | Transformer | TF | input | TETAP.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
11818 | DNOM Component | Transformer | TF | input | TETAP.BANDWITH | One sided bandwidth | Integer |  |  |  | TAPCHR
11819 | DNOM Component | Transformer | TF | input | TETAP.CTRATIO | Regulator CT ratio - used to determine the per unit LDC R and X required by the power flow | Float |  |  |  | TAPCHR
11820 | DNOM Component | Transformer | TF | input | TETAP.CTSECAMP | Regulator CT full load secondary amps (used to determine the per unit LDC R and X required by the power flow) | Float |  |  |  | TAPCHR
11821 | DNOM Component | Transformer | TF | input | TETAP.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
11822 | DNOM Component | Transformer | TF | input | TETAP.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
11823 | DNOM Component | Transformer | TF | input | TETAP.ID | Object unique ID | String |  |  |  | DNMOBJ
11824 | DNOM Component | Transformer | TF | input | TETAP.LDCCMPRV | Line drop compensation resistance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11825 | DNOM Component | Transformer | TF | input | TETAP.LDCCMPXV | Line drop compensation reactance (read in rom file and for display purposes) | Integer |  | Volts | Volts | TAPCHR
11826 | DNOM Component | Transformer | TF | input | TETAP.LDCCOMPR | Value for the line drop compensation resistance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11827 | DNOM Component | Transformer | TF | input | TETAP.LDCCOMPX | Value for the line drop compensation reactance (after preprocessing inside the Converter) | Integer |  | Ohms | Ohms | TAPCHR
11828 | DNOM Component | Transformer | TF | input | TETAP.MANBANDWITH | Override value of voltage bandwidth | Integer |  |  |  | TAPCHR
11829 | DNOM Component | Transformer | TF | input | TETAP.MANLDCCMPRV | Override value of line drop compensation resistance | Integer |  |  |  | TAPCHR
11830 | DNOM Component | Transformer | TF | input | TETAP.MANLDCCMPXV | Override value of line drop compensation reactance | Integer |  |  |  | TAPCHR
11831 | DNOM Component | Transformer | TF | input | TETAP.MANVTARGET | Override value of target voltage to regulate | Integer |  |  |  | TAPCHR
11832 | DNOM Component | Transformer | TF | input | TETAP.NAME | Tertiary tap name. | String |  |  |  | DNMOBJ
11833 | DNOM Component | Transformer | TF | input | TETAP.NORMTAP | Normal tap ratio (mainly set for fixed taps) | Integer |  |  |  | TAPCHR
11834 | DNOM Component | Transformer | TF | input | TETAP.NRMTPRAT | Fixed tap ratio value | Float |  |  |  | TAPCHR
11835 | DNOM Component | Transformer | TF | input | TETAP.PHSENSED | Regulation node phases that are sensed | Integer |  |  |  | TAPCHR
11836 | DNOM Component | Transformer | TF | input | TETAP.PTRATIO | Regulator PT ratio, used to determine the voltage target range (VMax and VMin) | Float |  |  |  | TAPCHR
11837 | DNOM Component | Transformer | TF | input | TETAP.REVREG | Flag indicating that the regulator has reverse regulation capability | Boolean |  |  |  | TAPCHR
11838 | DNOM Component | Transformer | TF | input | TETAP.TAPCNTRL | Tap control mode (0 - No tap control - for fixed tap, 1 - Remote only, 2 - Local only, 3 - Remote and local) | Enumeration |  |  |  | TAPCHR
11839 | DNOM Component | Transformer | TF | input | TETAP.TAPEND | Transformer winding with movable tap (0 - Primary, 1 - Secondary, 2 - Tertiary) | Enumeration |  |  |  | TAPCHR
11840 | DNOM Component | Transformer | TF | input | TETAP.TAPINIT | Initial tap position | Integer |  |  |  | TAPCHR
11841 | DNOM Component | Transformer | TF | input | TETAP.TAPLDCRMANOVER | Flag indicating the nominal line drop compensation resistance override | Boolean |  |  |  | TAPCHR
11842 | DNOM Component | Transformer | TF | input | TETAP.TAPLDCXMANOVER | Flag indicating the nominal line drop compensation reactance override | Boolean |  |  |  | TAPCHR
11843 | DNOM Component | Transformer | TF | input | TETAP.TAPMANTAPCOSTOPT | Override value of scale cost for tap move | Integer |  |  |  | TAPCHR
11844 | DNOM Component | Transformer | TF | input | TETAP.TAPMODE | Tap changer regulation mode (0 - No_Tap, 1 - Fixed, 2 - VoltageRegulation, 3 - VarRegulation) | Enumeration |  |  |  | TAPCHR
11845 | DNOM Component | Transformer | TF | input | TETAP.TAPNOM | Nominal tap ratio (deterned as terminal voltage divided by the internal transformer voltage) | Float |  |  |  | TAPCHR
11846 | DNOM Component | Transformer | TF | input | TETAP.TAPREDVALMANENABLE | A flag indicating the voltage reduction override | Boolean |  |  |  | TAPCHR
11847 | DNOM Component | Transformer | TF | input | TETAP.TAPSTEP | Final (resulting) tap position | Integer |  |  |  | TAPCHR
11848 | DNOM Component | Transformer | TF | input | TETAP.TAPTAPCOSTOPTMANENABLE | A flag indicating the scale cost for tap move override | Boolean |  |  |  | TAPCHR
11849 | DNOM Component | Transformer | TF | input | TETAP.TAPVBWMANENABLE | Flag indicating the voltage bandwidth override | Boolean |  |  |  | TAPCHR
11850 | DNOM Component | Transformer | TF | input | TETAP.TAPVTGMANENABLE | Flag indicating the voltage target override | Boolean |  |  |  | TAPCHR
11851 | DNOM Component | Transformer | TF | input | TETAP.VTARGET | Target voltage to regulate | Float |  |  |  | TAPCHR
11852 | DNOM Component | Transformer | TF | input | TETAP.VTARGMAX | Maximum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11853 | DNOM Component | Transformer | TF | input | TETAP.VTARGMIN | Minimum voltage target to regulate | Float |  | p.u. | p.u. | TAPCHR
11854 | DNOM Component | Transformer | TF | Output | TERNODEKW3PH | Sum of real power flow in kilo without angle of phase A,B,C on tertiary side | Float
11855 | DNOM Component | Transformer | TF | input | TERTAPCONTROLMODE | Tertiary tap control mode | String
11856 | DNOM Component | Transformer | TF | input | TERTBANDWTH | Tertiary tap bandwidth (per unit or configurable voltage base) | Float
11857 | DNOM Component | Transformer | TF | input | TERTCTRATIO | Tertiary winding tap CT ratio. | Float
11858 | DNOM Component | Transformer | TF | Input | TERTCTSECAMPRATING | Tertiary tap CT amps | Float
11859 | DNOM Component | Transformer | TF | input | TERTLDCR | Tertary winding line drop compensation resistance (V). | Float
11860 | DNOM Component | Transformer | TF | input | TERTLDCX | Tertary winding transformer line drop compensation reactance (V). | Float
11861 | DNOM Component | Transformer | TF | input | TERTMAXTAPKV | Tertiary tap - maximum tap position in kV | Float |  | kV | kV
11862 | DNOM Component | Transformer | TF | input | TERTMAXTAPPOS | Maximum tap position of the tap changer installed on the tertiary winding | Integer
11863 | DNOM Component | Transformer | TF | input | TERTMINTAPKV | Tertiary tap - minimum tap position in kV | Float |  | kV | kV
11864 | DNOM Component | Transformer | TF | input | TERTMINTAPPOS | Minimum tap position of the tap changer installed on the tertiary winding | Integer
11865 | DNOM Component | Transformer | TF | input | TERTNOMINALTAPKV | Tertiary tap - nominal tap position in kV | Float |  | kV | kV
11866 | DNOM Component | Transformer | TF | input | TERTNOMTAPPOS | Nominal tap position of the tap changer installed on the tertiary winding | Integer
11867 | DNOM Component | Transformer | TF | input | TERTNORMTAPPOS | Transformer tertiary side tap normal position. The value is “--“ (null) for "Regulating" or "None" (no tap exists for the winding) tap changer types, or an integer between (or equal to) the minimum and maximum tap position for the "Fixed" tap changer type. | Integer
11868 | DNOM Component | Transformer | TF | input | TERTPHASESENSED | Tertiary winding Phases Measured | String
11869 | DNOM Component | Transformer | TF | Input | TERTPTRATIO | Tertiary winding PT ratio | Float
11870 | DNOM Component | Transformer | TF | Input | TERTPTVMEASLL | Flag indicating regulation voltage is measured line to line for tertiary winding (True = line to line) | Boolean
11871 | DNOM Component | Transformer | TF |  | TERTTAPBLOCK | Tertiary tap blocked status | String
11872 | DNOM Component | Transformer | TF | input | TERTTAPCOST | Tertiary tap switching cost | String
11873 | DNOM Component | Transformer | TF |  | TERTTAPLOCALREMOTE | Tertiary tap remote control status | String
11874 | DNOM Component | Transformer | TF |  | TERTTAPMANREGULATIONON | Tertiary tap regulation status | String
11875 | DNOM Component | Transformer | TF |  | TERTTAPREGULATION | Tertiary tap regulation status | String
11876 | DNOM Component | Transformer | TF | input | TERTTAPSTEP | Tap step of the tap changer installed on the tertiary winding (%) | Float
11877 | DNOM Component | Transformer | TF | input | TERTTAPSTEPKV | Tertiary tap - tap step size in kV | Float |  | kV | kV
11878 | DNOM Component | Transformer | TF | input | TERTTARGETVOLT | Tertiary tap voltage target (per unit or configurable voltage base). | Float
11879 | DNOM Component | Transformer | TF | input | TERTVSETPNTDEADBAND | Tertiary voltage setpoint deadband | String
11880 | DNOM Component | Transformer | TF | input | TERTWIND | Tertiary winding connection type | Integer
11881 | DNOM Component | Transformer | TF | input | TETAP | Pointer to the tertiary winding tap changer | String
11882 | DNOM Component | Transformer | TF |  | TETAPINIT | Manually entered tertiary side tap position value | String
11883 | DNOM Component | Transformer | TF | Output | TETAPMANENABLE | Flag indicating the tap changer on the tertiary side has manual overridden value | Boolean
11884 | DNOM Component | Transformer | TF | Output | TETAPPOSITION | Tertiary Side Tap Position | Integer
11885 | DNOM Component | Transformer | TF | input | TFASCCURRENTREGULATIONSTATUS | The current value of the Arc Suppression Coil (ASC) Regulation On status (true = enabled and false = disabled) | Boolean
11886 | DNOM Component | Transformer | TF | input | TFASCREGULATION | The default value of the Arc Suppression Coil (ASC) Regulation On status (true = enabled and false = disabled) | Boolean
11887 | DNOM Component | Transformer | TF | input | TFASCREGULATIONCAPABLE | Specifies whether the ASC Regulation On status is regulation-capable | Boolean
11888 | DNOM Component | Transformer | TF | output | TFBACKFEEDVIOLATION | The number of power transformer backfeeds | Integer | DPF
11889 | DNOM Component | Transformer | TF | input | TFCONSOPERATEMIN | TF consequent operation in minutes | String
11890 | DNOM Component | Transformer | TF | Input | TFDEVICETYPE | Flag indicating the transformer is regulator | String |  | #N/A | #N/A
11891 | DNOM Component | Transformer | TF | input | TFDYNFEEDERS | IDs of feeders connected to the transformer | String
11892 | DNOM Component | Transformer | TF | input | TFFSDELIGIBLE | Specifies whether the transformer is eligible for the FSD application (the transformer must have an arc suppression coil fault indicator connected) | Boolean
11893 | DNOM Component | Transformer | TF |  | TFHASREGMODE | String indicating if a transformer has an active advanced regulation mode. | String
11894 | DNOM Component | Transformer | TF | output | TFHASREGULATINGTAP | Has regulating tap changer | Boolean |  | #N/A | #N/A
11895 | DNOM Component | Transformer | TF | Output | TFINITPOS | Initial tap position for delayed move | Integer
11896 | DNOM Component | Transformer | TF | input | TFISREGULATOR | Flag indicating if the transformer is a regulator | Boolean
11897 | DNOM Component | Transformer | TF | Output | TFKVARLOSS | Reactive power of transformer loss (core loss and copper loss) | Float
11898 | DNOM Component | Transformer | TF | Output | TFKWLOSS | Real power of transformer loss (core loss and copper loss) | Float
11899 | DNOM Component | Transformer | TF | input | TFLOADED | Connected load flag | Boolean
11900 | DNOM Component | Transformer | TF | input | TFMANASCREGULATION | The ASC Regulation On status manual override value | Boolean
11901 | DNOM Component | Transformer | TF | input | TFMANASCREGULATIONENABLE | Specifies whether the ASC Regulation On status is manually overriden | Boolean
11902 | DNOM Component | Transformer | TF | input | TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean
11903 | DNOM Component | Transformer | TF | input | TFMASK | All booleans will be combined into a single mask | Integer
11904 | DNOM Component | Transformer | TF | input | TFMODELUNITS | Rating units | String
11905 | DNOM Component | Transformer | TF | Output | TFMOVCREATETIME | The creation time for delayed move | String
11906 | DNOM Component | Transformer | TF | Output | TFMOVCREATETIME_TICKS | The creation time for delayed move in ticks count | Integer
11907 | DNOM Component | Transformer | TF | Output | TFMOVEEXPIRATIONTIME | The expiration time for delayed move | String
11908 | DNOM Component | Transformer | TF | Output | TFMOVEEXPIRATIONTIME_TICKS | The expiration time for delayed move in ticks count | Integer
11909 | DNOM Component | Transformer | TF | input | TFNSFAULTSTATUS | The arc suppression coil fault status. Measured value. | String
11910 | DNOM Component | Transformer | TF | output | TFPF | transformer power factor for primary side | Float | DPF | #N/A | #N/A
11911 | DNOM Component | Transformer | TF | Input | TFPRIMGNDRX | grounding impedances on primary winding | String
11912 | DNOM Component | Transformer | TF | input | TFPRIMWINDTYPE | Primary Winding Type. (Delta/Wye/Open Delta/Open Wye) | String
11913 | DNOM Component | Transformer | TF | input | TFPRITAPID | Source Side Tap Changer ID | String
11914 | DNOM Component | Transformer | TF | Output | TFPRITAPTYPE | Primary Side Tap Changer Type | String
11915 | DNOM Component | Transformer | TF | input | TFRATINGUNIT | transformer rated value and unit | String
11916 | DNOM Component | Transformer | TF | Output | TFRECOMMPOS | Recommended tap position for delayed move | Integer
11917 | DNOM Component | Transformer | TF | Output | TFREGCONTROLDEFINITIONID | The ID of a Regulator Control Definition object defined in the RegulatorControl.csv file. This field is optional. | String
11918 | DNOM Component | Transformer | TF |  | TFREGMODE1 | The first regulation mode defined in the regulation control definition. | String
11919 | DNOM Component | Transformer | TF |  | TFREGMODE2 | The second regulation mode defined in the regulation control definition. | String
11920 | DNOM Component | Transformer | TF |  | TFREGMODE3 | The third regulation mode defined in the regulation control definition. | String
11921 | DNOM Component | Transformer | TF |  | TFREGMODE4 | The fourth regulation mode defined in the regulation control definition. | String
11922 | DNOM Component | Transformer | TF |  | TFREGMODE5 | The fifth regulation mode defined in the regulation control definition. | String
11923 | DNOM Component | Transformer | TF |  | TFREGMODE6 | The sixth regulation mode defined in the regulation control definition. | String
11924 | DNOM Component | Transformer | TF | input | TFREGMODEDIRECTION | Active advanced regulation direction | String
11925 | DNOM Component | Transformer | TF |  | TFREGMODEFLDCR | The LDC resistance for forward regulation. | String
11926 | DNOM Component | Transformer | TF |  | TFREGMODEFLDCX | The LDC reactance for forward regulation. | String
11927 | DNOM Component | Transformer | TF | input | TFREGMODEFLOWDIRECTION | Flow direction on regulator with advanced regulation. | String
11928 | DNOM Component | Transformer | TF |  | TFREGMODEFNAME | The name of the forward regulation mode. | String
11929 | DNOM Component | Transformer | TF |  | TFREGMODEFSIDE | The side of the transformer used in forward regulation. | String
11930 | DNOM Component | Transformer | TF | input | TFREGMODEFTHRESH | Regulation mode current threshold primary | String |  | Amps | Amps
11931 | DNOM Component | Transformer | TF |  | TFREGMODEFV1 | The level 1 voltage target for forward regulation. | String
11932 | DNOM Component | Transformer | TF |  | TFREGMODEFV2 | The level 2 voltage target for forward regulation. | String
11933 | DNOM Component | Transformer | TF |  | TFREGMODEFV3 | The level 3 voltage target for forward regulation. | String
11934 | DNOM Component | Transformer | TF |  | TFREGMODEFVBANDWIDTH | The voltage regulation bandwidth for forward regulation. | String
11935 | DNOM Component | Transformer | TF |  | TFREGMODEFVREDCAP | The reverse voltage reduction capability status. | String
11936 | DNOM Component | Transformer | TF |  | TFREGMODEFVTARGET | The voltage target for forward regulation. | String
11937 | DNOM Component | Transformer | TF |  | TFREGMODEHASSCADA | String indicating if a transformer has a regulation mode SCADA measurement. | String
11938 | DNOM Component | Transformer | TF |  | TFREGMODEISREACFLOW | String indicating if a transforemr is can sense reactive flow. | String
11939 | DNOM Component | Transformer | TF |  | TFREGMODEMANCAPABLE | String indicating if a transformer is able to accept a manually entered regulation mode. | String
11940 | DNOM Component | Transformer | TF |  | TFREGMODEMANVALUE | The manually entered regulation mode value. | String
11941 | DNOM Component | Transformer | TF |  | TFREGMODENAME | The name of the active regulation mode. | String
11942 | DNOM Component | Transformer | TF |  | TFREGMODENOMINAL | The nominal regulation mode (measured value if valid, otherwise default value). | String
11943 | DNOM Component | Transformer | TF | input | TFREGMODEREACTFLOWSENSE | Flow direction sense | String
11944 | DNOM Component | Transformer | TF |  | TFREGMODERLDCR | The LDC resistance for reverse regulation. | String
11945 | DNOM Component | Transformer | TF |  | TFREGMODERLDCX | The LDC reactance for reverse regulation. | String
11946 | DNOM Component | Transformer | TF |  | TFREGMODERNAME | The name of the reverse regulation mode. | String
11947 | DNOM Component | Transformer | TF |  | TFREGMODERSIDE | The side of the transformer used in reverse regulation. | String
11948 | DNOM Component | Transformer | TF | input | TFREGMODERTHRESH | Regulation mode current threshold secondary | String |  | Amps | Amps
11949 | DNOM Component | Transformer | TF |  | TFREGMODERV1 | The level 1 voltage target for reverse regulation. | String
11950 | DNOM Component | Transformer | TF |  | TFREGMODERV2 | The level 2 voltage target for reverse regulation. | String
11951 | DNOM Component | Transformer | TF |  | TFREGMODERV3 | The level 3 voltage target for reverse regulation. | String
11952 | DNOM Component | Transformer | TF |  | TFREGMODERVBANDWIDTH | The voltage regulation bandwidth for reverse regulation. | String
11953 | DNOM Component | Transformer | TF |  | TFREGMODERVREDCAP | The forward voltage reduction capability status. | String
11954 | DNOM Component | Transformer | TF |  | TFREGMODERVTARGET | The voltage target for reverse regulation. | String
11955 | DNOM Component | Transformer | TF |  | TFREGMODESCADA | The SCADA measurement for regulation mode. | String
11956 | DNOM Component | Transformer | TF |  | TFREGMODEUSEMAN | String indicating if the manual value should be used for determining active regulation mode. | String
11957 | DNOM Component | Transformer | TF | input | TFREGTAPPOSSTATUS | Regulating tap position. Measured value | Integer
11958 | DNOM Component | Transformer | TF | input | TFREGULATIONSTATUS | Auto/Manual control type. Measured value. | String
11959 | DNOM Component | Transformer | TF |  | TFREGVOLTBASE | Advanced Regulation Voltage Base | String
11960 | DNOM Component | Transformer | TF | input | TFREMOTECONTROLSTATUS | Local/Remote control type. Measured value. | String
11961 | DNOM Component | Transformer | TF | Output | TFSCHEDULEDMOVEDELAYTIME | The minimum required delay time for delayed move | String
11962 | DNOM Component | Transformer | TF | Input | TFSEC1GNDRX | grounding impedances on secondary winding | String
11963 | DNOM Component | Transformer | TF | Input | TFSEC2GNDRX | grounding impedances on tertiary winding | String
11964 | DNOM Component | Transformer | TF | output | TFSECPF | transformer power factor for secondary side | Float | DPF | #N/A | #N/A
11965 | DNOM Component | Transformer | TF | input | TFSECTAPID | Secondary Side Tap Changer ID | String
11966 | DNOM Component | Transformer | TF | Output | TFSECTAPTYPE | Secondary Side Changer Type | String
11967 | DNOM Component | Transformer | TF | output | TFSECVA3PH | Apparent power of secondary side of transformer | Float | DPF | KVA or MVA | KVA or MVA
11968 | DNOM Component | Transformer | TF | output | TFSECVAR3PH | Reactive power of secondary side of transformer | Float | DPF | kVAR or MVAR | kVAR or MVAR
11969 | DNOM Component | Transformer | TF | output | TFSECWATT3PH | Real power of secondary side of transformer | Float | DPF | kW or MW | kW or MW
11970 | DNOM Component | Transformer | TF | input | TFSECWINDTYPE | Secondary Winding Type (Delta/Wye/Open Delta/Open Wye) | String
11971 | DNOM Component | Transformer | TF | Input | TFSUBNAME | The name of station that owns the transformer | String
11972 | DNOM Component | Transformer | TF | Input | TFTERTAPID | Tertiary Side Tap Changer ID | String
11973 | DNOM Component | Transformer | TF | Output | TFTERTAPTYPE | Tertiary Side Changer Type | String
11974 | DNOM Component | Transformer | TF |  | TFTERTPF | Transformer power factor for tertiary side | Float
11975 | DNOM Component | Transformer | TF |  | TFTERTVA3PH | Apparent power of tertiary side of transformer | Float
11976 | DNOM Component | Transformer | TF |  | TFTERTVAR3PH | Reactive power of tertiary side of transformer | Float
11977 | DNOM Component | Transformer | TF |  | TFTERTWATT3PH | Real power of tertiary side of transformer | Float
11978 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.ID | ID of the schedule | String |  |  |  | DNMOBJ
11979 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
11980 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
11981 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
11982 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
11983 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
11984 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
11985 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
11986 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
11987 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
11988 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
11989 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.YUNITONE | Y1 axis units | String |  |  |  | SCHED
11990 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
11991 | DNOM Component | Transformer | TF | input | TFTERTWINDTYPE | Tertiary Winding Type (Delta/Wye/Open Delta/Open Wye) | String
11992 | DNOM Component | Transformer | TF | input | USRVTLV2.COLORVLT | Associated color used for display purposes | String |  |  |  | UVLTLV
11993 | DNOM Component | Transformer | TF | input | USRVTLV2.DISTVLTL | Flag indicating that the voltage level represents a distribution voltage level (true - distribution, false - transmission) | String |  |  |  | UVLTLV
11994 | DNOM Component | Transformer | TF | input | USRVTLV2.ID | ID of the user voltage level | String |  |  |  | DNMOBJ
11995 | DNOM Component | Transformer | TF | input | USRVTLV2.KVLLVVAL | Voltage level (line to line) | String |  | kV | kV | UVLTLV
11996 | DNOM Component | Transformer | TF | Output | TFTERVANA | phase A voltage with angle on teritiary side | String
11997 | DNOM Component | Transformer | TF | Output | TFTERVANALG | phase A LG voltage with angle on teritiary side | String
11998 | DNOM Component | Transformer | TF | Output | TFTERVANALL | phase A LL voltage with angle on teritiary side | String
11999 | DNOM Component | Transformer | TF | Output | TFTERVANB | phase B voltage with angle on teritiary side | String
12000 | DNOM Component | Transformer | TF | Output | TFTERVANBLG | phase B LG voltage with angle on teritiary side | String
12001 | DNOM Component | Transformer | TF | Output | TFTERVANBLL | phase B LL voltage with angle on teritiary side | String
12002 | DNOM Component | Transformer | TF | Output | TFTERVANC | phase C voltage with angle on teritiary side | String
12003 | DNOM Component | Transformer | TF | Output | TFTERVANCLG | phase C LG voltage with angle on teritiary side | String
12004 | DNOM Component | Transformer | TF | Output | TFTERVANCLL | phase C LL voltage with angle on teritiary side | String
12005 | DNOM Component | Transformer | TF | Output | TFTERVANN | phase N voltage with angle on teritiary side | String
12006 | DNOM Component | Transformer | TF | Output | TFTERVANNLG | phase N LG voltage with angle on teritiary side | String
12007 | DNOM Component | Transformer | TF | Output | TFTERVANNLL | phase N LL voltage with angle on teritiary side | String
12008 | DNOM Component | Transformer | TF | Input | TFTERVNOMLL | line to line rated voltage(kV) and line to ground voltage(kV) on tertiary side | String
12009 | DNOM Component | Transformer | TF | Input | TFTIMEDELAYSCHEDULE | Time delay schedule name | String
12010 | DNOM Component | Transformer | TF | Output | TFTIMEELAPSED | The time elapsed since delayed tap move is created | String
12011 | DNOM Component | Transformer | TF | input | TFTIMELASTOPERATE | Date and time of the last operation | String
12012 | DNOM Component | Transformer | TF | input | TFTIMELASTOPERATE_TICKS | Date and time of the last operation in ticks | String
12013 | DNOM Component | Transformer | TF | output | TFVA3PH | Total apparent power (in KVA or MVA) of Three Phases | String |  | kVA or MVA | kVA or MVA
12014 | DNOM Component | Transformer | TF | output | TFVAR3PH | Total reactive power of Three Phases (in kW or MW) | String | DPF | kW or MW | kW or MW
12015 | DNOM Component | Transformer | TF |  | TFVOLTDROPEXCEEDED | Flag indicating that the voltage drop of the transformer exceeds the limit | Integer
12016 | DNOM Component | Transformer | TF | Input | TFVOLTIMBMANLIMIT | Manual voltage imbalance limit, in percentage | Float
12017 | DNOM Component | Transformer | TF | input | TFVOLTREDUCTSTATUS | Voltage reduction status. Measured value (Enable/Disable) | String
12018 | DNOM Component | Transformer | TF | Input | TFVOLTREGUNIT | Tap changer voltage units of associated transformer model | String
12019 | DNOM Component | Transformer | TF |  | TFVOLTTARGETMANCAPABLE | String indicating if a transformer is able to accept a manually entered voltage target. | String
12020 | DNOM Component | Transformer | TF | Output | TFWAITTIME | The time elapsed since delayed tap move is created and delayed | String
12021 | DNOM Component | Transformer | TF | output | TFWATT3PH | Total real power of Three Phases (in kW or MW) | String | DPF | kW or MW | kW or MW
12022 | DNOM Component | Transformer | TF | input | TIMEDELAYSCHEDULE | Pointer to the time delay schedule (for heuristic LVM) | String
12023 | DNOM Component | Transformer | TF | input | USRVTLV2 | Pointer to the assigned secondary voltage level | String
12024 | DNOM Component | Transformer | TF | Output | VOLTIMBLANCE | voltage imbalance in percent | Float
12025 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12026 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12027 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12028 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
12029 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12030 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.NAME | Name of the object | String |  |  |  | DNMOBJ
12031 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12032 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12033 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12034 | DNOM Component | Transformer | TF | Output | VOLTIMBLANCELIMIT | voltage imbalance limit in percent | Float
12035 | DNOM Component | Transformer | TF | input | VOLTPR | Primary voltage (kV line to ground). | Float
12036 | DNOM Component | Transformer | TF | input | VOLTREDBWCOMPENSATEFLAG | TF has voltage bandwidth reduction compensated? | Boolean
12037 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12038 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12039 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12040 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12041 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.NAME | Name of the object | String |  |  |  | DNMOBJ
12042 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK.NUMTF | The number of single-phase transformers in the bank. | Integer |  |  |  | TFBNK
12043 | DNOM Component | Transformer | TF | input | VOLTSC | Secondary voltage (kV line to ground). | Float
12044 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12045 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
12046 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | TF
12047 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean |  |  |  | TF
12048 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer |  |  |  | TF
12049 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12050 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12051 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | TF
12052 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | TF
12053 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float |  |  |  | TF
12054 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
12055 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | TF
12056 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | TF
12057 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.GROUNDTE | Tertiary grounded flag | Boolean |  |  |  | TF
12058 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12059 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.LVMPROFORMINDEX | LVM problem formulation index | Integer |  |  |  | TF
12060 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer |  |  |  | TF
12061 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  |  |  | TF
12062 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.NAME | Name of the object | String |  |  |  | DNMOBJ
12063 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12064 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12065 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.NOMCCUST | The number of nominally connected customers | Integer |  |  |  | TF
12066 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12067 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.PRIMGNDR | Primary grounding branch resistance | Float |  | Ohms | Ohms | TF
12068 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.PRIMGNDX | Primary grounding branch reactance | Float |  | Ohms | Ohms | TF
12069 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.PRIMWIND | Primary winding connection type | Integer |  |  |  | TF
12070 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.REGULATIONMARGIN | Regulation margin | Float |  |  |  | TF
12071 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | TF
12072 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.SEC1GNDR | Secondary grounding branch resistance | Float |  | Ohms | Ohms | TF
12073 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.SEC1GNDX | Secondary grounding branch reactance | Float |  | Ohms | Ohms | TF
12074 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.SEC2GNDR | Tertiary grounding branch resistance | Float |  | Ohms | Ohms | TF
12075 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.SEC2GNDX | Tertiary grounding branch reactance | Float |  | Ohms | Ohms | TF
12076 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.SECWIND | Secondary winding connection type | Integer |  |  |  | TF
12077 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.TERTWIND | Tertiary winding connection type | Integer |  |  |  | TF
12078 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.TFLOADED | Connected load flag | Boolean |  |  |  | TF
12079 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean |  |  |  | TF
12080 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | TF
12081 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.VOLTPR | Primary voltage (kV line to ground) | Float |  | kV | kV | TF
12082 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.VOLTSC | Secondary voltage (kV line to ground) | Float |  | kV | kV | TF
12083 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF.VOLTTE | Tertiary voltage (kV line to ground) | Float |  | kV | kV | TF
12084 | DNOM Component | Transformer | TF |  | VOLTTE | Tertiary voltage (in kV l-n) | Float |  | kV | kV
12085 | DNOM Component | Transformer | TF | Input | VOLTTERLEVEL | Nominal Voltage level (line to line and line to ground) | String
12086 | DNOM Component | Transformer | TF | input | VREDVAL | Regulating tap voltage reduction value (per unit or configurable voltage base). | Float
12087 | DNOM Component | Transformer | TF | input | VTARGET | Regulating transformer voltage target (per unit or configurable voltage base). | Float
12088 | DNOM Component | Transformer | TF | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
12089 | DNOM Component | Transformer | TF | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
12090 | DNOM Component | Transformer | TF | input | SELFPROTECTION | The value returned is binary equivalent of transformer self protection schemes. Example: If we set protection to Differential-Transformer, Other and query for SELFPROTECTION a value of 514 is returned.Binary representation of 514 is 1000000010 which indicates transformer self-protection types 1 and 9 are selected. Comma-separated list of integer values of the transformer self-protection types. Supported types are: None = 0 Differential - Transformer = 1 Differential - Bus = 2 Restricted Earth Fault (REF) = 3 Buchholz = 4 Distance = 5 Tank Earth = 6 Overfluxing = 7 Thermal = 8 Other = 9 | String |  | #N/A | #N/A | #N/A
12091 | DNOM Component | Transformer | TF | input | TFSELFPROTECTIONSCHEME | Comma-separated list of values of the transformer self-protection types. Supported types are: - None - Differential - Transformer - Differential - Bus - Restricted Earth Fault (REF) - Buchholz - Distance - Tank Earth - Overfluxing - Thermal - Other | String
12092 | DNOM Component | Transformer | TF | input | SECHASARCSUPPRESSIONCOIL | Specifies whether the Arc Suppression Coil (ASC) fault indicator is connected to the secondary side of the power transformer. | Boolean
12093 | DNOM Component | Transformer Bank | TFBNK | output | AGGREGATIONACTIVEDEMANDHIGHLOW | Total DPF calculated real power demand at the source side (primary) and at the load side (secondary) | String | DPF | MW | MW
12094 | DNOM Component | Transformer Bank | TFBNK | input | AREAIND | Integer (index) into station permission area list. | Integer
12095 | DNOM Component | Transformer Bank | TFBNK | output | AVRAGEVOLTAGEMEASAMPWEIGHTALLBUS | Weighted measured average voltage in per unit. Only station MV buses are accounted. The weighting factor is the measured current value on the same bus. | Float | DPF | p.u. | p.u.
12096 | DNOM Component | Transformer Bank | TFBNK | input | BANKSUBNAME | Power transformer bank substation name | String
12097 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.AENDDT | Season end date | String |  |  |  | SEASON
12098 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12099 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.ASTARTDT | Season start date | String |  |  |  | SEASON
12100 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.DESCRIPT | Season description | String |  |  |  | SEASON
12101 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.ID | Season unique ID | String |  |  |  | DNMOBJ
12102 | Global Object | Transformer Model | TFMOD | input | LIMSEAS.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
12103 | DNOM Component | Transformer Bank | TFBNK | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12104 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.AENDDT | Season end date | String |  |  |  | SEASON
12105 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12106 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.ASTARTDT | Season start date | String |  |  |  | SEASON
12107 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.DESCRIPT | Season description | String |  |  |  | SEASON
12108 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.ID | Season unique ID | String |  |  |  | DNMOBJ
12109 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
12110 | DNOM Component | Transformer Bank | TFBNK | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12111 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.AENDDT | Season end date | String |  |  |  | SEASON
12112 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12113 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.ASTARTDT | Season start date | String |  |  |  | SEASON
12114 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.DESCRIPT | Season description | String |  |  |  | SEASON
12115 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.ID | Season unique ID | String |  |  |  | DNMOBJ
12116 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER.iNumDateRanges | The number of date ranges for the season (given in month/day format) | Integer |  |  |  | SEASON
12117 | DNOM Component | Transformer Bank | TFBNK | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12118 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.ID | ID of the schedule | String |  |  |  | DNMOBJ
12119 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
12120 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
12121 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
12122 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
12123 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
12124 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
12125 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
12126 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
12127 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
12128 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
12129 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.YUNITONE | Y1 axis units | String |  |  |  | SCHED
12130 | Global Object | Transformer Model | TFMOD | input | LIMTEMP.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
12131 | DNOM Component | Transformer Bank | TFBNK | input | ISBANKEDPWRTF | Specifies whether the transformer bank includes banked power transformers | Boolean
12132 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.ID | ID of the schedule | String |  |  |  | DNMOBJ
12133 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
12134 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
12135 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
12136 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
12137 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
12138 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
12139 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
12140 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
12141 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
12142 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
12143 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.YUNITONE | Y1 axis units | String |  |  |  | SCHED
12144 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
12145 | DNOM Component | Transformer Bank | TFBNK | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
12146 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.ID | ID of the schedule | String |  |  |  | DNMOBJ
12147 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.LINEAR | Enumerated value indicating how the associated schedule points are connected. The enumeration has two values: 1 = Linear (connect the points together with straight lines), 2 = Step (a horizontal line is drawn for each point). | Integer |  |  |  | SCHED
12148 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.NORMALIZED | Flag indicating if the Y1 and Y2 data points in the schedule are on a normalized 0.0 to 1.0 scale | Boolean |  |  |  | SCHED
12149 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.NUMSKPNT | Number of schedule points | Integer |  |  |  | SCHED
12150 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.PAVERAGE | Load average (real power) value | Float |  |  |  | SCHED
12151 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.PEAKLOAD | Flag indicating that a schedule represents a peak schedule (for a load schedule only) | Boolean |  |  |  | SCHED
12152 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.QAVERAGE | Load average (reactive power) value | Float |  |  |  | SCHED
12153 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.SCHEDULETYPE | Schedule type, such as Load-to-Voltage Dependency. | String |  |  |  | SCHED
12154 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.SKEDTYPE | Enumerated schedule type, as defined in the ScheduleType entry in the CodedTranslationConfig.xml | Integer |  |  |  | SCHED
12155 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.XUNITS | X axis units (hours for a load schedule) | String |  |  |  | SCHED
12156 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.YAXTYPE | Type of value on y axis (real power, reactive power, or power factor for a load schedule) | String |  |  |  | SCHED
12157 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.YUNITONE | Y1 axis units | String |  |  |  | SCHED
12158 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER.YUNITTWO | Y2 axis units | String |  |  |  | SCHED
12159 | DNOM Component | Transformer Bank | TFBNK | input | NAME | Object name | String |  |  |  | DNMOBJ
12160 | DNOM Component | Transformer Bank | TFBNK | input | NUMTF | The number of single-phase transformers in the bank. | Integer
12161 | DNOM Component | Transformer Bank | TFBNK | input | PERMITAREAIDS | Permit area IDs of transformers in the TF bank | String
12162 | DNOM Component | Transformer Bank | TFBNK | input | PWRTFBANKID | Power transformer bank ID | String
12163 | DNOM Component | Transformer Bank | TFBNK | input | PWRTFBANKNAME | Power transformer bank name | String
12164 | DNOM Component | Transformer Bank | TFBNK | input | TFIDSINBANK | IDs of transformers in the TF bank | String
12165 | DNOM Component | Transformer Bank | TFBNK | input | TFINBANK | Dynamic array of transformer pointers | String
12166 | DNOM Component | Transformer Bank | TFBNK | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
12167 | DNOM Component | Transformer Bank | TFBNK | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
12168 | DNOM Component Placement | Transformer Bank Placement | TFBPLE | input | TFBANK | Pointer to the associated transformer bank | String
12169 | DNOM Component Placement | Transformer Label Placement | TFLBPL | input | TF | Pointer to the associated transformer | String
12170 | Global Object | Transformer Model | TFMOD |  | BANKCODE | Transformer bank code | String
12171 | Global Object | Transformer Model | TFMOD |  | CNSTTYPE | Configuration type (overhead, underground, padmount, others) | Integer
12172 | Global Object | Transformer Model | TFMOD |  | CYCREACT | CYC matrix elements - reactive portion | Integer
12173 | Global Object | Transformer Model | TFMOD | input | SELFPROTECTION | Comma-separated list of integer values of the transformer self-protection types None = 0 Differential - Transformer = 1 Differential - Bus = 2 Restricted Earth Fault (REF) = 3 Buchholz = 4 Distance = 5 Tank Earth = 6 Overfluxing = 7 Thermal = 8 Other = 9 | String |  | #N/A | #N/A | #N/A
12174 | Global Object | Transformer Model | TFMOD |  | CYCREAL | CYC matrix elements - real portion | Integer
12175 | Global Object | Transformer Model | TFMOD |  | DMSTYPE | Enumerated transformer type. The following values are used: 1 = Secondary transformer, 2 = Voltage regulator, 3 = Power transformer, 4 = Auto-transformer, 5 = Step Up/Down transformer, 6 = Zigzag transformer. | Integer
12176 | Global Object | Transformer Model | TFMOD |  | EXCITEPF | Magnetization power factor (optional if percent excitation current is provided). | Float
12177 | Global Object | Transformer Model | TFMOD |  | EXCTEAMP | Average percent excitation current (optional if the magnetizing power factor is provided). | Float
12178 | Global Object | Transformer Model | TFMOD | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12179 | Global Object | Transformer Model | TFMOD |  | LIMITEVENT | A flag indicating operational limit event | Boolean
12180 | Global Object | Transformer Model | TFMOD |  | LIMITEVENTSEC | A flag indicating secondary operational limit event | Boolean
12181 | Global Object | Transformer Model | TFMOD |  | LIMITEVENTTER | A flag indicating tertiary operational limit event | Boolean
12182 | Global Object | Transformer Model | TFMOD |  | LIMNAME | The name of the limit (such as Long Term, Medium Term, or Short Term). | String
12183 | Global Object | Transformer Model | TFMOD |  | LIMNAMES | The limits name in secondary winding. | String
12184 | Global Object | Transformer Model | TFMOD |  | LIMNAMET | The limits name in tertiary winding. | String
12185 | Global Object | Transformer Model | TFMOD | input | LIMSEAS | Season of the operational limit. | String
12186 | Global Object | Transformer Model | TFMOD | input | LIMSEASSEC | Season of the operational limit in secondary winding. | String
12187 | Global Object | Transformer Model | TFMOD | input | LIMSEASTER | Season of the operational limit in tertiary winding. | String
12188 | Global Object | Transformer Model | TFMOD | input | LIMTEMP | Array of temporary schedules | String
12189 | Global Object | Transformer Model | TFMOD | input | LIMTEMPSEC | Array of temporary schedules | String
12190 | Global Object | Transformer Model | TFMOD | input | LIMTEMPTER | Pointer to the temperature schedule | String
12191 | Global Object | Transformer Model | TFMOD |  | LIMUNIT | Enumerated limit units, 1 = Primary amps, 2 = KVA, 3 = MVA. | Integer
12192 | Global Object | Transformer Model | TFMOD |  | LIMUNITS | The limits unit in secondary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer
12193 | Global Object | Transformer Model | TFMOD |  | LIMUNITT | The limits unit in tertiary winding. 1 = Primary amps, 2 = KVA, 3 = MVA | Integer
12194 | Global Object | Transformer Model | TFMOD |  | LIMVALS | The limits value in secondary winding. | Float
12195 | Global Object | Transformer Model | TFMOD |  | LIMVALT | The limits value in tertiary winding. | Float
12196 | Global Object | Transformer Model | TFMOD |  | LIMVALUE | Value of the operational limit. | Float
12197 | Global Object | Transformer Model | TFMOD |  | MAGLOSS | Transformer nominal core loss (kW). | Float
12198 | Global Object | Transformer Model | TFMOD | input | MAGYZERO | Zero sequence magnetization conductance (optional). | Complex
12199 | Global Object | Transformer Model | TFMOD | input | NAME | Object name | String |  |  |  | DNMOBJ
12200 | Global Object | Transformer Model | TFMOD |  | NUMCYCEL | Number of elements | Integer
12201 | Global Object | Transformer Model | TFMOD |  | NUMCYCRW | Number of rows | Integer
12202 | Global Object | Transformer Model | TFMOD |  | NUMLIMIT | The number of operation limits. | Integer
12203 | Global Object | Transformer Model | TFMOD |  | NUMLIMSS | The number of the operation limits in secondary winding. | Integer
12204 | Global Object | Transformer Model | TFMOD |  | NUMLIMST | The number of the limits in tertiary winding. | Integer
12205 | Global Object | Transformer Model | TFMOD |  | NUMRGLIM | The number of regulator step limits. | Integer
12206 | Global Object | Transformer Model | TFMOD |  | PRIMGRDZ | Primary grounding impedance | Float
12207 | Global Object | Transformer Model | TFMOD |  | PRIMZ | Primary positive sequence reactance (per unit on transformer power base). | Float
12208 | Global Object | Transformer Model | TFMOD |  | REGLIMIT | Regulator step limit (amps). | Float
12209 | Global Object | Transformer Model | TFMOD |  | REGLIMITEVENT | A flag indicating regulation limit event | Boolean
12210 | Global Object | Transformer Model | TFMOD |  | REGRTGIV | Flag indicating whether the provided rating is the regulating VA. | Boolean
12211 | Global Object | Transformer Model | TFMOD |  | REGUNITS | Enumerated flag indicating the voltage units that should be used for transformers with voltage regulation capability. The following values can be used: 1 = Per unit voltage, 2 = Actual voltage (on configurable voltage base). | Integer
12212 | Global Object | Transformer Model | TFMOD |  | RGLIMSTP | The regulation step in percent voltage such as 5.0% or 10.0%. | Float
12213 | Global Object | Transformer Model | TFMOD |  | SECGRDZ | Secondary grounding impedance | Float
12214 | Global Object | Transformer Model | TFMOD |  | SECZ | Secondary positive sequence reactance (per unit on transformer power base). | Float
12215 | Global Object | Transformer Model | TFMOD |  | SRATING | Transformer rating (in kVA or MVA). | Float
12216 | Global Object | Transformer Model | TFMOD |  | SRATINGTER | Tertiary winding Rated capacity in kVA or MVA depending on the units flag | Float
12217 | Global Object | Transformer Model | TFMOD |  | SUNITS | A flag indicating units used for displaying transformer rating (true - kVA, false - MVA) | Boolean
12218 | Global Object | Transformer Model | TFMOD |  | TERTGRDZ | Tertiary grounding impedance | Float
12219 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12220 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
12221 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.CRITICAL | Flag indicating a critical customer is connected to the transformer | Boolean |  |  |  | TF
12222 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DISABLEALLFEEDERLVM | Flag to indicate if needs to disable LVM on all connected feeders if the transformer itself is set to uncontrollable. Default value is true. | Boolean |  |  |  | TF
12223 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DNAFENABLEDAPPS | DNAF application enabled bitmask | Integer |  |  |  | TF
12224 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12225 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12226 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DSECGRND | Grounded phase winding for a transformer | Integer |  |  |  | TF
12227 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.DSOOVER | Advanced application eligibility override status (0 - NotSet, 1 - AllowDSO, 2 - DisableDSO) | Enumeration |  |  |  | TF
12228 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.FLOWLIMITMAN | Manual entry flow limit, the same as normal unit, if the limit unit is amps, it is the secondary unit, if the limit unit is amps, it is the second | Float |  |  |  | TF
12229 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
12230 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.GROUNDPR | Primary grounded flag | Boolean |  |  |  | TF
12231 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.GROUNDSC | Secondary grounded flag | Boolean |  |  |  | TF
12232 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.GROUNDTE | Tertiary grounded flag | Boolean |  |  |  | TF
12233 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12234 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.LVMPROFORMINDEX | LVM problem formulation index | Integer |  |  |  | TF
12235 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.MAXOPERATIONS | Maximum number of daily operations for regulating transformer | Integer |  |  |  | TF
12236 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.MAXVOLTIMBALANCE | Maximum voltage imbalance percentage for regulating transformer | Float |  |  |  | TF
12237 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.NAME | Name of the object | String |  |  |  | DNMOBJ
12238 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12239 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12240 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.NOMCCUST | The number of nominally connected customers | Integer |  |  |  | TF
12241 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12242 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.PRIMGNDR | Primary grounding branch resistance | Float |  | Ohms | Ohms | TF
12243 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.PRIMGNDX | Primary grounding branch reactance | Float |  | Ohms | Ohms | TF
12244 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.PRIMWIND | Primary winding connection type | Integer |  |  |  | TF
12245 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.REGULATIONMARGIN | Regulation margin | Float |  |  |  | TF
12246 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.ROTATION | Transformer phase rotation (1 - No rotation, 2 - A to B, B to C, C to A, 4 = A to C, B to A, C to B) | Integer |  |  |  | TF
12247 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.SEC1GNDR | Secondary grounding branch resistance | Float |  | Ohms | Ohms | TF
12248 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.SEC1GNDX | Secondary grounding branch reactance | Float |  | Ohms | Ohms | TF
12249 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.SEC2GNDR | Tertiary grounding branch resistance | Float |  | Ohms | Ohms | TF
12250 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.SEC2GNDX | Tertiary grounding branch reactance | Float |  | Ohms | Ohms | TF
12251 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.SECWIND | Secondary winding connection type | Integer |  |  |  | TF
12252 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.TERTWIND | Tertiary winding connection type | Integer |  |  |  | TF
12253 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.TFLOADED | Connected load flag | Boolean |  |  |  | TF
12254 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.TFMANFLOWLIMITENABLE | Flag indicating having manual entry flow limit | Boolean |  |  |  | TF
12255 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.TFMASK | All booleans will be combined into a single mask | Integer |  |  |  | TF
12256 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.VOLTPR | Primary voltage (kV line to ground) | Float |  | kV | kV | TF
12257 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.VOLTSC | Secondary voltage (kV line to ground) | Float |  | kV | kV | TF
12258 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF.VOLTTE | Tertiary voltage (kV line to ground) | Float |  | kV | kV | TF
12259 | Global Object | Transformer Model | TFMOD |  | TERTZ | Tertiary positive sequence resistance (per unit on transformer power base). | Float
12260 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12261 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12262 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12263 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
12264 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.GROUNDED | Flag indicating shunt device is grounded | Boolean |  |  |  | SHUNT
12265 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12266 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.NAME | Name of the object | String |  |  |  | DNMOBJ
12267 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12268 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12269 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.NPHASE | A flag indicating the neutral phase | Boolean |  |  |  | TEMPGROUND
12270 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12271 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.OPCOMMNT | Operator inserted comment. | String |  |  |  | TEMPGROUND
12272 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.POSITIONTXT | Temporary ground label position | String |  |  |  | TEMPGROUND
12273 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.PRTDEVID | ID of the protection device | String |  |  |  | TEMPGROUND
12274 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.RGROUND | Grounding resistance (ohms) | Float |  | ohms | ohms | TEMPGROUND
12275 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.WYE | Flag indicating shunt device is wye connected | Boolean |  |  |  | SHUNT
12276 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround.XGROUND | Grounding reactance (ohms) | Float |  | ohms | ohms | TEMPGROUND
12277 | Global Object | Transformer Model | TFMOD |  | TFTYPE | Enumerated transformer type for linking the transformer model to a transformer type that is needed by the power flow function. | Integer
12278 | Global Object | Transformer Model | TFMOD |  | TFTYPEINDEX | Transformer configuration type index (as listed on the Transformer Configurations tab) | Integer
12279 | DNOM Component | Transformer Output | TFOUT |  | COPPLOSS | Total transformer core loss | Float |  | P + jQ | P + jQ
12280 | DNOM Component | Transformer Output | TFOUT |  | CORELOSS | Total transformer copper loss | Float |  | P + jQ | P + jQ
12281 | DNOM Component | Transformer Output | TFOUT |  | IPRIMA | Phase A current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
12282 | DNOM Component | Transformer Output | TFOUT |  | IPRIMB | Phase B current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
12283 | DNOM Component | Transformer Output | TFOUT |  | IPRIMC | Phase C current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
12284 | DNOM Component | Transformer Output | TFOUT |  | IPRIMN | Phase N current injected at primary end of transformer into the transformer | Float |  | Amps | Amps
12285 | DNOM Component | Transformer Output | TFOUT |  | ISEC1A | Phase A current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
12286 | DNOM Component | Transformer Output | TFOUT |  | ISEC1B | Phase B current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
12287 | DNOM Component | Transformer Output | TFOUT |  | ISEC1C | Phase C current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
12288 | DNOM Component | Transformer Output | TFOUT |  | ISEC1N | Phase N current injected at secondary1 end of transformer into the transformer | Float |  | Amps | Amps
12289 | DNOM Component | Transformer Output | TFOUT |  | ISEC2A | Phase A current injected at secondary2 end of transformer into the transformer | Float |  | Amps | Amps
12290 | DNOM Component | Transformer Output | TFOUT |  | ISEC2B | Phase B current injected at secondary2 end of transformer into the transformer | Float |  | Amps | Amps
12291 | DNOM Component | Transformer Output | TFOUT |  | ISEC2C | Phase C current injected at secondary2 end of transformer into the transformer | Float |  | Amps | Amps
12292 | DNOM Component | Transformer Output | TFOUT |  | ISEC2N | Phase N current injected at secondary2 end of transformer into the transformer | Float |  | Amps | Amps
12293 | DNOM Component | Transformer Output | TFOUT |  | LIMFLAGS | Limit violation flags | Integer
12294 | DNOM Component | Transformer Output | TFOUT |  | PQPRIMA | Phase A power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
12295 | DNOM Component | Transformer Output | TFOUT |  | PQPRIMB | Phase B power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
12296 | DNOM Component | Transformer Output | TFOUT |  | PQPRIMC | Phase C power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
12297 | DNOM Component | Transformer Output | TFOUT |  | PQPRIMN | Phase N power injected at primary end of transformer into the transformer | Float |  | KVA | KVA
12298 | DNOM Component | Transformer Output | TFOUT |  | PQSEC1A | Phase A power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
12299 | DNOM Component | Transformer Output | TFOUT |  | PQSEC1B | Phase B power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
12300 | DNOM Component | Transformer Output | TFOUT |  | PQSEC1C | Phase C power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
12301 | DNOM Component | Transformer Output | TFOUT |  | PQSEC1N | Phase N power injected at secondary1 end of transformer into the transformer | Float |  | KVA | KVA
12302 | DNOM Component | Transformer Output | TFOUT |  | PQSEC2A | Phase A power injected at secondary2 end of transformer into the transformer | Float |  | KVA | KVA
12303 | DNOM Component | Transformer Output | TFOUT |  | PQSEC2B | Phase B power injected at secondary2 end of transformer into the transformer | Float |  | KVA | KVA
12304 | DNOM Component | Transformer Output | TFOUT |  | PQSEC2C | Phase C power injected at secondary2 end of transformer into the transformer | Float |  | KVA | KVA
12305 | DNOM Component | Transformer Output | TFOUT |  | PQSEC2N | Phase N power injected at secondary2 end of transformer into the transformer | Float |  | KVA | KVA
12306 | DNOM Component Placement | Transformer Placement | TFPLE | input | TF | Pointer to the associated transformer | String
12307 | DNOM Component Placement | Temporary Ground Placement | TGRPLE | input | pTempGround | Pointer to the associated temporary ground | String
12308 | DNOM Component | Temporary Switch | TMPSWT | input | ABNDATETIME | Date and time when jumper is placed or time of last status change. | String
12309 | DNOM Component | Temporary Switch | TMPSWT |  | ABNDATETIME_TICKS | The device's last update time | String
12310 | DNOM Component | Temporary Switch | TMPSWT | Input | ABNDATETIMEUPDATE | The insertion time of temp switch | String
12311 | DNOM Component | Temporary Switch | TMPSWT | Input | ABNDATETIMEUPDATE_TICKS | The last update time of temp switch | String
12312 | DNOM Component | Temporary Switch | TMPSWT | Input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
12313 | DNOM Component | Temporary Switch | TMPSWT | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12314 | DNOM Component | Temporary Switch | TMPSWT |  | COMPJMPCOMP1 | ID of the first component the temporary jumper is connected | String
12315 | DNOM Component | Temporary Switch | TMPSWT |  | COMPJMPCOMP2 | ID of the second component the temporary jumper is connected | String
12316 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPFROMPHA | Flag indicating whether phase A exists at from node of the jumper. | Boolean
12317 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPFROMPHB | Flag indicating whether phase B exists at from node of the jumper. | Boolean
12318 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPFROMPHC | Flag indicating whether phase C exists at from node of the jumper. | Boolean
12319 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPFROMPHN | Flag indicating whether phase N exists at from node of the jumper. | Boolean
12320 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPPHASING | Phasing in both from and to node of the jumper. | String
12321 | DNOM Component | Temporary Switch | TMPSWT |  | COMPJMPSUB1 | ID of the first substation the temporary jumper is connected | String
12322 | DNOM Component | Temporary Switch | TMPSWT |  | COMPJMPSUB2 | ID of the second substation the temporary jumper is connected | String
12323 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPTOPHA | Flag indicating whether phase A exists at to node of the jumper. | Boolean
12324 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPTOPHB | Flag indicating whether phase B exists at to node of the jumper. | Boolean
12325 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPTOPHC | Flag indicating whether phase C exists at to node of the jumper. | Boolean
12326 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPTOPHN | Flag indicating whether phase N exists at to node of the jumper. | Boolean
12327 | DNOM Component | Temporary Switch | TMPSWT |  | COMPJMPTRPH | Temporary switch (cut or jumper) transfer phases bitmask | String
12328 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPX1 | X coordinates of the from node of the jumper. | Float
12329 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPX2 | X coordinates of the to node of the jumper. | Float
12330 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPY1 | Y coordinates of the from node of the jumper. | Float
12331 | DNOM Component | Temporary Switch | TMPSWT | input | COMPJMPY2 | Y coordinates of the to node of the jumper. | Float
12332 | DNOM Component | Temporary Switch | TMPSWT | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
12333 | DNOM Component | Temporary Switch | TMPSWT | Input | DNOMTABNAME | The dnom object name of temp switch | String
12334 | DNOM Component | Temporary Switch | TMPSWT | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12335 | DNOM Component | Temporary Switch | TMPSWT | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12336 | DNOM Component | Temporary Switch | TMPSWT | input | DYNFEEDERNAME2 | Second dynamic energizing feeder name for currently open switches. | String
12337 | DNOM Component | Temporary Switch | TMPSWT |  | DYNSTATIONNAME2 | Name of the abnormally energizing substation | String
12338 | DNOM Component | Temporary Switch | TMPSWT |  | FRLENGTH1 | Position of the first connection point of the temporary switch (cut or jumper) on the associated line segment, expressed as a fraction (for example, 0.32). Allowable values are 0-1, where 0 and 1 show that the connection point is placed on the node terminal. | Float
12339 | DNOM Component | Temporary Switch | TMPSWT |  | FRLENGTH2 | Position of the second connection point of the temporary switch (jumper) on the associated line segment, expressed as a fraction (for example, 0.32). Allowable values are 0-1, where 0 and 1 show that the connection point is placed on the node terminal. | Float
12340 | DNOM Component | Temporary Switch | TMPSWT | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean |  |  |  | TOPOLOGYOBJECT
12341 | DNOM Component | Temporary Switch | TMPSWT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12342 | DNOM Component | Temporary Switch | TMPSWT | output | IFROMA | Phase A current flow (Amps). | Float | DPF
12343 | DNOM Component | Temporary Switch | TMPSWT | output | IFROMB | Phase B current flow (Amps). | Float | DPF
12344 | DNOM Component | Temporary Switch | TMPSWT | output | IFROMC | Phase C current flow (Amps). | Float | DPF
12345 | DNOM Component | Temporary Switch | TMPSWT | output | IFROMN | Phase N current flow (Amps). | Float | DPF
12346 | DNOM Component | Temporary Switch | TMPSWT |  | ISORPHAN | A flag indicating that the temporary switch is orphan | Boolean
12347 | DNOM Component | Temporary Switch | TMPSWT | input | LBLPOSITION | Label position | Integer
12348 | DNOM Component | Temporary Switch | TMPSWT | input | LIMFLAGS | LIM flags | Integer
12349 | DNOM Component | Temporary Switch | TMPSWT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
12350 | DNOM Component | Temporary Switch | TMPSWT | input | NAME | Object name | String |  |  |  | DNMOBJ
12351 | DNOM Component | Temporary Switch | TMPSWT | input | NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12352 | DNOM Component | Temporary Switch | TMPSWT | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12353 | DNOM Component | Temporary Switch | TMPSWT | input | NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12354 | DNOM Component | Temporary Switch | TMPSWT | input | OPCOMMNT | Operator inserted comment. | String
12355 | DNOM Component | Temporary Switch | TMPSWT | input | PHASESTATUS | Phase status | Integer
12356 | DNOM Component | Temporary Switch | TMPSWT |  | POSITIONTXT | Position specific comments | Integer
12357 | DNOM Component | Temporary Switch | TMPSWT | input | SWCLOSEDPHASES | Switch closed phases | String
12358 | DNOM Component | Temporary Switch | TMPSWT | input | SWCURRENTPOSITION | Switch current position | String
12359 | DNOM Component | Temporary Switch | TMPSWT | input | SWOPENPHASES | Switch open phases | String
12360 | DNOM Component | Temporary Switch | TMPSWT | input | SWSTATUS | Switch status | String
12361 | DNOM Component | Temporary Switch | TMPSWT | input | TEMPMODDESCRIPT | Operator inserted comment. | String
12362 | DNOM Component | Temporary Switch | TMPSWT | input | TEMPMODPERMITAREA | Associated permission area name. | String
12363 | DNOM Component | Temporary Switch | TMPSWT | input | TMPSWSTAT | Current open status, the value is “True” or “False”. True = open, False = closed. | Boolean
12364 | DNOM Component | Temporary Switch | TMPSWT | input | TMPSWSTATSTR | Current open status, the value is Open" or "Closed"" | String
12365 | DNOM Component | Temporary Switch | TMPSWT | input | TMPSWTAMPLIMIT | Jumper flow limit (Amps). | Float
12366 | DNOM Component | Temporary Switch | TMPSWT |  | WASSNAPPED | A flag indicating that the position of the temporary device was updated | Boolean
12367 | DNOM Component | Temporary Switch | TMPSWT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
12368 | DNOM Component | Temporary Switch | TMPSWT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
12369 | Virtual Object | Topology Component | TOPOCOMP | input | BLOCKSTATECONTROL | Flag indicating that device state controls are blocked | Integer
12370 | Virtual Object | Topology Component | TOPOCOMP | input | DEVICEDISABLED | Flag indicating that the device is disabled for controls | Integer
12371 | Virtual Object | Topology Component | TOPOCOMP | input | _KEY | The unique identifier to represent a device. | String
12372 | Virtual Object | Topology Component | TOPOCOMP | input | ABNDATETIME | Get the time when the component’s status changed to abnormal. | String
12373 | Virtual Object | Topology Component | TOPOCOMP | output | ABNDATETIME_TICKS | The device's last update time | String
12374 | Virtual Object | Topology Component | TOPOCOMP | input | ABNORMALSTATUS | Status description when devices are in abnormal status (Open, Closed, Inserted, and others). | String
12375 | Virtual Object | Topology Component | TOPOCOMP | input | ALTGEOMETRY | The name of alternate geometries of the given topology device. | String
12376 | Virtual Object | Topology Component | TOPOCOMP | input | ALTID | For devices other than transformer, distribution transformer and shunt impedance (capacitor) this query returns the SECONDID if the field exists, otherwise returns the ADDRESS. For transformer, distribution transformer and shunt impedance (capacitor), the ADDRESS is returned. | String
12377 | Virtual Object | Topology Component | TOPOCOMP |  | BOUNDARYDEVICEISCONTROLLED | Flag indicating that the component can be controlled remotely | Boolean
12378 | Virtual Object | Topology Component | TOPOCOMP | input | COMPISLOOPED | Whether the component is in a loop. | Boolean
12379 | Virtual Object | Topology Component | TOPOCOMP | input | COMPISPARALLEL | Indicates whether the component is parallel looped | Boolean
12380 | Virtual Object | Topology Component | TOPOCOMP |  | CONNECTTOGROUND | Flag indicating that the component is energized and grounded | Boolean
12381 | Virtual Object | Topology Component | TOPOCOMP |  | CONNECTTOGROUND_A | Flag indicating that phase A of the component is energized and grounded | Boolean
12382 | Virtual Object | Topology Component | TOPOCOMP |  | CONNECTTOGROUND_B | Flag indicating that phase B of the component is energized and grounded | Boolean
12383 | Virtual Object | Topology Component | TOPOCOMP |  | CONNECTTOGROUND_C | Flag indicating that phase C of the component is energized and grounded | Boolean
12384 | Virtual Object | Topology Component | TOPOCOMP | input | CTRLPNTCNT | The number of control points | Integer
12385 | Virtual Object | Topology Component | TOPOCOMP | input | DEVICESERVCNTRNAME | Component’s service center name. | String
12386 | Virtual Object | Topology Component | TOPOCOMP | input | DEVICETYPECODE | Component’s device type code. | Integer
12387 | Virtual Object | Topology Component | TOPOCOMP | input | DEVICETYPENAME | Name of the device type(e.g. SUB, LOAD) | String
12388 | Virtual Object | Topology Component | TOPOCOMP |  | DYNAMICPHASING | Dynamic phasing information | String
12389 | Virtual Object | Topology Component | TOPOCOMP | input | EQUIPFROMEMS | Whether the component is station internal device. | String
12390 | Virtual Object | Topology Component | TOPOCOMP | input | FEEDERALTNAME | Component’s nominal feeder’s alternate name. When a component is associated with two feeders, shows the list of feeder alternate names separated by space. | String
12391 | Virtual Object | Topology Component | TOPOCOMP | input | FEEDERID | Component’s nominal feeder ID. When a component is associated with two feeders, shows the list of feeder IDs separated by space. | String
12392 | Virtual Object | Topology Component | TOPOCOMP |  | FEEDERMAIN | Flag indicating that the component is on feeder main | Boolean
12393 | Virtual Object | Topology Component | TOPOCOMP | input | FEEDERNAME | Component’s nominal feeder name. When a component is associated with two feeders, shows the list of feeder names separated by space. | String
12394 | Virtual Object | Topology Component | TOPOCOMP | input | STATIONFEEDERNAME | Component’s nominal station and feeder names separated by slash. When a component is associated with two stations or feeders, shows the list of station and feeder name pairs, separated by comma. | String
12395 | Virtual Object | Topology Component | TOPOCOMP |  | FROMNODE | Components from-node name | String
12396 | Virtual Object | Topology Component | TOPOCOMP | input | GEOGRAPHIC | The geometry name of given topology device. | String
12397 | Virtual Object | Topology Component | TOPOCOMP | input | HASMANUALSCADA | Flag indicating that the component has a “manual” (local) SCADA measurement | Boolean
12398 | Virtual Object | Topology Component | TOPOCOMP | input | HASTELEMETEREDSCADA | Flag indicating that the component has a “telemetered” (from RTU) SCADA measurement | Boolean
12399 | Virtual Object | Topology Component | TOPOCOMP | input | INSIDEVAULTORCAB | Get the ID of vault or cabinet containing the device. | String
12400 | Virtual Object | Topology Component | TOPOCOMP |  | INTERNALLYENERGIZED | Internally energized phases | String
12401 | Virtual Object | Topology Component | TOPOCOMP | input | ISAUTOMATEDSWITCH | Is the topology device automatic? | Boolean
12402 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | ADDRESS.NOAPPSTR | Address of the composite switch | String |  |  |  | NDPFST
12403 | Virtual Object | Topology Component | TOPOCOMP | input | ISDYNFEEDERLOOPED | Whether the component’s dynamic feeder is in a loop. | Boolean
12404 | Virtual Object | Topology Component | TOPOCOMP | input | ISSCADA | Flag indicating that the component is a SCADA component | Boolean
12405 | Virtual Object | Topology Component | TOPOCOMP | input | ISSCADAORDER | Flag indicating that the component is a SCADA component or an energy resource | Boolean
12406 | Virtual Object | Topology Component | TOPOCOMP | input | ISTELEMETEREDSWITCH | Flag indicating that the component is telemetered (this query is similar to ISTELEMETREDSWITCH - fixed a typo but kept for backward compatibility) | Boolean
12407 | Virtual Object | Topology Component | TOPOCOMP | input | ISTELEMETREDSWITCH | Flag indicating that the component is telemetered | Boolean
12408 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.ADDRESS | The feeder address | String |  |  |  | FDR
12409 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.ALTERNATENAME | Alternate name of the feeder | String |  |  |  | FDR
12410 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12411 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.BRHDFEND | Flow end for the feeder head branches | Integer |  |  |  | FDR
12412 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.DEFCOLOR | Default color | Integer |  |  |  | FDR
12413 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.DNAFENABLEDAPPS | If the DNAF applications is enabled in feeder | Boolean |  |  |  | FDR
12414 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12415 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12416 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.EMSCONNT | Flag indicating feeder connection was not made to the sub-transmission network. | Boolean |  |  |  | FDR
12417 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.FAILEDCAPCCTRLLIM | Maximum failed capacitor controller limit | Integer |  |  |  | FDR
12418 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.FAILEDREGLIM | Maximum failed regulating device limit | Integer |  |  |  | FDR
12419 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.FLLIMMLT | Flow limit scaling factor applied to all limits | Float |  |  |  | FDR
12420 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.HASMANAMPS | Flag indicating feeder is using a manual entry | Boolean |  |  |  | FDR
12421 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12422 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.ISLOOPED | Flag indicating if feeder is the Looped feeder | Boolean |  |  |  | FDR
12423 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.ISPRIMFDR | Flag indicating if the feeder is a primary feeder or a secondary feeder | Boolean |  |  |  | FDR
12424 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.LDNAME | EMS Netmom Load Name | String |  |  |  | FDR
12425 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.LVMPROFORMINDEX | Index of problem formulation in feeder | String |  |  |  | FDR
12426 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.LVMUNAVAILCTRLCOUNT | Number of unavailable controller on the feeder | Integer |  |  |  | FDR
12427 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MANAMPSA | A manually entered phase A feeder amp value | Float |  |  |  | FDR
12428 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MANAMPSB | A manually entered phase B feeder amp value | Float |  |  |  | FDR
12429 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MANAMPSC | A manually entered phase C feeder amp value | Float |  |  |  | FDR
12430 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MANPF | A manually entered power factor feeder head value | Float |  |  |  | FDR
12431 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MAXUNCTRLCAPACITORS | Maximum uncontrollable capacitors | Integer |  |  |  | FDR
12432 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.MAXUNCTRLTAPS | Maximum Uncontrollable Tap Changers | Integer |  |  |  | FDR
12433 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NAME | Name of the object | String |  |  |  | DNMOBJ
12434 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NOMINALCUSTCOUNTA | Number of customers connected to phase A of the feeder | String |  |  |  | FDR
12435 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NOMINALCUSTCOUNTB | Number of customers connected to phase B of the feeder | String |  |  |  | FDR
12436 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NOMINALCUSTCOUNTC | Number of customers connected to phase C of the feeder | String |  |  |  | FDR
12437 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NOMINALCUSTCOUNTMULTPHASE | Number of customers connected to all phases of the feeder | String |  |  |  | FDR
12438 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.NUMLDCAT | Number of load categories for the station | Integer |  |  |  | FDR
12439 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.PNOMLOAD | Array of nominal P load values by load category | String |  |  |  | FDR
12440 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.VOLTAGE | Nominal voltage level (kV line to ground). | Float |  |  |  | FDR
12441 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED.VOLTFLATTENLIMIT | Voltage flattening limit.Default value: 1%,Range: [0 - 10] | Float |  |  |  | FDR
12442 | Virtual Object | Topology Component | TOPOCOMP | input | ISTRACED | Flag indicating that the component is currently traced (this is a client-side query, therefore, to query this value, the "IsLocal" flag must be set to true) | Boolean
12443 | Virtual Object | Topology Component | TOPOCOMP |  | LOCATEOBJID | Locate object ID | String
12444 | Virtual Object | Topology Component | TOPOCOMP |  | NODENUM | Node name | String
12445 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
12446 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
12447 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
12448 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
12449 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
12450 | Virtual Object | Topology Component | TOPOCOMP |  | OBJGEOMETRYNAME | Object geometry name | String
12451 | Virtual Object | Topology Component | TOPOCOMP |  | OPERATOR | The name of the operator who performed the last change of state. | String
12452 | Virtual Object | Topology Component | TOPOCOMP | input | PERMITAREAID | Component’s permit area ID. | String
12453 | Virtual Object | Topology Component | TOPOCOMP |  | SITE | Site of the component | String
12454 | Virtual Object | Topology Component | TOPOCOMP | input | STATIONNAME | Component’s nominal station name. | String
12455 | Virtual Object | Topology Component | TOPOCOMP |  | SWITCHCUSTCNT | Number of energized downstream customers | String
12456 | Virtual Object | Topology Component | TOPOCOMP |  | SWITCHCUSTCNT_A | Number of energized downstream customers connected to phase A | String
12457 | Virtual Object | Topology Component | TOPOCOMP |  | SWITCHCUSTCNT_B | Number of energized downstream customers connected to phase B | String
12458 | Virtual Object | Topology Component | TOPOCOMP |  | SWITCHCUSTCNT_C | Number of energized downstream customers connected to phase C | String
12459 | Virtual Object | Topology Component | TOPOCOMP | input | TAGCAPABLE | Display of capability to be tagged | String
12460 | Virtual Object | Topology Component | TOPOCOMP | input | TAGGINGSUBDMS | Nominal DMS substation name. | String
12461 | Virtual Object | Topology Component | TOPOCOMP | input | TAGGINGSUBEMS | Nominal EMS substation name. | String
12462 | Virtual Object | Topology Component | TOPOCOMP | input | TNABNORMAL | Component’s energization status. Return “NORMAL” or “ABNORMAL”. | String
12463 | Virtual Object | Topology Component | TOPOCOMP | input | TNABNORMALNOEMS | Energization status of devices outside the station fence. Return “NORMAL” or “ABNORMAL”. | String
12464 | Virtual Object | Topology Component | TOPOCOMP |  | TONODE | Components to-node name | String
12465 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12466 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.BOUNDARY | The boundary flag | Boolean |  |  |  | BRANCH
12467 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12468 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12469 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.FROMEMS | A flag indicating that the data is from the EMS | Integer |  |  |  | TOPOLOGYOBJECT
12470 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12471 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.NAME | Name of the object | String |  |  |  | DNMOBJ
12472 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.NEWATMSK | Additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12473 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.NEWATMSK2 | Second additional attributes bitmask flag | Integer |  |  |  | TOPOLOGYOBJECT
12474 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.NTPFLAG | Enumerated NTP flag | Integer |  |  |  | TOPOLOGYOBJECT
12475 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.OPCOMMNT | Operator inserted comment | String |  |  |  | TMPSWT
12476 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch.POSITIONTXT | Position specific comments | Integer |  |  |  | TMPSWT
12477 | Virtual Object | Topology Component | TOPOCOMP | input | TOPOAREA | Area name | String
12478 | Virtual Object | Topology Component | TOPOCOMP | input | TOPOAREAID | Area ID | String
12479 | Virtual Object | Topology Component | TOPOCOMP | output | TOPODPFSTATUS | DPF status of specified topology object. | String
12480 | Virtual Object | Topology Component | TOPOCOMP | input | TOPOEMSSUBNAME | Nominal EMS substation name. | String
12481 | Virtual Object | Topology Component | TOPOCOMP |  | TOPOENERGIZED | Phases energized | String
12482 | Virtual Object | Topology Component | TOPOCOMP | input | TOPOSUBNAME | Nominal DMS substation name. | String
12483 | Virtual Object | Topology Component | TOPOCOMP | output | SWITCHCRITCUSTCNT | The number of energized critical customers downstream. Applies to switching devices | Integer
12484 | Virtual Object | Topology Component | TOPOCOMP | output | SWITCHCRITCUSTCNT_A | The number of energized critical customers downstream, for phase A. Applies to switching devices | Integer
12485 | Virtual Object | Topology Component | TOPOCOMP | output | SWITCHCRITCUSTCNT_B | The number of energized critical customers downstream, for phase B. Applies to switching devices | Integer
12486 | Virtual Object | Topology Component | TOPOCOMP | output | SWITCHCRITCUSTCNT_C | The number of energized critical customers downstream, for phase C. Applies to switching devices | Integer
12487 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | ADDRESS | Pointer to a string with the address in the station vector collection | String |  |  |  | NDPFST
12488 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12489 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12490 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12491 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean |  |  |  | UICNTR
12492 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.FUNCTYPE | Dynamic array of objects collected in the UI container | Enumeration |  |  |  | UICNTR
12493 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.ID | ID of the object | String |  |  |  | DNMOBJ
12494 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.NAME | Object name | String |  |  |  | DNMOBJ
12495 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean |  |  |  | UICNTR
12496 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER.UICNTMSK | UI bitmask | Integer |  |  |  | UICNTR
12497 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | FROMEMS | A flag indicating that the data is from the EMS | Boolean
12498 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12499 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12500 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12501 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean |  |  |  | UICNTR
12502 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.FUNCTYPE | Dynamic array of objects collected in the UI container | Enumeration |  |  |  | UICNTR
12503 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.ID | ID of the object | String |  |  |  | DNMOBJ
12504 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.NAME | Object name | String |  |  |  | DNMOBJ
12505 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean |  |  |  | UICNTR
12506 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER.UICNTMSK | UI bitmask | Integer |  |  |  | UICNTR
12507 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NEWATMSK | Additional attributes bitmask flag, also includes the Future bit | Integer
12508 | DNOM Component | UI Container | UICNTR | input | ADDRESS.NOAPPSTR | Address of the composite switch | String |  |  |  | NDPFST
12509 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NEWATMSK2 | Second additional attributes bitmask flag | Integer
12510 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NEWATMSK3 | Third additional attributes bitmask flag, includes bits for non-active equipment states (FutureRemoved and Removed), and for equipment owned by an external company (ThirdPartyOwnedDevice). (The Future bit is part of NEWATMSK) The following fields are part for this bitmask. FutureRemovedPhaseA 1 FutureRemovedPhaseB (1 << 1) FutureRemovedPhaseC (1 << 2) FutureRemovedPhaseN (1 << 3) RemovedPhaseA (1 << 4) RemovedPhaseB (1 << 5) RemovedPhaseC (1 << 6) RemovedPhaseN (1 << 7) ThirdPartyOwnedDevice (1 << 8) CommissionState for a component is calculated depending on the component's Future, FutureRemoved, or Removed bit. Possible values are: Future = 0, Active, FutureRemoved, Removed | Integer
12511 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NOMFEED | Each topology object also has a pointer to its dynamic feeder. This pointer may change depending on switching operations. | String
12512 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | NTPFLAG | Enumerated NTP flag | Integer
12513 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | PRJID | Future equipment commissioning/decommissioning project ID | String
12514 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | SERVCNTR | Pointer to the associated service center | String
12515 | DNOM Group Object | Topology Object | TOPOLOGYOBJECT | input | STAGE | Future equipment commissioning/decommissioning project stage | String
12516 | DNOM Component | Temporary Switch Output | TSWOUT |  | IFROMA | Phase A current injected at from end of line into the line | Float |  | Amps | Amps
12517 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12518 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12519 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
12520 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12521 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12522 | DNOM Component | UI Container | UICNTR | input | JUNCCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
12523 | DNOM Component | Temporary Switch Output | TSWOUT |  | IFROMB | Phase B current injected at from end of line into the line | Float |  | Amps | Amps
12524 | DNOM Component | Temporary Switch Output | TSWOUT |  | IFROMC | Phase C current injected at from end of line into the line | Float |  | Amps | Amps
12525 | DNOM Component | Temporary Switch Output | TSWOUT |  | IFROMN | Phase N current injected at from end of line into the line | Float |  | Amps | Amps
12526 | DNOM Component | Temporary Switch Output | TSWOUT |  | PQFROMA | Phase A power injected at from end of line into the line | Float |  | kVA | KVA
12527 | DNOM Component | Temporary Switch Output | TSWOUT |  | PQFROMB | Phase B power injected at from end of line into the line | Float |  | kVA | KVA
12528 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.AX | Dynamic array of X coordinates | String |  |  |  | CMBPLS
12529 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.AY | Dynamic array of Y coordinates | String |  |  |  | CMBPLS
12530 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
12531 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
12532 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
12533 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
12534 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
12535 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
12536 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
12537 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
12538 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
12539 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
12540 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
12541 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
12542 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.NUMVERT | Number of vertices (line or polygon) | String |  |  |  | CMBPLS
12543 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.ROTATION | Rotation anagle of the placement | String |  | degrees | degrees | CMBPLS
12544 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.SIZE | Size of the object | String |  |  |  | CMBPLS
12545 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.X | X coordinate of the placement | String |  |  |  | CMBPLS
12546 | DNOM Component | UI Container | UICNTR | input | PLACEMNT.Y | Y coordinate of the placement | String |  |  |  | CMBPLS
12547 | DNOM Component | Temporary Switch Output | TSWOUT |  | PQFROMC | Phase C power injected at from end of line into the line | Float |  | kVA | KVA
12548 | DNOM Component | Temporary Switch Output | TSWOUT |  | PQFROMN | Phase N power injected at from end of line into the line | Float |  | kVA | KVA
12549 | DNOM Component | UI Container | UICNTR | input | SERVCNTR.AREAIND | Permission area index of the associated service center | String |  |  |  | DNMOBJ
12550 | DNOM Component | UI Container | UICNTR | input | SERVCNTR.DNOMX | X coordinate of the associated service center | String |  |  |  | DNMOBJ
12551 | DNOM Component | UI Container | UICNTR | input | SERVCNTR.DNOMY | Y coordinate of the associated service center | String |  |  |  | DNMOBJ
12552 | DNOM Component | UI Container | UICNTR | input | SERVCNTR.ID | ID of the associated service center | String |  |  |  | DNMOBJ
12553 | DNOM Component | UI Container | UICNTR | input | SERVCNTR.NAME | Name of the associated service center | String |  |  |  | DNMOBJ
12554 | DNOM Component Placement | Temporary Switch Placement | TSWPLE | input | pTempSwitch | Pointer to the associated temporary switch | String
12555 | DNOM Component | Trouble Ticket | TTK | input | AREAIND | Integer (index) into station permission area list. | Integer
12556 | DNOM Component | Trouble Ticket | TTK | input | DEVICEID | Associated suspect device ID. | String
12557 | DNOM Component | Trouble Ticket | TTK | input | DNOMX | Horizontal coordinate of DNOM object | Float
12558 | DNOM Component | Trouble Ticket | TTK | input | DNOMY | Vertical coordinate of DNOM object | Float
12559 | DNOM Component | Trouble Ticket | TTK | input | FSTSTAGE | First stage device. | String
12560 | DNOM Component | UI Container | UICNTR | input | USRVLTLV.COLORVLT | Associated color used for display purposes | String |  |  |  | UVLTLV
12561 | DNOM Component | UI Container | UICNTR | input | USRVLTLV.DISTVLTL | Flag indicating that the voltage level represents a distribution voltage level (true - distribution, false - transmission) | String |  |  |  | UVLTLV
12562 | DNOM Component | UI Container | UICNTR | input | USRVLTLV.ID | ID of the user voltage level | String |  |  |  | DNMOBJ
12563 | DNOM Component | UI Container | UICNTR | input | USRVLTLV.KVLLVVAL | Voltage level (line to line) | String |  | kV | kV | UVLTLV
12564 | DNOM Component | Trouble Ticket | TTK | input | ID | Unique and persistent ID. | String
12565 | DNOM Component | UI Container | UICNTR | input | VLTOBJ.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12566 | DNOM Component | UI Container | UICNTR | input | VLTOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12567 | DNOM Component | UI Container | UICNTR | input | VLTOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12568 | DNOM Component | UI Container | UICNTR | input | VLTOBJ.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12569 | DNOM Component | UI Container | UICNTR | input | VLTOBJ.NAME | Name of the object | String |  |  |  | DNMOBJ
12570 | DNOM Component | Trouble Ticket | TTK | input | NAME | Name. | String
12571 | DNOM Component | Trouble Ticket | TTK | input | STATUS | Ticket status. | String
12572 | DNOM Component | Trouble Ticket | TTK | input | TICKTYPE | Ticket Type. | String
12573 | DNOM Component | Trouble Ticket | TTK | input | X | X Coordinate. | Float
12574 | DNOM Component | Trouble Ticket | TTK | input | Y | Y Coordinate. | Float
12575 | DNOM Component Placement | UI Container Label Placement | UICLBL | input | CNTAINER | Pointer to the associated UI container | String
12576 | DNOM Component Placement | UI Container Placement | UICNTP | input | CNTAINER | Pointer to the associated UI container | String
12577 | DNOM Component | Vault | VAULT | input | ADDRESS.NOAPPSTRING | Address. | String
12578 | DNOM Component | UI Container | UICNTR | input | ADDRESS | Pointer to a string with the address in the station vector collection | String |  |  |  | NDPFST
12579 | DNOM Component | UI Container | UICNTR | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
12580 | DNOM Component | UI Container | UICNTR | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12581 | DNOM Component | UI Container | UICNTR | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12582 | DNOM Component | UI Container | UICNTR |  | ENUMTYPE | UI container type enumeration (0 - UI_No_Uincnter, 1 - UI_OCR_Bypass, 2 - UI_OH_Auto, 3 - UI_Reg_Bypass, 4 - UI_VacInt_Bypass, 5 - UI_SwCab_Sw, 6 - UI_CompSw_Throwover, 7 - UI_Elbow_Group, 8 - UI_Fuse_Group, 9 - UI_Recloser_Group, 10 - UI_Sect_Group, 11 - UI_Jumper_Group, 12 - UI_Tf_Group, 13 - UI_Comp_Sw) | Enumeration
12583 | DNOM Component | UI Container | UICNTR |  | FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean
12584 | DNOM Component | UI Container | UICNTR |  | FUNCTYPE | Dynamic array of objects collected in the UI container | Enumeration
12585 | DNOM Component | UI Container | UICNTR | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12586 | DNOM Component | UI Container | UICNTR | input | JUNCCONT | Pointer to the junction container | String
12587 | DNOM Component | UI Container | UICNTR | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
12588 | DNOM Component | UI Container | UICNTR | input | NAME | Object name | String |  |  |  | DNMOBJ
12589 | DNOM Component | UI Container | UICNTR |  | NUMOBJ | The number of objects contained in the UI container | Integer |  | count | count
12590 | DNOM Component | UI Container | UICNTR |  | PERMITAREAID | UI container’s permit area ID | String
12591 | DNOM Component | Vault | VAULT | input | JUNCCONT.GEOX | X geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12592 | DNOM Component | Vault | VAULT | input | JUNCCONT.GEOY | Y geoschematic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12593 | DNOM Component | Vault | VAULT | input | JUNCCONT.NTPFLAG | Enumerated NTP flag | String |  |  |  | JUNCCT
12594 | DNOM Component | Vault | VAULT | input | JUNCCONT.RAWX | X geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12595 | DNOM Component | Vault | VAULT | input | JUNCCONT.RAWY | Y geographic coordinate of this container or its parent or its parent's parent, etc. | String |  |  |  | JUNCCT
12596 | DNOM Component | Vault | VAULT | input | JUNCCONT.TYPEMASK | Type | String |  |  |  | JUNCCT
12597 | DNOM Component | UI Container | UICNTR | input | PLACEMNT | Pointer to the UI container placement | String
12598 | DNOM Component | UI Container | UICNTR |  | RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean
12599 | DNOM Component | UI Container | UICNTR | input | SERVCNTR | Pointer to the associated service center | String
12600 | DNOM Component | UI Container | UICNTR | input | STATIONNAME | Nominal station name of the UI container | String
12601 | DNOM Component | UI Container | UICNTR |  | UICNTMSK | UI bitmask | Integer
12602 | DNOM Component | UI Container | UICNTR | input | UICONTEMSNAME | Nominal EMS station name of the UI container | String
12603 | DNOM Component | UI Container | UICNTR |  | UICONTHASSCADAMEAS | Flag indicating that the UI container has SCADA measurements | Boolean
12604 | DNOM Component | UI Container | UICNTR | input | UICONTSTATNAME | Substation name the UI container belongs to | String
12605 | DNOM Component | UI Container | UICNTR | input | USRVLTLV | Pointer to the user voltage level | String
12606 | DNOM Component | UI Container | UICNTR | input | VLTOBJ | Dynamic array of objects collected in the UI container | String
12607 | DNOM Component | UI Container | UICNTR | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
12608 | DNOM Component | UI Container | UICNTR | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
12609 | DNOM Component | User Voltage Level | UVLTLV |  | COLORVLT | Associated color used for display purposes | Integer
12610 | DNOM Component | User Voltage Level | UVLTLV |  | DISTVLTL | Flag indicating that the voltage level represents a distribution voltage level (true - distribution, false - transmission) | Boolean
12611 | DNOM Component | User Voltage Level | UVLTLV | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12612 | DNOM Component | Vault | VAULT | input | OWNEDOBJ.AREAIND | Dynamic array of permission area indices of collected objects | String |  |  |  | DNMOBJ
12613 | DNOM Component | Vault | VAULT | input | OWNEDOBJ.DNOMX | Dynamic array of X coordinations of collected objects | String |  |  |  | DNMOBJ
12614 | DNOM Component | Vault | VAULT | input | OWNEDOBJ.DNOMY | Dynamic array of Y coordinations of collected objects | String |  |  |  | DNMOBJ
12615 | DNOM Component | Vault | VAULT | input | OWNEDOBJ.ID | Dynamic array of IDs of collected objects | String |  |  |  | DNMOBJ
12616 | DNOM Component | Vault | VAULT | input | OWNEDOBJ.NAME | Dynamic array of names of collected objects | String |  |  |  | DNMOBJ
12617 | DNOM Component | User Voltage Level | UVLTLV |  | KVLLVVAL | Voltage level (line to line) | Integer |  | kV | kV
12618 | DNOM Component | User Voltage Level | UVLTLV | input | NAME | Object name | String |  |  |  | DNMOBJ
12619 | DNOM Component | Vault | VAULT | input | PLACEMNT.AX | Dynamic array of X coordinates | String |  |  |  | CMBPLS
12620 | DNOM Component | Vault | VAULT | input | PLACEMNT.AY | Dynamic array of Y coordinates | String |  |  |  | CMBPLS
12621 | DNOM Component | Vault | VAULT | input | PLACEMNT.BITMASK | Bitmask index. Bit positions are as follows: 0 - Removed (i.e. could remove the booleans that are there now on polys, switches, and switch labels placements); 1 - Feeder Main. Set by scrubber/converter 1= feeder main. For non-electrical objects, make a guess; 2 - Scrubbed. Set by a scrubber if it was added after the converter; 3 - Geographic (?) . If 1, then it is somewhat geographic. Scrubber/converter would initialize geographic geometry placements to 1, others to 0; 4 - Declutter 1 -May be set to 1 by scrubber. 1 = hide if declutter condition is met (zoom matches some range); 5 - Declutter 2; 6 - Declutter 3; 7 - Declutter 4; 8-15 - User bits to be set by scrubber; 16-31 - Reserved for future items. | Integer |  |  |  | PLACE
12622 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY | Pointer to associated geometry | String | N/A | N/A |  | PLACE
12623 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.DEFZOOML | Default zoom level | Float |  |  |  | GEOM
12624 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.MANBOUND | Manual bounding rectangle calculated flag. Converter does not calculate the bounding rectangle if this attribute is true. | Boolean |  |  |  | GEOM
12625 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.XFOUR | X coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
12626 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.XONE | X coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
12627 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.XTHREE | X coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
12628 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.XTWO | X coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
12629 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.YFOUR | Y coordinate of the fourth boundary rectangle vertice | Float |  |  |  | GEOM
12630 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.YONE | Y coordinate of the first boundary rectangle vertice | Float |  |  |  | GEOM
12631 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.YTHREE | Y coordinate of the third boundary rectangle vertice | Float |  |  |  | GEOM
12632 | DNOM Component | Vault | VAULT | input | PLACEMNT.GEOMETRY.YTWO | Y coordinate of the second boundary rectangle vertice | Float |  |  |  | GEOM
12633 | DNOM Component | Vault | VAULT | input | PLACEMNT.NUMVERT | Number of vertices (line or polygon) | String |  |  |  | CMBPLS
12634 | DNOM Component | Vault | VAULT | input | PLACEMNT.ROTATION | Rotation anagle of the placement | String |  | degrees | degrees | CMBPLS
12635 | DNOM Component | Vault | VAULT | input | PLACEMNT.SIZE | Size of the object | String |  |  |  | CMBPLS
12636 | DNOM Component | Vault | VAULT | input | PLACEMNT.X | X coordinate of the placement | String |  |  |  | CMBPLS
12637 | DNOM Component | Vault | VAULT | input | PLACEMNT.Y | Y coordinate of the placement | String |  |  |  | CMBPLS
12638 | DNOM Component | Vault | VAULT | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
12639 | DNOM Component | Vault | VAULT | input | AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12640 | DNOM Component | Vault | VAULT | input | BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
12641 | DNOM Component | Vault | VAULT | input | DNOMRECORDNAME | Object name in the DNOM | String |  |  |  | DNMOBJ
12642 | DNOM Component | Vault | VAULT | input | DNOMTABNAME | The DNOM table name of the vault | String
12643 | DNOM Component | Vault | VAULT | input | DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12644 | DNOM Component | Vault | VAULT | input | VLTOBJ.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12645 | DNOM Component | Vault | VAULT | input | VLTOBJ.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12646 | DNOM Component | Vault | VAULT | input | VLTOBJ.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12647 | DNOM Component | Vault | VAULT | input | VLTOBJ.ID | Unique and persistent ID of the object | String |  |  |  | DNMOBJ
12648 | DNOM Component | Vault | VAULT | input | VLTOBJ.NAME | Name of the object | String |  |  |  | DNMOBJ
12649 | DNOM Component | Vault | VAULT | input | DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12650 | DNOM Component | Vault | VAULT | input | ESCOINVAULTCNT | Specifies whether ESCO switch is in the vault container | Boolean
12651 | DNOM Component | Vault | VAULT |  | EXTRNOBJ | Dynamic array of external device IDs | String
12652 | DNOM Component | Vault | VAULT |  | FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean
12653 | DNOM Component | Vault | VAULT | input | ID | Object unique ID | String |  |  |  | DNMOBJ
12654 | DNOM Component | Vault | VAULT |  | IVLTTYPE | Vault type enumeration | Integer
12655 | DNOM Component | Vault | VAULT | input | JUNCCONT | Pointer to the junction container | String
12656 | DNOM Component | Vault | VAULT | input | LOCATION | Object location, X and Y coordinates | String |  |  |  | DNOMOBJ
12657 | DNOM Component | Vault | VAULT | input | NAME | Object name | String |  |  |  | DNMOBJ
12658 | DNOM Component | Vault | VAULT | input | NELECSUBNAME | Name of the substation the non-electrical object belongs to | String |  |  |  | NONELECTRICAL
12659 | DNOM Component | Vault | VAULT | input | NMEXTOBJ | The number of objects owned in external station | Integer |  | count | count
12660 | DNOM Component | Vault | VAULT | input | NMOWNOBJ | The number of objects contained in the vault (new collection) | Integer |  | count | count
12661 | DNOM Component | Vault | VAULT | input | NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
12662 | DNOM Component | Vault | VAULT | input | NUM1PHRECONFIGSW | The number of 1-phase reconfigurable switches contained in the cabinet | String
12663 | DNOM Component | Vault | VAULT | input | NUM1PHSWITCHES | The number of 1-phase switches contained in the cabinet | String
12664 | DNOM Component | Vault | VAULT | input | NUM3PHRECONFIGSW | The Number of reconfigurable 3-phase switches contained in the cabinet | String
12665 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12666 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12667 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12668 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT.ID | ID of the object | String |  |  |  | DNMOBJ
12669 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT.NAME | Object name | String |  |  |  | DNMOBJ
12670 | DNOM Component | Vault | VAULT | input | NUM3PHSWITCHES | The number of 3-phase switches contained in the cabinet | String
12671 | DNOM Component | Vault | VAULT | input | NUM3PHSWNOTINCAB | The number of thee-phase switches not in the cabinet | Integer
12672 | DNOM Component | Vault | VAULT |  | NUMCABINETS | Number of cabinets in the vault | String
12673 | DNOM Component | Vault | VAULT | input | NUMOBJ | The number of objects contained in the vault. | Integer
12674 | DNOM Component | Vault | VAULT | input | NUMRECONFIGCABS | The number of reconfigurable cabinets | Integer
12675 | DNOM Component | Vault | VAULT | input | OWNEDOBJ | Pointer to the dynamic array of objects collected in the vault | String
12676 | DNOM Component | Vault | VAULT | input | PERMITAREAID | Object’s permit area ID. | String |  |  |  | TOPOCOMP
12677 | DNOM Component | Vault | VAULT | input | PLACEMNT | Pointer to the vault placement | String
12678 | DNOM Component | Vault | VAULT |  | RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean
12679 | DNOM Component | Vault | VAULT | input | REFDRAW | Reference drawing | String
12680 | DNOM Component | Vault | VAULT | input | VAULTFEEDMAIN | Flag indicating whether the vault is connected to the feeder main. | Boolean
12681 | DNOM Component | Vault | VAULT | input | VAULTSWCABSECNAME | Alternate name for vault (based on alternate name for a device contained within the vault). | String
12682 | DNOM Component | Vault | VAULT | input | VAULTTYPE | Vault type description. | String
12683 | DNOM Component | Vault | VAULT | input | VLTOBJ | Dynamic array of objects collected in the vault | String
12684 | DNOM Component | Vault | VAULT | input | XCOORDINATE | X coordinate of the object | String |  |  |  | DNMOBJ
12685 | DNOM Component | Vault | VAULT | input | YCOORDINATE | Y coordinate of the object | String |  |  |  | DNMOBJ
12686 | DNOM Component Placement | Value Placement | VLEPLE |  | ANCHORPOINT | Enumeration of the value placement anchor point | Enumeration
12687 | DNOM Component Placement | Value Placement | VLEPLE |  | ARROWLABELCALCULATED | Used to manually indicate the arrow angle | Integer
12688 | DNOM Component Placement | Value Placement | VLEPLE |  | ARROWROTATION | Indicates whether the initial arrow angle is calculated by the Converter or set manually | Boolean
12689 | DNOM Component Placement | Value Placement | VLEPLE |  | CMPONENTTYPE | Associated component type | String
12690 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX1 | The color of the label and arrow of the measurement type 1 | Integer
12691 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX2 | The color of the label and arrow of the measurement type 2 | Integer
12692 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX3 | The color of the label and arrow of the measurement type 3 | Integer
12693 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX4 | The color of the label and arrow of the measurement type 4 | Integer
12694 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX5 | The color of the label and arrow of the measurement type 5 | Integer
12695 | DNOM Component Placement | Value Placement | VLEPLE |  | COLORIDX6 | The color of the label and arrow of the measurement type 6 | Integer
12696 | DNOM Component Placement | Value Placement | VLEPLE |  | CONNPOINTX | X coordinate of the value placement connection point | Integer
12697 | DNOM Component Placement | Value Placement | VLEPLE |  | CONNPOINTY | Y coordinate of the value placement connection point | Integer
12698 | DNOM Component Placement | Value Placement | VLEPLE |  | DNOMID | DNOM ID of the DNOM object | String
12699 | DNOM Component Placement | Value Placement | VLEPLE | input | DNOMOBJECT | Pointer to the associated object | String
12700 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
12701 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12702 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
12703 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12704 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12705 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
12706 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean |  |  |  | VAULT
12707 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.ID | ID of the object | String |  |  |  | DNMOBJ
12708 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.IVLTTYPE | Vault type enumeration | Integer |  |  |  | VAULT
12709 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.NAME | Object name | String |  |  |  | DNMOBJ
12710 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.NMEXTOBJ | The number of objects owned in external station | Integer |  |  |  | VAULT
12711 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.NMOWNOBJ | The number of objects contained in the vault (new collection) | Integer |  |  |  | VAULT
12712 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
12713 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.NUMOBJ | The number of objects contained in the vault (old collection) | Integer |  |  |  | VAULT
12714 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean |  |  |  | VAULT
12715 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT.REFDRAW | Reference drawing | String |  |  |  | VAULT
12716 | DNOM Component Placement | Value Placement | VLEPLE |  | GEOMETRYTYPE | Geometry type | String
12717 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.ALTERNATENAME | Alternate name | String |  |  |  | NONELECTRICAL
12718 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.AREAIND | Integer (index) into station permission area list | Integer |  |  |  | DNMOBJ
12719 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.BOUNDARY | Flag indicating the non-electrical object is on the station boundary | Boolean |  |  |  | NONELECTRICAL
12720 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.DNOMX | X coordinate | Float |  |  |  | DNMOBJ
12721 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.DNOMY | Y coordinate | Float |  |  |  | DNMOBJ
12722 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.EXSBNAME | External substation name | String |  |  |  | NONELECTRICAL
12723 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.FEEDMAIN | A flag indicating that the UI container is on feeder backbone | Boolean |  |  |  | VAULT
12724 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.ID | ID of the object | String |  |  |  | DNMOBJ
12725 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.IVLTTYPE | Vault type enumeration | Integer |  |  |  | VAULT
12726 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.NAME | Object name | String |  |  |  | DNMOBJ
12727 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.NMEXTOBJ | The number of objects owned in external station | Integer |  |  |  | VAULT
12728 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.NMOWNOBJ | The number of objects contained in the vault (new collection) | Integer |  |  |  | VAULT
12729 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.NONELBIT | Bitmask with flags for UI and boundary processing | Integer |  |  |  | NONELECTRICAL
12730 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.NUMOBJ | The number of objects contained in the vault (old collection) | Integer |  |  |  | VAULT
12731 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.RECONFIG | A flag indicating that the UI container is on non-reconfigurable section | Boolean |  |  |  | VAULT
12732 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT.REFDRAW | Reference drawing | String |  |  |  | VAULT
12733 | DNOM Component Placement | Value Placement | VLEPLE |  | ID | ID of the DNOM object | String
12734 | DNOM Component Placement | Value Placement | VLEPLE |  | ISMEASUREMENT | A flag indicating the measurement | Boolean
12735 | DNOM Component Placement | Value Placement | VLEPLE |  | LABELROTATION | Manually indicated text angle | Integer
12736 | DNOM Component Placement | Value Placement | VLEPLE |  | LABELROTCALCULATED | Indicates whether the initial text angle is calculated by the Converter or set manually | Boolean
12737 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL1 | The label/text to show next to the measurement value 1 | String
12738 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL2 | The label/text to show next to the measurement value 2 | String
12739 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL3 | The label/text to show next to the measurement value 3 | String
12740 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL4 | The label/text to show next to the measurement value 4 | String
12741 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL5 | The label/text to show next to the measurement value 5 | String
12742 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASLABEL6 | The label/text to show next to the measurement value 6 | String
12743 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW1 | Indicates whether the arrow for measurement type 1 is shown or not | Boolean
12744 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW2 | Indicates whether the arrow for measurement type 2 is shown or not | Boolean
12745 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW3 | Indicates whether the arrow for measurement type 3 is shown or not | Boolean
12746 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW4 | Indicates whether the arrow for measurement type 4 is shown or not | Boolean
12747 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW5 | Indicates whether the arrow for measurement type 5 is shown or not | Boolean
12748 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASSHOWARROW6 | Indicates whether the arrow for measurement type 6 is shown or not | Boolean
12749 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE1 | Measurement type 1 associated with the value placement | Enumeration
12750 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE2 | Measurement type 2 associated with the value placement | Enumeration
12751 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE3 | Measurement type 3 associated with the value placement | Enumeration
12752 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE4 | Measurement type 4 associated with the value placement | Enumeration
12753 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE5 | Measurement type 5 associated with the value placement | Enumeration
12754 | DNOM Component Placement | Value Placement | VLEPLE |  | MEASTYPE6 | Measurement type 6 associated with the value placement | Enumeration
12755 | DNOM Component Placement | Value Placement | VLEPLE |  | NAME | Name of the DNOM object | String
12756 | DNOM Component Placement | Value Placement | VLEPLE |  | SHOWCONNPOINT | A flag indicating that the connection points are displayed | Boolean
12757 | DNOM Component Placement | Value Placement | VLEPLE |  | XVLPLACE | X coordinate of the value placement | Integer
12758 | DNOM Component Placement | Value Placement | VLEPLE |  | YVLPLACE | Y coordinate of the value placement | Integer
12759 | Virtual Object | Voltage Limit | VOLTLIM | input | ALTID | Returns the SECONDID if the field exists, otherwise returns the ADDRESS | String
12760 | DNOM Component | Vault | VOLTLV |  | NOMVOLT | Voltage level (line to neutral) | Integer
12761 | DNOM Component Placement | Vault Label Placement | VTLBPL | input | VAULT | Pointer to the associated vault | String
12762 | DNOM Component Placement | Vault Placement | VTPLE | input | VAULT | Pointer to the associated vault | String

## Query Object Mapping
Object Type | Object Description | Object Name | Mapped Real Queryable Object Record Name | Mapped Real Queryable Object Record Description
DNOM Group Object | Combination Placement | CMBPLS | CBPLE | Switch Cabinet Placement
DNOM Group Object | Combination Placement | CMBPLS | CSWPLE | Composite Switch Placement
DNOM Group Object | Combination Placement | CMBPLS | UICNTP | UI Container Placement
DNOM Group Object | Combination Placement | CMBPLS | VTPLE | Vault Placement
DNOM Group Object | Common Electrical | COMELC | BUS | Bus
DNOM Group Object | Common Electrical | COMELC | FLTIND | Fault Indicator
DNOM Group Object | DNOM Object | DNMOBJ | All | All types except for placements
DNOM Group Object | DNOM Object | DNOMOBJ | All | All types except for placements
DNOM Group Object | Lavel Placement | LBPLCE | BSLBPL | Bus Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | CBLBPL | Switch Cabinet Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | CSLBPL | Composite Switch Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | DBLBPL | Duct Bank Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | DTLBPL | Distribution Transformer Bank Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | ENERGYRESLBPL | Energy Resource Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | FDLBPL | Feeder Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | FILBPL | Fault Indicator Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | GNLBPL | Generator Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | GRLBPL | Ground Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | LDLBPL | Load Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | LELPLE | Loop End Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | LNLBPL | Line Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | MHLBPL | Manhole Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | RCLBPL | Reserved Capacity Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SBLBPL | Splice Box Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SELBPL | Series Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SHLBPL | Shunt Impedance Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SLLBPL | Sensor Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | STLBPL | Substation Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SVLBPL | Service Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | SWLBPL | Switch Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | TBLBPL | Transformer Bank Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | TFLBPL | Transformer Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | UICLBL | UI Container Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | VTLBPL | Vault Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | INVERTERGRPLBPL | Inverter Group Label Placement
DNOM Group Object | Lavel Placement | LBPLCE | INVERTERLBPL | Inverter Label Placement
DNOM Group Object | None Electrical Device | NONELECTRICAL | CABNET | Switch Cabinet
DNOM Group Object | None Electrical Device | NONELECTRICAL | DBANK | Duct Bank
DNOM Group Object | None Electrical Device | NONELECTRICAL | MHOLE | Manhole
DNOM Group Object | None Electrical Device | NONELECTRICAL | SPLBOX | Splice Box
DNOM Group Object | None Electrical Device | NONELECTRICAL | VAULT | Vault
DNOM Group Object | None Electrical Device | NONELECTRICAL | RESERVEDCAPACITY | Reserved Capacity
DNOM Group Object | Placement Object | PLACE | CMBPLS | Combination Placement
DNOM Group Object | Placement Object | PLACE | LBPLCE | Label Placement
DNOM Group Object | Placement Object | PLACE | PTPLCE | Point Placement
DNOM Group Object | Placement Object | PLACE | PYPLCE | Poly Placement
DNOM Group Object | Placement Object | PLACE | TSWPLE | Temporary Switch Placement
DNOM Group Object | Placement Object | PLACE | VLEPLE | Value Placement
DNOM Group Object | Point Placement | PTPLCE | CUTPLE | Cut Placement
DNOM Group Object | Point Placement | PTPLCE | DTFPLE | Distribution Transformer Bank Placement
DNOM Group Object | Point Placement | PTPLCE | ENERGYPLE | Energy Resource Placement
DNOM Group Object | Point Placement | PTPLCE | FIPLE | Fault Indicator Placement
DNOM Group Object | Point Placement | PTPLCE | GENPLE | Generator Placement
DNOM Group Object | Point Placement | PTPLCE | ENERGYPLE | Energy Resource Placement
DNOM Group Object | Point Placement | PTPLCE | INVERTERPLE | Inverter Placement
DNOM Group Object | Point Placement | PTPLCE | INVERTERGRPPLE | Inverter Group Placement
DNOM Group Object | Point Placement | PTPLCE | GNDPLE | Ground Placement
DNOM Group Object | Point Placement | PTPLCE | LDPLE | Load Placement
DNOM Group Object | Point Placement | PTPLCE | MHPLE | Manhole Placement
DNOM Group Object | Point Placement | PTPLCE | RCPLE | Reserved Capacity Placement
DNOM Group Object | Point Placement | PTPLCE | PHJPLE | Phase Jumper Placement
DNOM Group Object | Point Placement | PTPLCE | SERPLE | Series Placement
DNOM Group Object | Point Placement | PTPLCE | SHPPLE | Shunt Impedance Placement
DNOM Group Object | Point Placement | PTPLCE | SLPLE | Sensor Placement
DNOM Group Object | Point Placement | PTPLCE | SVCPLE | Service Placement
DNOM Group Object | Point Placement | PTPLCE | SWTPLE | Switch Placement
DNOM Group Object | Point Placement | PTPLCE | TAGPLE | Tag Placement
DNOM Group Object | Point Placement | PTPLCE | TCKPLE | Trouble Ticket Placement
DNOM Group Object | Point Placement | PTPLCE | TFBPLE | Transformer Bank Placement
DNOM Group Object | Point Placement | PTPLCE | TFPLE | Transformer Placement
DNOM Group Object | Point Placement | PTPLCE | TGRPLE | Temporary Ground Placement
DNOM Group Object | Poly Placement | PYPLCE | BUSPLE | Bus Placement
DNOM Group Object | Poly Placement | PYPLCE | DBPLE | Duct Bank Placement
DNOM Group Object | Poly Placement | PYPLCE | FDPOPL | Feeder Polygon Placement
DNOM Group Object | Poly Placement | PYPLCE | LNPLE | Line Placement
DNOM Group Object | Poly Placement | PYPLCE | SBPLE | Splice Box Placement
DNOM Group Object | Poly Placement | PYPLCE | SWPOPL | Switch Polygon Placement
DNOM Group Object | Poly Placement | PYPLCE | TSWPLE | Temporary Switch Placement
DNOM Group Object | Shunt Object | SHUNT | ENERGYRES | Energy Resource
DNOM Group Object | Shunt Object | SHUNT | GEN | Generator
DNOM Group Object | Shunt Object | SHUNT | GRND | Ground
DNOM Group Object | Shunt Object | SHUNT | LOAD | Load
DNOM Group Object | Shunt Object | SHUNT | RFBSIF | Reference Bus Interface
DNOM Group Object | Shunt Object | SHUNT | SHIMP | Shunt Impedance
DNOM Group Object | Shunt Object | SHUNT | SV | Static VAR Compensator
DNOM Group Object | Substation Polygon Placement | STPOPL | PYPLCE | Substation Polygon Placement
DNOM Group Object | Substation Placement | SUBPLE | PYPLCE | Substation Placement
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | CUT | Cut
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | DISTTF | Distribution Transformer
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | ENERGYRES | Energy Resource
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | GEN | Generator
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | GRND | Ground
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | LN | Line
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | LOAD | Load
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | RFBSIF | Reference Bus Interface
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | SERIES | Series
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | SHIMP | Shunt Impedance
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | SV | Static VAR Compensator
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | SVECTR | Service Center
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | SWT | Switch
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | TMPSWT | Temporary Switch
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | TF | Transformer
DNOM Group Object | Topology Object | TOPOLOGYOBJECT | RESERVEDCAPACITY | Reserved Capacity
Virtual Object | Abnormal | ABNRML | COMPSW | Composite Switch
Virtual Object | Abnormal | ABNRML | CUT | Cut
Virtual Object | Abnormal | ABNRML | DISTTF | Distribution Transformer
Virtual Object | Abnormal | ABNRML | SWT | Switch
Virtual Object | Abnormal | ABNRML | TEMPGROUND | Temporary Ground
Virtual Object | Abnormal | ABNRML | TMPSWT | Temporary Switch
Virtual Object | All Energy Sources | ALLENERGYSOURCE | ENERGYRES | Energy Resource
Virtual Object | All Energy Sources | ALLENERGYSOURCE | GEN | Generator
Virtual Object | Transformer Component | ALLTF | DISTTF | Distribution Transformer
Virtual Object | Transformer Component | ALLTF | TF | Transformer
Virtual Object | Branch | BRANCH | CUT | Cut
Virtual Object | Branch | BRANCH | LN | Line
Virtual Object | Branch | BRANCH | SWT | Switch
Virtual Object | Branch and Shunt | BRNCHSHUNT | DISTTF | Distribution Transformer
Virtual Object | Branch and Shunt | BRNCHSHUNT | ENERGYRES | Energy Resource
Virtual Object | Branch and Shunt | BRNCHSHUNT | GEN | Generator
Virtual Object | Branch and Shunt | BRNCHSHUNT | LN | Line
Virtual Object | Branch and Shunt | BRNCHSHUNT | LOAD | Load
Virtual Object | Branch and Shunt | BRNCHSHUNT | RFBSIF | Reference Bus Interface
Virtual Object | Branch and Shunt | BRNCHSHUNT | SERIES | Series Reactor
Virtual Object | Branch and Shunt | BRNCHSHUNT | SWT | Switch
Virtual Object | Branch and Shunt | BRNCHSHUNT | TF | Transformer
Virtual Object | Branch and Shunt | BRNCHSHUNT | TMPSWT | Temporary Switch
Virtual Object | Bus and Regulator | BUSANDREGULATOR | BUS | Bus
Virtual Object | Bus and Regulator | BUSANDREGULATOR | TF | Transformer
Virtual Object | Container Object | CONTAINER | CABNET | Switch Cabinet
Virtual Object | Container Object | CONTAINER | VAULT | Vault
Virtual Object | Container Object | CONTAINER | UICNTP | UI Container Placement
Virtual Object | Container Object | CONTAINER | COMPSW | Composite Switch
Virtual Object | DMS Component | COMP | LN | Line
Virtual Object | DMS Component | COMP | LOAD | Load
Virtual Object | DMS Component | COMP | SWT | Switch
Virtual Object | LVM Control Device | CONTROLDEV | TF | Transformer
Virtual Object | LVM Control Device | CONTROLDEV | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | LVM Control Device | CONTROLDEV | GEN | Generator
Virtual Object | LVM Control Device | CONTROLDEV | ENERGYRES | Energy Resource
Virtual Object | LVM Control Device | CONTROLDEV | SWT | Switch
Virtual Object | De-Energized | DEENRG | LOAD | Load
Virtual Object | DMS Branch Component | DMSBRANCH | CUT | Cut
Virtual Object | DMS Branch Component | DMSBRANCH | DISTTF | Distribution Transformer
Virtual Object | DMS Branch Component | DMSBRANCH | LN | Line
Virtual Object | DMS Branch Component | DMSBRANCH | SERIES | Series Reactor
Virtual Object | DMS Branch Component | DMSBRANCH | SWT | Switch
Virtual Object | DMS Branch Component | DMSBRANCH | TF | Transformer
Virtual Object | DMS Branch Component | DMSBRANCH | TMPSWT | Temporary Switch
Virtual Object | DMS Component | DMSCOMP | CUT | Cut
Virtual Object | DMS Component | DMSCOMP | DISTTF | Distribution Transformer
Virtual Object | DMS Component | DMSCOMP | ENERGYRES | Energy Resource
Virtual Object | DMS Component | DMSCOMP | GEN | Generator
Virtual Object | DMS Component | DMSCOMP | GRND | Ground
Virtual Object | DMS Component | DMSCOMP | LN | Line
Virtual Object | DMS Component | DMSCOMP | LOAD | Load
Virtual Object | DMS Component | DMSCOMP | RFBSIF | Reference Bus Interface
Virtual Object | DMS Component | DMSCOMP | SERIES | Series Reactor
Virtual Object | DMS Component | DMSCOMP | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | DMS Component | DMSCOMP | SV | SVC
Virtual Object | DMS Component | DMSCOMP | SWT | Switch
Virtual Object | DMS Component | DMSCOMP | TEMPGROUND | Temporary Ground
Virtual Object | DMS Component | DMSCOMP | TF | Transformer
Virtual Object | DMS Component | DMSCOMP | TMPSWT | Temporary Switch
Virtual Object | DMS Shunt Component | DMSSHUNT | SERIES | Series Reactor
Virtual Object | DMS Shunt Component | DMSSHUNT | ENERGYRES | Energy Resource
Virtual Object | DMS Shunt Component | DMSSHUNT | GEN | Generator
Virtual Object | DMS Shunt Component | DMSSHUNT | GRND | Ground
Virtual Object | DMS Shunt Component | DMSSHUNT | LOAD | Load
Virtual Object | DMS Shunt Component | DMSSHUNT | RFBSIF | Reference Bus Interface
Virtual Object | DMS Shunt Component | DMSSHUNT | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | DMS Shunt Component | DMSSHUNT | SV | SVC
Virtual Object | DMS Shunt Component | DMSSHUNT | TEMPGROUND | Temporary Ground
Virtual Object | Energizing Source | ENGZSOURCE | GEN | Generator
Virtual Object | Energizing Source | ENGZSOURCE | INTFC | Interface
Virtual Object | Flow Limit | FLWLIM | DISTTF | Distribution Transformer
Virtual Object | Flow Limit | FLWLIM | LN | Line
Virtual Object | Flow Limit | FLWLIM | SERIES | Series Reactor
Virtual Object | Flow Limit | FLWLIM | SWT | Switch
Virtual Object | Flow Limit | FLWLIM | TF | Transformer
Virtual Object | Flow Limit | FLWLIM | TMPSWT | Temporary Switch
Virtual Object | Future Topology Component | FUTURETOP | BUS | Bus
Virtual Object | Future Topology Component | FUTURETOP | DISTTF | Distribution Transformer
Virtual Object | Future Topology Component | FUTURETOP | LN | Line
Virtual Object | Future Topology Component | FUTURETOP | LOAD | Load
Virtual Object | Future Topology Component | FUTURETOP | SERIES | Series Reactor
Virtual Object | Future Topology Component | FUTURETOP | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | Future Topology Component | FUTURETOP | SWT | Switch
Virtual Object | Future Topology Component | FUTURETOP | TF | Transformer
Virtual Object | Global Find Placement | GSPLACEMENT | BUSPLE | Bus placements
Virtual Object | Global Find Placement | GSPLACEMENT | CBPLE | Switch cabinet placements
Virtual Object | Global Find Placement | GSPLACEMENT | CSWPLE | Composite switch placements
Virtual Object | Global Find Placement | GSPLACEMENT | CUTPLE | Cut placements
Virtual Object | Global Find Placement | GSPLACEMENT | DBPLE | Duct bank placements
Virtual Object | Global Find Placement | GSPLACEMENT | DTFPLE | Distribution transformer placements
Virtual Object | Global Find Placement | GSPLACEMENT | FIPLE | Fault indicator placements
Virtual Object | Global Find Placement | GSPLACEMENT | GENPLE | Generator placements
Virtual Object | Global Find Placement | GSPLACEMENT | GNDPLE | Ground device placements
Virtual Object | Global Find Placement | GSPLACEMENT | LDPLE | Load placements
Virtual Object | Global Find Placement | GSPLACEMENT | LNPLE | Line placements
Virtual Object | Global Find Placement | GSPLACEMENT | MHPLE | Manhole placements
Virtual Object | Global Find Placement | GSPLACEMENT | SBPLE | Splice box placements
Virtual Object | Global Find Placement | GSPLACEMENT | SERPLE | Series reactor placements
Virtual Object | Global Find Placement | GSPLACEMENT | SHPPLE | Shunt impedance (capacitor) placements
Virtual Object | Global Find Placement | GSPLACEMENT | SVCPLE | SVC placements
Virtual Object | Global Find Placement | GSPLACEMENT | SWTPLE | Switch placements
Virtual Object | Global Find Placement | GSPLACEMENT | TFBPLE | Transformer bank placements
Virtual Object | Global Find Placement | GSPLACEMENT | TFPLE | Transformer placements
Virtual Object | Global Find Placement | GSPLACEMENT | TGRPLE | Temporary ground placements
Virtual Object | Global Find Placement | GSPLACEMENT | TSWPLE | Jumper (temporary switch) placements
Virtual Object | Global Find Placement | GSPLACEMENT | UICNTP | UI container placements
Virtual Object | Global Find Placement | GSPLACEMENT | VTPLE | Vault placements
Virtual Object | Inline Branches | INLINEBR | LN | Line
Virtual Object | Inline Branches | INLINEBR | TF | Transformer
Virtual Object | Inline Branches | INLINEBR | SWT | Switch
Virtual Object | Inline Branches | INLINEBR | SERIES | Series Reactor
Virtual Object | Load and Bus | LDBUS | BUS | Bus
Virtual Object | Load and Bus | LDBUS | LOAD | Load
Virtual Object | Load Limit | LDLIM | LOAD | Load
Virtual Object | Line and Series | LNSERIES | LN | Line
Virtual Object | Line and Series | LNSERIES | SERIES | Series Reactor
Virtual Object | Optimization Device | OPTDEVICE | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | Optimization Device | OPTDEVICE | TF | Transformer
Virtual Object | Optimization Device | OPTDEVICE | ENERGYRES | Energy Resource
Virtual Object | Optimization Device | OPTDEVICE | GEN | Generator
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | BUS | Bus
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | CABNET | Switch Cabinet
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | COMPSW | Composite Switch
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | CUT | Cut
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | DBANK | Duct Bank
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | DISTTF | Distribution Transformer
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | FDR | Feeder
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | FLTIND | Fault Indicator
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | GRND | Ground
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | LN | Line
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | LOAD | Load
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | SERIES | Series Reactor
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | SPLBOX | Splice Box
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | SWT | Switch
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | TF | Transformer
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | TFBNK | Transformer Bank
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | TMPSWT | Temporary Switch
Virtual Object | OSM Specific Device | OSMQUERYDEVICE | VAULT | Vault
Virtual Object | Specific Combination of Branch | SELECTBR | SWT | Switch
Virtual Object | Specific Combination of Branch | SELECTBR | TMPSWT | Temporary Switch
Virtual Object | Station Internal Input Component | STATINPUTINT | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | Station Internal Input Component | STATINPUTINT | SWT | Switch
Virtual Object | Station Internal Input Component | STATINPUTINT | TF | Transformer
Virtual Object | Station Internal Component | STATINT | LN | Line
Virtual Object | Station Internal Component | STATINT | SERIES | Series Reactor
Virtual Object | Station Internal Component | STATINT | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | Station Internal Component | STATINT | SWT | Switch
Virtual Object | Station Internal Component | STATINT | TF | Transformer
Virtual Object | Switches and Composite Switches | SWTCOMPSW | SWT | Switch
Virtual Object | Switches and Composite Switches | SWTCOMPSW | COMPSW | Composite Switch
Virtual Object | Temporary Object | TEMPOBJ | CUT | Cut
Virtual Object | Temporary Object | TEMPOBJ | TEMPGROUND | Temporary Ground
Virtual Object | Temporary Object | TEMPOBJ | TMPSWT | Temporary Switch
Virtual Object | Topology Component | TOPOCOMP | CUT | Cut
Virtual Object | Topology Component | TOPOCOMP | DISTTF | Distribution Transformer
Virtual Object | Topology Component | TOPOCOMP | ENERGYRES | Energy Resource
Virtual Object | Topology Component | TOPOCOMP | EXTBRC | External Branch
Virtual Object | Topology Component | TOPOCOMP | GEN | Generator
Virtual Object | Topology Component | TOPOCOMP | GRND | Ground
Virtual Object | Topology Component | TOPOCOMP | LN | Line
Virtual Object | Topology Component | TOPOCOMP | LOAD | Load
Virtual Object | Topology Component | TOPOCOMP | NODE | NODE
Virtual Object | Topology Component | TOPOCOMP | RFBSIF | Reference Bus Interface
Virtual Object | Topology Component | TOPOCOMP | SERIES | Series Reactor
Virtual Object | Topology Component | TOPOCOMP | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | Topology Component | TOPOCOMP | SV | SVC
Virtual Object | Topology Component | TOPOCOMP | SWT | Switch
Virtual Object | Topology Component | TOPOCOMP | TEMPGROUND | Temporary Ground
Virtual Object | Topology Component | TOPOCOMP | TF | Transformer
Virtual Object | Topology Component | TOPOCOMP | TMPSWT | Temporary Switch
Virtual Object | SCADA or DER Component | SCADA_OR_DER (or CONTROLLABLE_MEAS) | Configurable by the SCADA_OR_DER_COLLECTION parameter. By default, LOAD,GEN,ENERGYRES,SWT,TF,SHIMP,EXTBRC,RFBSIF,SV,SERIES,DISTTF | Indexed collection of SCADA or DER devices. Supports the same queries as TOPOCOMP. Filters only SCADA and DER devices.
Virtual Object | Voltage Limit | VOLTLIM | BUS | Bus
Virtual Object | Voltage Limit | VOLTLIM | LOAD | Load
Virtual Object | DNOM Component | DNOMCOMP | CUT | Cut
Virtual Object | DNOM Component | DNOMCOMP | DISTTF | Distribution Transformer
Virtual Object | DNOM Component | DNOMCOMP | ENERGYRES | Energy Resource
Virtual Object | DNOM Component | DNOMCOMP | EXTBRC | External Branch
Virtual Object | DNOM Component | DNOMCOMP | GEN | Generator
Virtual Object | DNOM Component | DNOMCOMP | GRND | Ground
Virtual Object | DNOM Component | DNOMCOMP | LN | Line
Virtual Object | DNOM Component | DNOMCOMP | LOAD | Load
Virtual Object | DNOM Component | DNOMCOMP | NODE | NODE
Virtual Object | DNOM Component | DNOMCOMP | RFBSIF | Reference Bus Interface
Virtual Object | DNOM Component | DNOMCOMP | SERIES | Series Reactor
Virtual Object | DNOM Component | DNOMCOMP | SHIMP | Shunt Impedance (Capacitor)
Virtual Object | DNOM Component | DNOMCOMP | SV | SVC
Virtual Object | DNOM Component | DNOMCOMP | SWT | Switch
Virtual Object | DNOM Component | DNOMCOMP | TEMPGROUND | Temporary Ground
Virtual Object | DNOM Component | DNOMCOMP | TF | Transformer
Virtual Object | DNOM Component | DNOMCOMP | TMPSWT | Temporary Switch
Virtual Object | DNOM Component | DNOMCOMP | BUS | Bus
Virtual Object | DNOM Component | DNOMCOMP | CABNET | Switch Cabinet
Virtual Object | DNOM Component | DNOMCOMP | VAULT | Vault
Virtual Object | DNOM Component | DNOMCOMP | SENSOR | Sensor
Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | ENERGYRES | Energy Resource
Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | GEN | Generator
Virtual Object | All Generators, Energy Resources, and Loads | ALLGENERATION | LOAD | Load

## Transformer Enumerations
Enumeration | Value | Literal | XML or SUB.CSV Property Name | Comments
Tap Type | 0 1 2 | None Fixed Regulating | Any of: <Transformer><PriTap> <Transformer><SecTap> <Transformer><TerTapType> | The Literal is expected in the input file, e.g. <TerTapType>None</TerTapType>
Transformer Self-protection | 0 1 2 3 4 5 6 7 8 9 | None Differential - Transformer Differential - Bus Restricted Earth Fault (REF) Buchholz Distance Tank Earth Overfluxing Thermal Other | <Transformer><SelfProtection> CSV Field: SELFPROTECTION_TF | In the input XML file, element value is a list of comma separated integers. The integer value represents the selected transformer self-protection types. Ex: <SelfProtection>2,8</SelfProtection>
Transformer Size Units | 1 2 3 | kVA MVA Regulated_kVA | <Transformer><SizeUnits> | The Literal is expected in the input file, e.g. <SizeUnits>MVA</SizeUnits>
Transformer Type | 0 1 2 3 4 5 6 | None Secondary Transformer Voltage Regulator Power Transformer Auto Transformer Step Up/Down Transformer Zigzag Transformer | <Transformer><TransType> | The Literal is expected in the input file, e.g. <TransType>Power</TransType> Note, the ADMS client displays these types distinctly based on Viewer Config settings on the Bitmaps and Object Properties tab).
Winding Type | 0 1 2 3 4 | None Delta Grounded_Wye Wye ZigZag | Any of: <Transformer><PriWinding> <Transformer><SecWinding> <Transformer><TerWinding> | The Literal is expected in the input file, e.g. <PriWinding>Delta</PriWinding> This is used for substation internals only.

## Transformer Configurations
Transformer Configuration Type | Description | TfType Name (listed in tftype.dat file) | Phasing | Primary Winding | Secondary Winding | Tertiary Winding | Secondary Lagging Primary Phase (Deg) | Tertiary Lagging Primary Phase (Deg) | Secondary Center Tap Grounded | Tertiary Center Tap Grounded | Number of Transformers | Number of Banks | Revised Phasing (Primary-Secondary) | Comments
1 | Wye/Wye Transformer | StarStarX | 3 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 0°
2 | Wye/Wye Bank | StarStarBankX | 1 | Wye | Wye | -- | 0 | -- | No | -- | 3 | 1 |  | Single-phase non split winding for making banked wye/wye transformer with secondary lagging primary by 0°
3 | Wye/Delta Transformer | StarDelta1ModX | 3 | Wye | Delta | -- | 30 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 30°
4 | Wye/Delta Bank | StarDeltaBankModX | 1 | Wye | Delta | -- | 30 | -- | Yes | -- | 3 | 1 |  | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 30°
5 | Open Wye/Open Delta Bank | StarDeltaBankModX | 1 | Wye | Delta | -- | 30 | -- | Yes | -- | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 30°
6 | Delta/Delta Transformer | DeltaDeltaMod | 3 | Delta | Delta | -- | 0 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 0°
7 | Delta/Delta Bank | DeltaDeltaBankMod | 1 | Delta | Delta | -- | 0 | -- | Yes | -- | 3 | 1 |  | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 0°
8 | Delta/Wye Transformer | DeltaStar1 | 3 | Delta | Wye | -- | 30 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/wye transformer with secondary lagging primary by 30°
9 | Delta/Wye Bank | DeltaStarBank | 1 | Delta | Wye | -- | 30 | -- | No | -- | 3 | 1 | BA->bn CB->cn AC->an | Single-phase non split winding for delta/wye bank with secondary lagging primary by 30°
10 | Single-Phase Regulator | AutoBankX | 1 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Single-phase autotransformer (regulator) with neutrals
11 | Three-Phase Regulator | Auto3X | 3 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Three-phase autotransformers (regulator) with neutrals
12 | Single-Phase Wye Transformer | Type6SimpleX | 1 | Wye | Wye | -- | 0 | -- | Yes | -- | 1 | 0 |  | Single-phase split secondary winding for wye/wye transformer with secondary lagging primary by 0° typically used to support 120/240 Volt operation
13 | Single-Phase Delta Transformer | DeltaStarSinglePhase | 1 | Delta | Wye | -- | 30 | -- | No | -- | 1 | 0 | BA->bn CB->cn AC->an | Single-phase non split winding for delta/wye bank with secondary lagging primary by 30°
14 | Single-Phase Wye/Wye Autotransformer | StarStarBankX | 1 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Single-phase non split winding for wye/wye bank with secondary lagging primary by 0°
15 | Wye/Delta Autotransformer Bank | StarDeltaBankModX | 3 | Wye | Delta | -- | 30 | -- | No | -- | 3 | 1 |  | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 30°
16 | Three-Phase Autotransformer | StarStarX | 3 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 0°
17 | Delta/Delta/Delta Three Winding Transformer | DeltaDeltaDelta | 3 | Delta | Delta | Delta | 0 | 0 | No | No | 1 | 0 |  | Three winding three-phase delta/delta/delta transformer with secondary lagging primary by 0° and tertiary lagging primary by 0°
18 | Wye/Wye/Wye Three Winding Transformer | StarStarStar | 3 | Wye | Wye | Wye | 0 | 0 | No | No | 1 | 0 |  | Three winding three-phase wye/wye/wye transformer with secondary lagging primary by 0° and tertiary lagging primary by 0°
19 | Wye/Delta/Delta Three Winding Transformer | StarDelta1Delta1 | 3 | Wye | Delta | Delta | 30 | 30 | No | No | 1 | 0 |  | Three winding three-phase wye/delta /delta transformer with secondary lagging primary by 30° and tertiary lagging primary by 30°
20 | Single-Phase Wye/Delta | SinglePhaseWyeDelta | 1 | Wye | Delta | -- | 30 | -- | No | -- | 1 | 0 |  | Single-phase non split winding for wye/delta transformer with secondary lagging primary by 30°
21 | Delta/Delta/Wye Transformer | DeltaDeltaStar | 3 | Delta | Delta | Wye | 0 | 330 | No | No | 1 | 0 |  | Three winding three-phase delta/delta/star transformer with secondary lagging primary by 0° and tertiary lagging primary by 330°
22 | Open Delta/OpenDelta Transformer | DeltaDeltaBankMod | 1 | Delta | Delta | -- | 0 | -- | Yes | -- | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 0°
23 | Wye/Wye Transformer | StarStar2X | 3 | Wye | Wye | -- | 60 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 60°
24 | Wye/Wye Transformer | StarStar4X | 3 | Wye | Wye | -- | 120 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 120°
25 | Wye/Wye Transformer | StarStar6X | 3 | Wye | Wye | -- | 180 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 180°
26 | Wye/Wye Transformer | StarStar8X | 3 | Wye | Wye | -- | 240 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 240°
27 | Wye/Wye Transformer | StarStar10X | 3 | Wye | Wye | -- | 300 | -- | No | -- | 1 | 0 |  | Two winding three-phase wye/wye transformer with secondary lagging primary by 300°
28 | Wye/Wye Bank | StarStar2BankX | 1 | Wye | Wye | -- | 60 | -- | No | -- | 3 | 1 | AN->nb BN->nc CN->na | Single-phase non split winding for wye/wye bank with secondary lagging primary by 60°
29 | Wye/Wye Bank | StarStarBankX | 1 | Wye | Wye | -- | 120 | -- | No | -- | 3 | 1 | AN->cn BN->an CN->bn | Single-phase non split winding for wye/wye bank with secondary lagging primary by 120°
30 | Wye/Wye Bank | StarStar2BankX | 1 | Wye | Wye | -- | 180 | -- | No | -- | 3 | 1 | AN->na BN->nb CN->nc | Single-phase non split winding for wye/wye bank with secondary lagging primary by 180°
31 | Wye/Wye Bank | StarStarBankX | 1 | Wye | Wye | -- | 240 | -- | No | -- | 3 | 1 | AN->bn BN->cn CN->an | Single-phase non split winding for wye/wye bank with secondary lagging primary by 240°
32 | Wye/Wye Bank | StarStar2BankX | 1 | Wye | Wye | -- | 300 | -- | No | -- | 3 | 1 | AN->nc BN->na CN->nb | Single-phase non split winding for wye/wye bank with secondary lagging primary by 300°
33 | Wye/Delta Transformer | StarDelta3 | 3 | Wye | Delta | -- | 90 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 90°
34 | Wye/Delta Transformer | StarDelta5 | 3 | Wye | Delta | -- | 150 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 150°
35 | Wye/Delta Transformer | StarDelta7 | 3 | Wye | Delta | -- | 210 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 210°
36 | Wye/Delta Transformer | StarDelta9 | 3 | Wye | Delta | -- | 270 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 270°
37 | Wye/Delta Transformer | StarDelta11 | 3 | Wye | Delta | -- | 330 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 330°
38 | Wye/Delta Transformer | StarDelta1 | 3 | Wye | Delta | -- | 30 | -- | No | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with secondary lagging primary by 30°
39 | Wye/Delta Transformer | StarDelta3ModX | 3 | Wye | Delta | -- | 90 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 90°
40 | Wye/Delta Transformer | StarDelta5ModX | 3 | Wye | Delta | -- | 150 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 150°
41 | Wye/Delta Transformer | StarDelta7ModX | 3 | Wye | Delta | -- | 210 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 210°
42 | Wye/Delta Transformer | StarDelta9ModX | 3 | Wye | Delta | -- | 270 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 270°
43 | Wye/Delta Transformer | StarDelta11ModX | 3 | Wye | Delta | -- | 330 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase star/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 330°
44 | Wye/Delta Bank | StarDeltaBank | 1 | Wye | Delta | -- | 30 | -- | No | -- | 3 | 1 |  | Single-phase non split winding for banked wye/delta transformer with secondary lagging primary by 30°
45 | Wye/Delta Bank | StarDelta3Bank | 1 | Wye | Delta | -- | 90 | -- | No | -- | 3 | 1 | AN->cb BN->ac CN->ba | Single-phase non split winding for wye/delta bank with secondary lagging primary by 90°
46 | Wye/Delta Bank | StarDelta5Bank | 1 | Wye | Delta | -- | 150 | -- | No | -- | 3 | 1 | AN->ca BN->ab CN->bc | Single-phase non split winding for wye/delta bank with secondary lagging primary by 150°
47 | Wye/Delta Bank | StarDelta7Bank | 1 | Wye | Delta | -- | 210 | -- | No | -- | 3 | 1 | AN->ba BN->cb CN->ac | Single-phase non split winding for wye/delta bank with secondary lagging primary by 210°
48 | Wye/Delta Bank | StarDelta9Bank | 1 | Wye | Delta | -- | 270 | -- | No | -- | 3 | 1 | AN->bc BN->ca CN->ab | Single-phase non split winding for wye/delta bank with secondary lagging primary by 270°
49 | Wye/Delta Bank | StarDelta11Bank | 1 | Wye | Delta | -- | 330 | -- | No | -- | 3 | 1 | AN->ac BN->ba CN->cb | Single-phase non split winding for wye/delta bank with secondary lagging primary by 330°
50 | Wye/Delta Bank | StarDelta3BankModX | 1 | Wye | Delta | -- | 90 | -- | Yes | -- | 3 | 1 | AN->cb BN->ac CN->ba | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 90°
51 | Wye/Delta Bank | StarDelta5BankModX | 1 | Wye | Delta | -- | 150 | -- | Yes | -- | 3 | 1 | AN->ca BN->ab CN->bc | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 150°
52 | Wye/Delta Bank | StarDelta7BankModX | 1 | Wye | Delta | -- | 210 | -- | Yes | -- | 3 | 1 | AN->ba BN->cb CN->ac | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 210°
53 | Wye/Delta Bank | StarDelta9BankModX | 1 | Wye | Delta | -- | 270 | -- | Yes | -- | 3 | 1 | AN->bc BN->ca CN->ab | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 270°
54 | Wye/Delta Bank | StarDelta11BankModX | 1 | Wye | Delta | -- | 330 | -- | Yes | -- | 3 | 1 | AN->ac BN->ba CN->cb | Single-phase split secondary winding for wye/delta bank with secondary lagging primary by 330°
55 | Delta/Delta Transformer | DeltaDelta | 3 | Delta | Delta | -- | 0 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 0°
56 | Delta/Delta Transformer | DeltaDelta2 | 3 | Delta | Delta | -- | 60 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 60°
57 | Delta/Delta Transformer | DeltaDelta4 | 3 | Delta | Delta | -- | 120 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 120°
58 | Delta/Delta Transformer | DeltaDelta6 | 3 | Delta | Delta | -- | 180 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 180°
59 | Delta/Delta Transformer | DeltaDelta8 | 3 | Delta | Delta | -- | 240 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 240°
60 | Delta/Delta Transformer | DeltaDelta10 | 3 | Delta | Delta | -- | 300 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with secondary lagging primary by 300°
61 | Delta/Delta Transformer | DeltaDelta2Mod | 3 | Delta | Delta | -- | 60 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 60°
62 | Delta/Delta Transformer | DeltaDelta4Mod | 3 | Delta | Delta | -- | 120 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 120°
63 | Delta/Delta Transformer | DeltaDelta6Mod | 3 | Delta | Delta | -- | 180 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 180°
64 | Delta/Delta Transformer | DeltaDelta8Mod | 3 | Delta | Delta | -- | 240 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 240°
65 | Delta/Delta Transformer | DeltaDelta10Mod | 3 | Delta | Delta | -- | 300 | -- | Yes | -- | 1 | 0 |  | Two winding three-phase delta/delta transformer with one grounded secondary center tap winding with secondary lagging primary by 300°
66 | Delta/Delta Bank | DeltaDeltaBank | 1 | Delta | Delta | -- | 0 | -- | No | -- | 3 | 1 |  | Single-phase non split winding for delta/delta bank with secondary lagging primary by 0°
67 | Delta/Delta Bank | DeltaDelta2Bank | 1 | Delta | Delta | -- | 60 | -- | No | -- | 3 | 1 | AB->cb BC->ac CA->ba | Single-phase non split winding for delta/delta bank with secondary lagging primary by 60°
68 | Delta/Delta Bank | DeltaDelta4Bank | 1 | Delta | Delta | -- | 120 | -- | No | -- | 3 | 1 | AB->ca BC->ab CA->bc | Single-phase non split winding for delta/delta bank with secondary lagging primary by 120°
69 | Delta/Delta Bank | DeltaDelta4Bank | 1 | Delta | Delta | -- | 180 | -- | No | -- | 3 | 1 | AB->ba BC->cb CA->ac | Single-phase non split winding for delta/delta bank with secondary lagging primary by 180°
70 | Delta/Delta Bank | DeltaDelta8Bank | 1 | Delta | Delta | -- | 240 | -- | No | -- | 3 | 1 | AB->bc BC->ca CA->ab | Single-phase non split winding for delta/delta bank with secondary lagging primary by 240°
71 | Delta/Delta Bank | DeltaDeltaBank | 1 | Delta | Delta | -- | 300 | -- | No | -- | 3 | 1 | AB->ac BC->ba CA->cb | Single-phase non split winding for delta/delta bank with secondary lagging primary by 300°
72 | Delta/Delta Bank | DeltaDelta2BankMod | 1 | Delta | Delta | -- | 60 | -- | Yes | -- | 3 | 1 | AB->cb BC->ac CA->ba | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 60°
73 | Delta/Delta Bank | DeltaDelta4BankMod | 1 | Delta | Delta | -- | 120 | -- | Yes | -- | 3 | 1 | AB->ca BC->ab CA->bc | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 120°
74 | Delta/Delta Bank | DeltaDelta4BankMod | 1 | Delta | Delta | -- | 180 | -- | Yes | -- | 3 | 1 | AB->ba BC->cb CA->ac | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 180°
75 | Delta/Delta Bank | DeltaDelta8BankMod | 1 | Delta | Delta | -- | 240 | -- | Yes | -- | 3 | 1 | AB->bc BC->ca CA->ab | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 240°
76 | Delta/Delta Bank | DeltaDeltaBankMod | 1 | Delta | Delta | -- | 300 | -- | Yes | -- | 3 | 1 | AB->ac BC->ba CA->cb | Single-phase split secondary winding for delta/delta bank with secondary lagging primary by 300°
77 | Delta/Wye Transformer | DeltaStar3 | 3 | Delta | Wye | -- | 90 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/star transformer with secondary lagging primary by 90°
78 | Delta/Wye Transformer | DeltaStar5 | 3 | Delta | Wye | -- | 150 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/star transformer with secondary lagging primary by 150°
79 | Delta/Wye Transformer | DeltaStar7 | 3 | Delta | Wye | -- | 210 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/star transformer with secondary lagging primary by 210°
80 | Delta/Wye Transformer | DeltaStar9 | 3 | Delta | Wye | -- | 270 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/star transformer with secondary lagging primary by 270°
81 | Delta/Wye Transformer | DeltaStar11 | 3 | Delta | Wye | -- | 330 | -- | No | -- | 1 | 0 |  | Two winding three-phase delta/star transformer with secondary lagging primary by 330°
82 | Delta/Wye Bank | DeltaStar3Bank | 1 | Delta | Wye | -- | 90 | -- | No | -- | 3 | 1 | AB->cn BC->an CA->bn | Single-phase non split winding for delta/wye bank with secondary lagging primary by 90°
83 | Delta/Wye Bank | DeltaStar5Bank | 1 | Delta | Wye | -- | 150 | -- | No | -- | 3 | 1 |  | Single-phase non split winding for delta/wye bank with secondary lagging primary by 150°
84 | Delta/Wye Bank | DeltaStar3Bank | 1 | Delta | Wye | -- | 210 | -- | No | -- | 3 | 1 | AB->bn BC->cn CA->an | Single-phase non split winding for delta/wye bank with secondary lagging primary by 210°
85 | Delta/Wye Bank | DeltaStarBank | 1 | Delta | Wye | -- | 270 | -- | No | -- | 3 | 1 | BA->cn CB->an AC->bn | Single-phase non split winding for delta/wye bank with secondary lagging primary by 270°
86 | Delta/Wye Bank | DeltaStar11Bank | 1 | Delta | Wye | -- | 330 | -- | No | -- | 3 | 1 |  | Single-phase non split winding for delta/wye bank with secondary lagging primary by 330°
87 | Single-Phase Delta Transformer | DeltaStar3SinglePhase | 1 | Delta | Wye | -- | 90 | -- | No | -- | 1 | 0 | AB->cn BC->an CA->bn | Single-phase non split winding for delta/wye bank with secondary lagging primary by 90°
88 | Single-Phase Delta Transformer | DeltaStar5SinglePhase | 1 | Delta | Wye | -- | 150 | -- | No | -- | 1 | 0 |  | Single-phase non split winding for delta/wye bank with secondary lagging primary by 150°
89 | Single-Phase Delta Transformer | DeltaStar3SinglePhase | 1 | Delta | Wye | -- | 210 | -- | No | -- | 1 | 0 | AB->bn BC->cn CA->an | Single-phase non split winding for delta/wye bank with secondary lagging primary by 210°
90 | Single-Phase Delta Transformer | DeltaStarSinglePhase | 1 | Delta | Wye | -- | 270 | -- | No | -- | 1 | 0 | BA->cn CB->an AC->bn | Single-phase non split winding for delta/wye bank with secondary lagging primary by 270°
91 | Single-Phase Delta Transformer | DeltaStar11SinglePhase | 1 | Delta | Wye | -- | 330 | -- | No | -- | 1 | 0 |  | Single-phase non split winding for delta/wye bank with secondary lagging primary by 330°
92 | Ungrounded_Wye/Wye/Delta Three Winding Transformer | UngstarStarDelta1 | 3 | Wye | Wye | Delta | 0 | 30 | No | No | 1 | 0 |  | Three winding three-phase ungrounded wye/wye/delta with secondary lagging primary by 0° and tertiary lagging primary by 30°
93 | Ungrounded_Wye/Wye/Delta Three Winding Transformer | UngstarStarDelta11 | 3 | Wye | Wye | Delta | 0 | 330 | No | No | 1 | 0 |  | Three winding three-phase ungrounded wye/wye/delta with secondary lagging primary by 0° and tertiary lagging primary by 330°
94 | Open Wye/Open Delta Bank | StarDeltaBank | 1 | Wye | Delta | -- | 30 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 30°
95 | Open Wye/Open Delta Bank | StarDelta3Bank | 1 | Wye | Delta | -- | 90 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 90°
96 | Open Wye/Open Delta Bank | StarDelta5Bank | 1 | Wye | Delta | -- | 150 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 150°
97 | Open Wye/Open Delta Bank | StarDelta7Bank | 1 | Wye | Delta | -- | 210 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 210°
98 | Open Wye/Open Delta Bank | StarDelta9Bank | 1 | Wye | Delta | -- | 270 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 270°
99 | Open Wye/Open Delta Bank | StarDelta11Bank | 1 | Wye | Delta | -- | 330 | -- | No | -- | 2 | 1 |  | Single-phase non split winding for open wye/open delta bank with secondary lagging primary by 330°
100 | Ungrounded_Wye/Wye Transformer | UngstarStar | 3 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Two winding three-phase ungrounded wye/wye transformer with secondary lagging primary by 0°
101 | Open Wye/Open Delta Bank | StarDelta3BankModX | 1 | Wye | Delta | -- | 90 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 90°
102 | Open Wye/Open Delta Bank | StarDelta5BankModX | 1 | Wye | Delta | -- | 150 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 150°
103 | Open Wye/Open Delta Bank | StarDelta7BankModX | 1 | Wye | Delta | -- | 210 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 210°
104 | Open Wye/Open Delta Bank | StarDelta9BankModX | 1 | Wye | Delta | -- | 270 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 270°
105 | Open Wye/Open Delta Bank | StarDelta11BankModX | 1 | Wye | Delta | -- | 330 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open wye/delta bank with secondary lagging primary by 330°
106 | Wye/Wye/Delta Transformer | StarStarDelta1 | 3 | Wye | Wye | Delta | 0 | 30 | No | No | 1 | 0 |  | Three winding three-phase grounded wye/grounded wye /delta transformer with tertiary lagging primary by 30°
107 | Zigzag/Star 1 | ZigzagStar1 | 3 | ZigZag | Wye |  | 30 | -- | No | No | 1 | 0 |  | Two winding three-phase zigzag/star transformer with secondary lagging primary by 30°
108 | Zigzag/Delta | ZigzagDelta | 3 | ZigZag | Delta |  | 30 | -- | No | No | 1 | 0 |  | Two winding three-phase zigzag/delta transformer with secondary lagging primary by 30°
109 | Zigzag Grounded | ZigzagGround | 3 | ZigZag |  |  | -- | -- | -- | -- | 1 | 0 |  | Two winding three-phase zigzag grounding transformer
110 | Zigzag/Star 11 | ZigzagStar11 | 3 | ZigZag | Wye |  | 330 | -- | No | No | 1 | 0 |  | Two winding three-phase zigzag/star transformer with secondary lagging primary by 330°
111 | Star/Zigzag 1 | StarZigzag1 | 3 | Wye | ZigZag |  | 30 | -- | No | No | 1 | 0 |  | Two winding three-phase star/zigzag transformer with secondary lagging primary by 30°
112 | Star/Zigzag 11 | StarZigzag11 | 3 | Wye | ZigZag |  | 330 | -- | No | No | 1 | 0 |  | Two winding three-phase star/zigzag transformer with secondary lagging primary by 330°
113 | DeltaZigzag | DeltaZigzag | 3 | Delta | ZigZag |  | 30 | -- | No | No | 1 | 0 |  | Two winding three-phase delta/zigzag transformer with secondary lagging primary by 30°
114 | Open Delta/OpenDelta Transformer | DeltaDelta2BankMod | 1 | Delta | Delta | -- | 60 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 60°
115 | Open Delta/OpenDelta Transformer | DeltaDelta4BankMod | 1 | Delta | Delta | -- | 120 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 120°
116 | Open Delta/OpenDelta Transformer | DeltaDelta4BankMod | 1 | Delta | Delta | -- | 180 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 180°
117 | Open Delta/OpenDelta Transformer | DeltaDelta8BankMod | 1 | Delta | Delta | -- | 240 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 240°
118 | Open Delta/OpenDelta Transformer | DeltaDeltaBankMod | 1 | Delta | Delta | -- | 300 | -- | Yes | Yes | 2 | 1 |  | Single-phase split secondary winding for open delta/delta bank with secondary lagging primary by 300°
119 | Single-Phase Wye/Wye Transformer | StarStarBankX | 1 | Wye | Wye | -- | 0 | -- | No | -- | 1 | 0 |  | Single-phase non split winding for wye/wye transformer with secondary lagging primary by 0°
120 | Single-Phase Delta/Wye Transformer | DeltaStar11SinglePhaseMod | 1 | Delta | Wye | -- | 330 | -- | Yes | -- | 1 | 0 |  | Single-phase split secondary winding for delta/wye transformer with secondary lagging primary by 330° typically used to support 120/240 Volt operation
121 | Three-Phase Closed Delta Regulator | ClosedDeltaRegulatorX | 3 | Delta | Delta | -- | 0 | -- | No | -- | 1 | 0 |  | Three-phase closed delta connected autotransformer (regulator)
122 | Single-Phase Open Delta Regulator | OpenDeltaRegulator0 | 1 | Delta | Delta | -- | 0 | -- | No | -- | 1 | 0 |  | Single-phase open delta connected autotransformer (regulator). This transformer type is connected to another transformer type, 123, to form a three-phase open delta autotransformer (regulator). If the two regulators have phases AB and BC, the AB regulator uses type 122 and the BC regulator uses type 123. If the two regulators have phases BC and CA, the BC regulator uses type 122 and the CA regulator uses type 123. If the two regulators have phases CA and AB, the CA regulator uses type 122 and the AB regulator uses type 123.
123 | Single-Phase Open Delta Regulator | OpenDeltaRegulator1 | 1 | Delta | Delta | -- | 0 | -- | No | -- | 1 | 0 |  | Single-phase open delta connected autotransformer (regulator). When this type is used with another type 122 regulator to form a three-phase open delta autotransformer (regulator). If the two regulators are phase AB and BC, AB regulator uses type 122 and BC regulator uses type 123. If the two regulators are phase BC and CA, BC regulator uses type 122 and CA regulator uses type 123. If the two regulators are phase CA and AB, CA regulator uses type 122 and AB regulator uses type 123.
124 | Single-Phase Delta Regulator | DeltaSinglePhaseRegulator | 1 | Delta | Delta | -- | 0 | -- | No | -- | 3 | 0 |  | Single-phase delta regulator connected to create a three-phase closed delta connected autotransformer (regulator)

## Schedule Point Validation
Schedule Name | Schedule Type | Description | Axis | Axis Description | Unit | Min Value | Max Value
Ampacity Reduction | 9 | Cable ampacity reduction schedule. | X | Cables | cables | 0 | 30
Ampacity Reduction | 9 | Cable ampacity reduction schedule. | Y1 | Cable ampacity | % ampacity | 0 | 100
Billing | 3 | Billing schedule. | N/A | N/A | N/A | N/A | N/A
Cold Load Pick-Up | 5 | Cold-load pick-up schedule. | X | Outage duration in hours | hours | 0 | 48
Cold Load Pick-Up | 5 | Cold-load pick-up schedule. | Y1 | Load multiplier | times normal load | 1 | 3
Cold Load Pick-Up | 5 | Cold-load pick-up schedule. | Y2 | Increased load duration in hours | hours | 0 | 48
Control Cost | 11 | Advanced application control cost schedule. | N/A | N/A | N/A | N/A | N/A
Gen Capability | 16 | Generator capability curve schedule. | X | Active power | kW | 0 | 50000
Gen Capability | 16 | Generator capability curve schedule. | Y1 | Reactive power | kVAR | -30000 | 30000
Gen Capability | 16 | Generator capability curve schedule. | Y2 | Reactive power | kVAR | -30000 | 30000
Load | 1 | Load schedule. | X | Time in hours | hours | 0 | 23
Load | 1 | Load schedule. | Y1 | Peak P in per unit | per unit load | -1.5 | 1.5
Load | 1 | Load schedule. | Y1 | Average P in per unit | per unit load | -3 | 3
Load | 1 | Load schedule. | Y2 | Power factor (exclude 0.0) | power factor | -1 | 1
Load | 1 | Load schedule. | Y2 | Peak Q in per unit | per unit load | -1.5 | 1.5
Load | 1 | Load schedule. | Y2 | Average Q in per unit | per unit load | -3 | 3
Load To Voltage | 2 | Load-to-voltage dependency schedule. | X | Time in hours | hours | 0 | 23
Load To Voltage | 2 | Load-to-voltage dependency schedule. | Y1 | Voltage Dependency Coefficient | coefficient | -99 | 99
Load To Voltage | 2 | Load-to-voltage dependency schedule. | Y2 | Voltage Dependency Coefficient | coefficient | -99 | 99
Load with Generation | 20 | Generation curve embedded in a load curve. | X | Time in hours | hours | 0 | 23
Load with Generation | 20 | Generation curve embedded in a load curve. | Y1 | P in per unit | per unit load | 0 | 1
Load with Generation | 20 | Generation curve embedded in a load curve. | Y2 | Power factor (exclude 0.0) | power factor | -1 | 1
Power | 7 | Real power generation dynamic schedule. | X | Time in hours | hours | 0 | 23
Power | 7 | Real power generation dynamic schedule. | Y1 | Real power target | kW | -50000 | 50000
Power Factor | 13 | Power factor schedule (load on x axis) for the VVC area wide support. | X | Active power | MW | 0 | 20000
Power Factor | 13 | Power factor schedule (load on x axis) for the VVC area wide support. | Y1 | Power factor | power factor | -1 | 2
Problem Definition | 10 | VVC objective function schedule. | X | Time in hours | hours | 0 | 23
Profile Multiplier | 21 | Profile multiplier schedule for use in BLA. | X | Time in hours | hours | 0 | 23
Profile Multiplier | 21 | Profile multiplier schedule for use in BLA. | Y1 | Peak P in per unit | profile multiplier | 0 | 10
Profile Multiplier | 21 | Profile multiplier schedule for use in BLA. | Y2 | Peak Q in per unit | profile multiplier | 0 | 10
Reactive Power | 17 | Reactive power generation dynamic schedule. | X | Time in hours | hours | 0 | 23
Reactive Power | 17 | Reactive power generation dynamic schedule. | Y1 | Reactive power target | kVAR | -30000 | 30000
Power | 22 | Real power load dynamic schedule. | X | Time in hours | hours | 0 | 23
Power | 22 | Real power load dynamic schedule. | Y1 | Real power target | kW | -50000 | 50000
Reactive Power | 23 | Reactive power load dynamic schedule. | X | Time in hours | hours | 0 | 23
Reactive Power | 23 | Reactive power load dynamic schedule. | Y1 | Reactive power target | kVAR | -50000 | 50000
Temp Ampacity | 15 | Temperature ampacity schedule (temp on x axis). | X | Temperature | degrees F | -500 | 200
Temp Ampacity | 15 | Temperature ampacity schedule (temp on x axis). | Y1 | Amp limit | Amp | 1 | 3800
Temperature | 19 | Temperature driven on/off schedule for capacitors. | X | degrees F | degrees F | -80 | 140
Temperature | 19 | Temperature driven on/off schedule for capacitors. | X | degrees C | degrees C | -63 | 60
Temperature | 19 | Temperature driven on/off schedule for capacitors. | Y | On/Off/Unchanged (0/1/2) | On/Off/Unchanged | 0 | 2
Temperature Adjustment | 12 | Temperature adjustment schedule for the BLA. | X | degrees F | degrees F | -80 | 140
Temperature Adjustment | 12 | Temperature adjustment schedule for the BLA. | X | degrees C | degrees C | -63 | 60
Temperature Adjustment | 12 | Temperature adjustment schedule for the BLA. | Y1 | Times nominal load | times nominal load | 0 | 3
Time | 6 | Time (on/off) schedule. | X | Time in hours | hours | 0 | 23
Time | 6 | Time (on/off) schedule. | Y1 | Off/On (just 0 or 1) | on/off | 0 | 1
Time delay schedule | 18 | Time Delay Schedule. | X | Voltage Difference | % | 0 | 20
Time delay schedule | 18 | Time Delay Schedule. | Y1 | Time in seconds | seconds | 0 | 1200
Voltage | 8 | Voltage regulation schedule. | X | Time in hours | hours | 0 | 23
Voltage | 8 | Voltage regulation schedule. | Y1 | V minimum in percent Volt | percent Volt | 0 | 150
Voltage | 8 | Voltage regulation schedule. | Y2 | V maximum in percent Volt | percent Volt | 0 | 150
Voltage Drop | 4 | Secondary voltage drop schedule. | X | Percent transformer loading | % Transformer loading | 0 | 1000
Voltage Drop | 4 | Secondary voltage drop schedule. | Y1 | Percent secondary voltage drop | % Volt Drop | 0 | 100

## Cond Model Mandatory Fields
Field Conductor Type | DIAMETER_CONDMOD | DIAMNEUTRAL_CONDMOD | DIAMSHIELD_CONDMOD | GMRNEUT_CONDMOD | GMRPHASE_CONDMOD | INSULATION_CONDMOD | NEUTDIST_CONDMOD | NUMSTRANDS_CONDMOD | PHDIST_CONDMOD | RNEUTRAL_CONDMOD | RPHASE_CONDMOD | SHIELDTHICK_CONDMOD | R1_CONDMOD | X1_CONDMOD | R0_CONDMOD | X0_CONDMOD
Bare Wire - 0 | Required |  |  |  | Required | [5 empty] | Required
One 3-phase Concentric Neutral - 4 | Required | Required |  | Required | Required | Required | Required | Required | Required | Required | Required
One 3-Phase Tape Shield - 2 | Required |  | Required |  | Required | Required |  |  | Required |  | Required | Required
Secondary Cable - 5 | Required |  |  |  | Required | [5 empty] | Required |  | Required | Required | Required | Required
Singe Phase Tape Shield - 1 | Required |  | Required |  | Required | Required |  |  |  |  | Required | Required
Single Phase Concentric Neutral - 3 | Required | Required |  | Required | Required | Required | Required | Required |  | Required | Required